## BoQ1
Government eProcurement System Created By: PALLIPPATTU RAVI HARI Created Date/Time: 02-Jul-2024 04:22 PM Tender Title: Facility Management of E and M Installations area at Calicut International Airport during 2024_2026 Tender ID: 2024_AAI_197477_1
Tender Inviting Authority: Asst. General Manager Engg(Elect),Calicut Airport
Name of Work : Facility Management of E&M Installations in Operational Area at Calicut International Airport during 2024-26
Contract No: <2024_AAI_197477_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Blue Star Limited (GSTN-27AAACB4487D1ZS) BID ID -709952 |  | MPC ELECTRICALS AND ENGINEERS (GSTN-08ABUPP6558K1ZM) BID ID -713915 |  | STERLING AND WILSON PRIVATE LIMITED(GSTN-NA)--714297 |  | ABHISHEK INTEGRATIONS LIMITED(GSTN-NA)--714283
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Daily operation and periodic maintenance of entire installations related to perimeter lighting, carrying out preventive and breakdown maintenance of E&M installations in new & operational power houses, fire station, ancillary buildings, CISF Barrack, Nav-Aids, power supply to water pumping installations in the operational area including providing required assistance to AAI in maintaining the installations of Calicut Airport as required as per Sl. No. 1 of Annexure A of particular specification. | 24.00 | Month |  | 396043.00 | 9505032.00 | 380000.00 | 9120000.00 | 344777.00 | 8274648.00 | 413740.00 | 9929760.00 | 8274648.00 | STERLING AND WILSON PRIVATE LIMITED
2.00 | Daily operation & Maintenance of grid connected 750KWp, 20kWp and 5kWp Solar plants including minor repairs, replacing devices/components/equipment that are supplied by AAI or OEM integrating the same to system (both hardware and software) and carrying out preventive maintenance, periodic cleaning of SPV panels to ensure optimum generation etc as per Sl. No. 2 of Annexure A of partricular specification. | 24.00 | Month |  | 53562.00 | 1285488.00 | 62000.00 | 1488000.00 | 80270.00 | 1926480.00 | 50246.00 | 1205904.00 | 1205904.00 | ABHISHEK INTEGRATIONS LIMITED
3.00 | Periodic Maintenance, Safe keeping, operation of SPOL & RLIL system as and when needed on the instructions of AAI, co-ordination with AAI and the maintaining the premises of the installations in neat and tidy condition by removing wild growth and timely grass cutting, clearing debris, floor & ceiling cleaning etc for Solar Powered Obstruction Lights installations at 05 Locations and Runway Lead In Lights at 04 Locations, on all days including ensuring serviceability monitoring, maintaining required records etc., as required as per Sl. No. 4 of Annexure A of particular specification. | 24.00 | Month |  | 225032.00 | 5400768.00 | 185400.00 | 4449600.00 | 213977.00 | 5135448.00 | 201841.00 | 4844184.00 | 4449600.00 | MPC ELECTRICALS AND ENGINEERS
4.00 | Daily operation and Maintenance of Sewage Treatment Plant of 400 KLD capacity including carrying out Preventive and Breakdown Maintenance, round the clock, on all days including Sundays and Holidays etc. as required as per Sl. No. 3 of Annexure A of particular specification | 24.00 | Month |  | 151710.00 | 3641040.00 | 146000.00 | 3504000.00 | 164624.00 | 3950976.00 | 188069.00 | 4513656.00 | 3504000.00 | MPC ELECTRICALS AND ENGINEERS
5.00 | Daily operation and Maintenance of Sewage Treatment Plant ( As per the inventory details provided in the tender document) installed at CISF barrack including carrying out Preventive and Breakdown Maintenance, round the clock, on all days including Sundays and Holidays etc. as required as per Sl. No. 3 of Annexure A of particular specification | 24.00 | Month |  | 24529.00 | 588696.00 | 26000.00 | 624000.00 | 71381.00 | 1713144.00 | 21988.00 | 527712.00 | 527712.00 | ABHISHEK INTEGRATIONS LIMITED
6.00 | Providing unskilled manpower for urgent maintenance works such as excavation to locate cable fault, clearing stores, or assisting maintenance related activities etc. as per direction of the EIC. | 200.00 | Days |  | 1049.00 | 209800.00 | 710.00 | 142000.00 | 850.00 | 170000.00 | 651.00 | 130200.00 | 130200.00 | ABHISHEK INTEGRATIONS LIMITED
7.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 1.5TR split type wall mounted type Air conditioners. | 504.00 | Job |  | 390.00 | 196560.00 | 206.00 | 103824.00 | 170.00 | 85680.00 | 196.00 | 98784.00 | 85680.00 | STERLING AND WILSON PRIVATE LIMITED
8.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 1.5TR split type wall mounted type Air conditioners (Inverter type). | 252.00 | Job |  | 390.00 | 98280.00 | 206.00 | 51912.00 | 170.00 | 42840.00 | 196.00 | 49392.00 | 42840.00 | STERLING AND WILSON PRIVATE LIMITED
9.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 2TR split type wall mounted Air conditioners. | 576.00 | Job |  | 520.00 | 299520.00 | 260.00 | 149760.00 | 210.00 | 120960.00 | 250.00 | 144000.00 | 120960.00 | STERLING AND WILSON PRIVATE LIMITED
10.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 2TR Inverter split type Air conditioners. | 1236.00 | Job |  | 520.00 | 642720.00 | 260.00 | 321360.00 | 210.00 | 259560.00 | 250.00 | 309000.00 | 259560.00 | STERLING AND WILSON PRIVATE LIMITED
11.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 3TR Floor mounted 3 phase split Air conditioners . | 360.00 | Job |  | 779.00 | 280440.00 | 404.00 | 145440.00 | 300.00 | 108000.00 | 350.00 | 126000.00 | 108000.00 | STERLING AND WILSON PRIVATE LIMITED
12.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 3TR Cassette type 3 phase split Air conditioners. | 144.00 | Job |  | 866.00 | 124704.00 | 404.00 | 58176.00 | 300.00 | 43200.00 | 350.00 | 50400.00 | 43200.00 | STERLING AND WILSON PRIVATE LIMITED
13.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 3TR Ductable type 3 phase split Air conditioners. | 264.00 | Job |  | 779.00 | 205656.00 | 404.00 | 106656.00 | 300.00 | 79200.00 | 350.00 | 92400.00 | 79200.00 | STERLING AND WILSON PRIVATE LIMITED
14.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 3 TR Cassette type Inverter single phase Air conditioner | 72.00 | Job |  | 866.00 | 62352.00 | 404.00 | 29088.00 | 330.00 | 23760.00 | 350.00 | 25200.00 | 23760.00 | STERLING AND WILSON PRIVATE LIMITED
15.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 3 TR Cassette type Inverter three phase Air conditioner | 40.00 | Job |  | 866.00 | 34640.00 | 404.00 | 16160.00 | 330.00 | 13200.00 | 350.00 | 14000.00 | 13200.00 | STERLING AND WILSON PRIVATE LIMITED
16.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 4TR Cassette type 3 phase split Air conditioners. | 192.00 | Job |  | 1154.00 | 221568.00 | 440.00 | 84480.00 | 350.00 | 67200.00 | 500.00 | 96000.00 | 67200.00 | STERLING AND WILSON PRIVATE LIMITED
17.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 4TR Cassette type inverter split Air conditioners. | 36.00 | Job |  | 1154.00 | 41544.00 | 530.00 | 19080.00 | 350.00 | 12600.00 | 500.00 | 18000.00 | 12600.00 | STERLING AND WILSON PRIVATE LIMITED
18.00 | All inclusive Comprehensive Maintenance of following type, make and capacity of air-conditioners installed at different locations including providing all necessary consumables and spares carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation (1 Job = Comprehensive maintenance of 01 AC unit for one month) Note. CMC of split AC and water cooler includes manpower as per Sl. No. 5 of Annexure A of particular specification 5.5TR Ductable type 3 phase split Air conditioners. | 48.00 | Job |  | 1429.00 | 68592.00 | 620.00 | 29760.00 | 520.00 | 24960.00 | 700.00 | 33600.00 | 24960.00 | STERLING AND WILSON PRIVATE LIMITED
19.00 | Comprehensive Maintenance of VRV multi split Airconditioning system of 30 HP capacities comprising of inverter scroll compressor, air cooled condenser, system controller, R 410 refrigerant, including providing all necessary consumables and spares carrying out various maintenance activities by maintaining adequate technical tie up with OEM (Blue star) as required. (1 Job = Maintaining entire system for 1 year) Details 1) Outdoor unit capacity of 30 HP (12HP-1 No.,10HP-1 No.,8HP-1 No.) 2) Indoor units : 2 Ton High wall split -4 Nos., 1 TR cassette type AC unit - 3 Nos., 2 TR cassette type AC unit - 2 Nos., 2.8 TR cassette type AC unit - 1 No., 4 TR cassette type AC unit - 3 Nos. | 2.00 | Job |  | 155857.00 | 311714.00 | 125000.00 | 250000.00 | 96000.00 | 192000.00 | 150000.00 | 300000.00 | 192000.00 | STERLING AND WILSON PRIVATE LIMITED
20.00 | All inclusive Comprehensive Maintenance of horizontal FAN COIL UNITS, blow through type, 3 rows deep chilled water coil, centrifugal fans, metalic filters, main condensate drain pans, casing, coil piping connections, condensate drain connections working at 230 + 6% volts, 50 cycles, single phase power supply. Fan Coil are of 3TR and 1200CFM refrigeration capacities ( 1 Job = Comprehensive maintenance of the Unit with accesseries for one month ). | 144.00 | Job |  | 375.00 | 54000.00 | 134.00 | 19296.00 | 81.00 | 11664.00 | 130.00 | 18720.00 | 11664.00 | STERLING AND WILSON PRIVATE LIMITED
21.00 | Comprehensive maintenance of water coolers of various makes of following capacities installed at different locations including providing all necessary consumables and spares, carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation including periodic checking of all units for proper functionality etc. complete as required. (1 Job =Comprehensive maintenance of 01 water cooler unit per month) 20/40 Ltr | 96.00 | Job |  | 251.00 | 24096.00 | 80.00 | 7680.00 | 90.00 | 8640.00 | 87.00 | 8352.00 | 7680.00 | MPC ELECTRICALS AND ENGINEERS
22.00 | Comprehensive maintenance of water coolers of various makes of following capacities installed at different locations including providing all necessary consumables and spares, carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation including periodic checking of all units for proper functionality etc. complete as required. (1 Job =Comprehensive maintenance of 01 water cooler unit per month) 40/80 Ltr | 144.00 | Job |  | 266.00 | 38304.00 | 80.00 | 11520.00 | 100.00 | 14400.00 | 92.00 | 13248.00 | 11520.00 | MPC ELECTRICALS AND ENGINEERS
23.00 | Comprehensive maintenance of water coolers of various makes of following capacities installed at different locations including providing all necessary consumables and spares, carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation including periodic checking of all units for proper functionality etc. complete as required. (1 Job =Comprehensive maintenance of 01 water cooler unit per month) 60/120 Ltr | 120.00 | Job |  | 283.00 | 33960.00 | 80.00 | 9600.00 | 110.00 | 13200.00 | 98.00 | 11760.00 | 9600.00 | MPC ELECTRICALS AND ENGINEERS
24.00 | Comprehensive maintenance of 125 ltr/Hr capacity water cooler with UV and Ozone purifying technologies with necessary filters and water dispensing Mechanism with hot, normal and cool water facilities with stainless steel body, suitable compressor, insulation etc. as required (Model No.HIMA 7 NHC- 3 nos) (1 Job =Comprehensive maintenance of 01 water cooler unit per month). | 72.00 | Job |  | 470.00 | 33840.00 | 170.00 | 12240.00 | 140.00 | 10080.00 | 163.00 | 11736.00 | 10080.00 | STERLING AND WILSON PRIVATE LIMITED
25.00 | Comprehensive maintenance 50 ltr/Hr capacity water Dispenser with Ozone purifying technologies with necessary filters and water dispensing Mechanism with normal water facilities with SS body,insulation etc. as required (Model No. VARUNA 2: -1 nos) (1 Job =Comprehensive maintenance of 01 water cooler unit per month). | 24.00 | Job |  | 421.00 | 10104.00 | 143.00 | 3432.00 | 150.00 | 3600.00 | 146.00 | 3504.00 | 3432.00 | MPC ELECTRICALS AND ENGINEERS
26.00 | Comprehensive maintenance of hot and cold water dispensers of USHA model HNCCC21V9S or similar installed at different locations including providing all necessary consumables and spares, carrying out various maintenance activities as per AAI maintenance manual/OEM recommendation including daily checking of all units for proper functionality etc. complete as required. (1 Job =Comprehensive maintenance of 01 water cooler unit per month) | 600.00 | Job |  | 421.00 | 252600.00 | 143.00 | 85800.00 | 140.00 | 84000.00 | 146.00 | 87600.00 | 84000.00 | STERLING AND WILSON PRIVATE LIMITED
27.00 | Comprehensive maintenance of stand alone type Kelby make water cooler Model No.Brook 250 NHC / any other make including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts. ( 1 Job = 1 unit/year) Ist year (First 12 months) | 7.00 | Job |  | 8305.00 | 58135.00 | 3500.00 | 24500.00 | 4200.00 | 29400.00 | 4000.00 | 28000.00 | 24500.00 | MPC ELECTRICALS AND ENGINEERS
28.00 | Comprehensive maintenance of stand alone type Kelby make water cooler Model No.Brook 250 NHC / any other make including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts. ( 1 Job = 1 unit/year) IInd year (Next 12 months) | 12.00 | Job |  | 8887.00 | 106644.00 | 4400.00 | 52800.00 | 4200.00 | 50400.00 | 4000.00 | 48000.00 | 48000.00 | ABHISHEK INTEGRATIONS LIMITED
29.00 | Comprehensive maintenance of stand alone type Kelby make water cooler Model No.Brook 125 NHC/ any other make including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts ( 1 Job = 1 Unit for 01 year) Ist year (First 12 months) | 4.00 | Job |  | 7592.00 | 30368.00 | 3500.00 | 14000.00 | 3400.00 | 13600.00 | 3400.00 | 13600.00 | 13600.00 | ABHISHEK INTEGRATIONS LIMITED, STERLING AND WILSON PRIVATE LIMITED
30.00 | Comprehensive maintenance of stand alone type Kelby make water cooler Model No.Brook 125 NHC/ any other make including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts ( 1 Job = 1 Unit for 01 year) IInd year (Next 12 months) | 4.00 | Job |  | 8148.00 | 32592.00 | 3500.00 | 14000.00 | 3400.00 | 13600.00 | 3400.00 | 13600.00 | 13600.00 | ABHISHEK INTEGRATIONS LIMITED, STERLING AND WILSON PRIVATE LIMITED
31.00 | Comprehensive maintenance of wall mount type Kelby make water purifier Model No.Brook 125 N including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts ( 1 Job = 1 Unit for 01 year) Ist year (First 12 months) | 13.00 | Job |  | 8783.00 | 114179.00 | 2600.00 | 33800.00 | 3400.00 | 44200.00 | 3000.00 | 39000.00 | 33800.00 | MPC ELECTRICALS AND ENGINEERS
32.00 | Comprehensive maintenance of wall mount type Kelby make water purifier Model No.Brook 125 N including two half yearly mandatory services with replacement of spun and carbon filters and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts ( 1 Job = 1 Unit for 01 year) IInd year (Next 12 months) | 13.00 | Job |  | 8783.00 | 114179.00 | 2600.00 | 33800.00 | 3400.00 | 44200.00 | 3000.00 | 39000.00 | 33800.00 | MPC ELECTRICALS AND ENGINEERS
33.00 | Comprehensive maintenance of 100 LPH Reverse Osmosis Plant (RO plant) having UV sterilization system carrying out various maintenance activities, replacement of filters, servicing, attending breakdowns etc as required.( 1 Job = 1 unit/year) | 2.00 | Job |  | 23843.00 | 47686.00 | 8000.00 | 16000.00 | 14800.00 | 29600.00 | 8000.00 | 16000.00 | 16000.00 | MPC ELECTRICALS AND ENGINEERS, ABHISHEK INTEGRATIONS LIMITED
34.00 | Comprehensive maintenance of stand alone type Blue star make water cooler with UV purifier of 80Litre storage capacity having cold and normal water outlet including two half yearly mandatory services with replacement of spun and carbon filters (internal & external) and attending breakdown/ malfunction within 24 Hrs throughout the year including repair/replacement of all defective parts(1 Job =Comprehensive maintenance of 01 water cooler unit per month). | 48.00 | Job |  | 962.00 | 46176.00 | 800.00 | 38400.00 | 248.00 | 11904.00 | 550.00 | 26400.00 | 11904.00 | STERLING AND WILSON PRIVATE LIMITED
35.00 | Relocating existing 1.5/2.0 Ton split type AC including dismantling, shifting re installing and re commissioning at new location complete as required [excluding any extra materials]. | 10.00 | Job |  | 2666.00 | 26660.00 | 2600.00 | 26000.00 | 3000.00 | 30000.00 | 3500.00 | 35000.00 | 26000.00 | MPC ELECTRICALS AND ENGINEERS
36.00 | Relocating existing 3.0 Ton split type AC including dismantling, shifting re installing and re commissioning at new location complete as required [excluding any extra materials]. | 3.00 | Job |  | 3333.00 | 9999.00 | 3050.00 | 9150.00 | 4500.00 | 13500.00 | 4000.00 | 12000.00 | 9150.00 | MPC ELECTRICALS AND ENGINEERS
37.00 | Providing & laying of following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit. 1/4 inch | 20.00 | Meter |  | 598.00 | 11960.00 | 260.00 | 5200.00 | 280.00 | 5600.00 | 230.00 | 4600.00 | 4600.00 | ABHISHEK INTEGRATIONS LIMITED
38.00 | Providing & laying of following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit. 1/2 inch | 20.00 | Meter |  | 691.00 | 13820.00 | 290.00 | 5800.00 | 330.00 | 6600.00 | 460.00 | 9200.00 | 5800.00 | MPC ELECTRICALS AND ENGINEERS
39.00 | Providing & laying of following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit. 3/8 inch | 60.00 | Meter |  | 658.00 | 39480.00 | 530.00 | 31800.00 | 340.00 | 20400.00 | 345.00 | 20700.00 | 20400.00 | STERLING AND WILSON PRIVATE LIMITED
40.00 | Providing & laying of following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit. 5/8 inch | 50.00 | Meter |  | 934.00 | 46700.00 | 710.00 | 35500.00 | 480.00 | 24000.00 | 512.00 | 25600.00 | 24000.00 | STERLING AND WILSON PRIVATE LIMITED
41.00 | Providing & laying of following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit. 3/4 inch | 25.00 | Meter |  | 981.00 | 24525.00 | 710.00 | 17750.00 | 560.00 | 14000.00 | 690.00 | 17250.00 | 14000.00 | STERLING AND WILSON PRIVATE LIMITED
42.00 | Providing and laying of UPVC pipe 1" dia for AC drain including fixing on existing surface complete as required. | 20.00 | meter |  | 345.00 | 6900.00 | 80.00 | 1600.00 | 230.00 | 4600.00 | 80.00 | 1600.00 | 1600.00 | MPC ELECTRICALS AND ENGINEERS, ABHISHEK INTEGRATIONS LIMITED
43.00 | Providing & laying (2+1E) Core x 2.5 sq.mm FR insulated, PVC sheathed unarmored multi strand copper cable suitable for the AC outdoor unit connection. | 50.00 | Meter |  | 128.00 | 6400.00 | 107.00 | 5350.00 | 200.00 | 10000.00 | 108.00 | 5400.00 | 5350.00 | MPC ELECTRICALS AND ENGINEERS
44.00 | Testing of water samples taken from water purifiers/cooler outlet in NABL/state goverment accredited Lab for the following parameters and submitting reports as required. 1) PH value 2) Turbidity 3)TDS 4)Total Iron ( Fe) 5)coliform 6) E coli | 300.00 | Job |  | 555.00 | 166500.00 | 1160.00 | 348000.00 | 1400.00 | 420000.00 | 550.00 | 165000.00 | 165000.00 | ABHISHEK INTEGRATIONS LIMITED
45.00 | Monthly Testing of water samples taken from treated water of STP in NABL/state government accredited Lab for the following parameters and submitting reports as required. 1) PH value 2) Suspended solids 3)COD 4)BOD for 3 days at 27 degree C 5)Oil & grease | 48.00 | Job |  | 1111.00 | 53328.00 | 1250.00 | 60000.00 | 1400.00 | 67200.00 | 1045.00 | 50160.00 | 50160.00 | ABHISHEK INTEGRATIONS LIMITED
46.00 | Replacement of approved consumable iron birm media of the exisiting water purifiers ( 1 Job = Two Times replacement in a year ). | 56.00 | Job |  | 436.00 | 24416.00 | 530.00 | 29680.00 | 790.00 | 44240.00 | 500.00 | 28000.00 | 24416.00 | Blue Star Limited
47.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 800A, 415 Volts | 8.00 | Job |  | 1944.00 | 15552.00 | 2600.00 | 20800.00 | 3900.00 | 31200.00 | 1200.00 | 9600.00 | 9600.00 | ABHISHEK INTEGRATIONS LIMITED
48.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 1000A, 415 Volts | 8.00 | Job |  | 1944.00 | 15552.00 | 2240.00 | 17920.00 | 3900.00 | 31200.00 | 1200.00 | 9600.00 | 9600.00 | ABHISHEK INTEGRATIONS LIMITED
49.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 1250A, 415 Volts | 16.00 | Job |  | 1944.00 | 31104.00 | 2600.00 | 41600.00 | 3900.00 | 62400.00 | 1200.00 | 19200.00 | 19200.00 | ABHISHEK INTEGRATIONS LIMITED
50.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 1600A, 415 Volts | 4.00 | Job |  | 1944.00 | 7776.00 | 2240.00 | 8960.00 | 4100.00 | 16400.00 | 1200.00 | 4800.00 | 4800.00 | ABHISHEK INTEGRATIONS LIMITED
51.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 2000A, 415 Volts | 10.00 | Job |  | 1944.00 | 19440.00 | 2240.00 | 22400.00 | 4250.00 | 42500.00 | 1200.00 | 12000.00 | 12000.00 | ABHISHEK INTEGRATIONS LIMITED
52.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 2500A, 415 Volts | 2.00 | Job |  | 1944.00 | 3888.00 | 2600.00 | 5200.00 | 4250.00 | 8500.00 | 1200.00 | 2400.00 | 2400.00 | ABHISHEK INTEGRATIONS LIMITED
53.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 3200 A, 415 Volts | 6.00 | Job |  | 1944.00 | 11664.00 | 2600.00 | 15600.00 | 4500.00 | 27000.00 | 1200.00 | 7200.00 | 7200.00 | ABHISHEK INTEGRATIONS LIMITED
54.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). L&T Make 4000A,415Volts | 18.00 | Job |  | 1944.00 | 34992.00 | 2600.00 | 46800.00 | 4500.00 | 81000.00 | 1200.00 | 21600.00 | 21600.00 | ABHISHEK INTEGRATIONS LIMITED
55.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). GE make Spectronics 4P, 415V,800A | 30.00 | Job |  | 1944.00 | 58320.00 | 2600.00 | 78000.00 | 3900.00 | 117000.00 | 1200.00 | 36000.00 | 36000.00 | ABHISHEK INTEGRATIONS LIMITED
56.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). GE make Spectronics 4P, 415V,1000A | 8.00 | Job |  | 1944.00 | 15552.00 | 2600.00 | 20800.00 | 3900.00 | 31200.00 | 1200.00 | 9600.00 | 9600.00 | ABHISHEK INTEGRATIONS LIMITED
57.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). GE make 4P, 415V,1250A | 72.00 | Job |  | 1944.00 | 139968.00 | 2240.00 | 161280.00 | 3900.00 | 280800.00 | 1200.00 | 86400.00 | 86400.00 | ABHISHEK INTEGRATIONS LIMITED
58.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). GE make 4P, 415V,2000A | 4.00 | Job |  | 1944.00 | 7776.00 | 2600.00 | 10400.00 | 4250.00 | 17000.00 | 1200.00 | 4800.00 | 4800.00 | ABHISHEK INTEGRATIONS LIMITED
59.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). ABB Make 1250 A, 4P, 415 V | 44.00 | Job |  | 1944.00 | 85536.00 | 2600.00 | 114400.00 | 3900.00 | 171600.00 | 1200.00 | 52800.00 | 52800.00 | ABHISHEK INTEGRATIONS LIMITED
60.00 | Servicing of following air circuit breakers through specialised service personnel, overhauling; carrying out preventive maintenance checks as per manufacturer's specification and attending breakdown calls as and when required. Spares if any required shall be provided by AAI (services for an ACB in 1 year i.e. one overhauling & servicing in one year= 1 Job). Schneider make 1250 A, 4P, 415V | 22.00 | Job |  | 1944.00 | 42768.00 | 2600.00 | 57200.00 | 3900.00 | 85800.00 | 1200.00 | 26400.00 | 26400.00 | ABHISHEK INTEGRATIONS LIMITED
61.00 | Testing of BDV of transformer oil from approved testing facility and submission of report to AAI | 5.00 | Job |  | 667.00 | 3335.00 | 350.00 | 1750.00 | 950.00 | 4750.00 | 1100.00 | 5500.00 | 1750.00 | MPC ELECTRICALS AND ENGINEERS
62.00 | Filtration of the transformer oil to achieve satisfactory BDV value for the following transformers installed at Calicut International Airport, including topping up of oil (if required, the transformer oil for topping up will be supplied by AAI) and testing the BDV of the transformer oil after filtration and submission of reports to AAI. (01 job = carrying the work once in one transformer) 2000 KVA Make : Voltamp, with OLTC Year of Manufacture : 2006 Oil : 1456 ltrs (approx.) | 4.00 | Job |  | 9998.00 | 39992.00 | 6200.00 | 24800.00 | 23000.00 | 92000.00 | 14560.00 | 58240.00 | 24800.00 | MPC ELECTRICALS AND ENGINEERS
63.00 | Filtration of the transformer oil to achieve satisfactory BDV value for the following transformers installed at Calicut International Airport, including topping up of oil (if required, the transformer oil for topping up will be supplied by AAI) and testing the BDV of the transformer oil after filtration and submission of reports to AAI. (01 job = carrying the work once in one transformer) 2000 KVA, Make : Kirlosker, without OLTC Year of Manufacture : 2007 Oil :1900 ltrs (approx.) | 6.00 | Job |  | 9998.00 | 59988.00 | 8000.00 | 48000.00 | 26000.00 | 156000.00 | 16016.00 | 96096.00 | 48000.00 | MPC ELECTRICALS AND ENGINEERS
64.00 | Supply and changing of silica gel of 11/0.433 KV transformer of new and old power house | 20.00 | Kg |  | 525.00 | 10500.00 | 404.00 | 8080.00 | 550.00 | 11000.00 | 275.00 | 5500.00 | 5500.00 | ABHISHEK INTEGRATIONS LIMITED
65.00 | Arresting of oil leakage in 2000KVA 11/0.433 KV Transformer LT side by replacement of joint gaskets between conservator to oil tank, Bucholz relay, tap switch, any areas and changing of oil guage glass indicator and removing and fixing of bus duct complete as required. | 3.00 | Job |  | 24440.00 | 73320.00 | 17000.00 | 51000.00 | 22500.00 | 67500.00 | 15000.00 | 45000.00 | 45000.00 | ABHISHEK INTEGRATIONS LIMITED
66.00 | Servicing of Areva/ equivalent Make 11 KV, 50Hz vacuum circuit breaker i/c cleaning of CTs, PTs, Busbars and testing etc. as required and as per manufacturers guidelines(Timer test, contact resistance test, 5KV megger test are included) of different rating: | 16.00 | Job |  | 5554.00 | 88864.00 | 7100.00 | 113600.00 | 4750.00 | 76000.00 | 2000.00 | 32000.00 | 32000.00 | ABHISHEK INTEGRATIONS LIMITED
67.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Differential protection Relay, Type : CAG, electromechanical Model no:CAG34AF71A, Make : AREVA | 8.00 | Job |  | 555.00 | 4440.00 | 440.00 | 3520.00 | 2900.00 | 23200.00 | 300.00 | 2400.00 | 2400.00 | ABHISHEK INTEGRATIONS LIMITED
68.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Earth Fault Relay(Inverse), Type : CDG, Electromechanical, Model no : CDG11AF006SACH, Make : ALSTOM | 4.00 | Job |  | 444.00 | 1776.00 | 440.00 | 1760.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
69.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. OVER CURRENT RELAY(Inverse) all the 3 elements, Type : CDV, Electromechanical, Model no : CDV62EG8512ACH, Make : AREVA | 4.00 | Job |  | 555.00 | 2220.00 | 1250.00 | 5000.00 | 1250.00 | 5000.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
70.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Undervoltage Relay, Type : VDG, electromechanical, Model no : VDG 13AF9101ACH, Make : ALSTOM | 4.00 | Job |  | 444.00 | 1776.00 | 530.00 | 2120.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
71.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Differential protection Relay, Reverse Power Relay , Type : CCUM21,electromechanical, Model no : CCUM21PF132A, Make: AREVA | 4.00 | Job |  | 444.00 | 1776.00 | 1250.00 | 5000.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
72.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Overvoltage Relay Type : VDG, electromechanical, Model no:VDG11AF001SBCH, Make : ALSTOM | 4.00 | Job |  | 555.00 | 2220.00 | 800.00 | 3200.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
73.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Overcurrent & Earth Relay(Inverse) - all the 3 elements Type : CDG, electromechanical, Model no:CDG31EG002SBCH/CDG61EG101ZRCH Make :AREVA | 8.00 | Job |  | 667.00 | 5336.00 | 1250.00 | 10000.00 | 1250.00 | 10000.00 | 300.00 | 2400.00 | 2400.00 | ABHISHEK INTEGRATIONS LIMITED
74.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Underfrequency/Overfrequency Relay, Type: MFVUM22, Digital, Model no ; MFVUM22D1AA0015A, Make : Alstom | 4.00 | Job |  | 667.00 | 2668.00 | 800.00 | 3200.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
75.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Instantaneous Under/Over voltage Relay Type : VAGM , electromechanical Model no:VAGM22AF171G, Make: AREVA | 4.00 | Job |  | 555.00 | 2220.00 | 800.00 | 3200.00 | 950.00 | 3800.00 | 300.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
76.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Earth fault relay, Type SC14S, Make: L&T | 6.00 | Job |  | 555.00 | 3330.00 | 800.00 | 4800.00 | 1250.00 | 7500.00 | 300.00 | 1800.00 | 1800.00 | ABHISHEK INTEGRATIONS LIMITED
77.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Over/under voltage relay, Type MV12 , Make:L&T | 6.00 | Job |  | 667.00 | 4002.00 | 800.00 | 4800.00 | 950.00 | 5700.00 | 300.00 | 1800.00 | 1800.00 | ABHISHEK INTEGRATIONS LIMITED
78.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Overcurrent & Earth Relay(Inverse) - all the 3 elements Type CDG, Model no:CDG 31EG001SBCH, Make AREVA | 12.00 | Job |  | 555.00 | 6660.00 | 1250.00 | 15000.00 | 1250.00 | 15000.00 | 300.00 | 3600.00 | 3600.00 | ABHISHEK INTEGRATIONS LIMITED
79.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Overcurrent & Time delay , Short Circuit & Time delay, Ground fault & Time delay, Type : SR18G Make L&T | 24.00 | Job |  | 555.00 | 13320.00 | 1250.00 | 30000.00 | 950.00 | 22800.00 | 300.00 | 7200.00 | 7200.00 | ABHISHEK INTEGRATIONS LIMITED
80.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Overcurrent & Time delay, Short Circuit & Time delay,Ground fault& Time delay, Instantaneous, Type : RMS7, Make : GE Spectronics | 114.00 | Job |  | 555.00 | 63270.00 | 1250.00 | 142500.00 | 1250.00 | 142500.00 | 300.00 | 34200.00 | 34200.00 | ABHISHEK INTEGRATIONS LIMITED
81.00 | Testing, Calibration of relays at Calicut Airport (As per the Annexure attached) by secondary injection method with suitable testing kit with a Govt. approved Laboratory/ Test centre including submission of report of calibration to AAI. Restricted E/F relay Make: Alstom, trip circuit efficacy testing by simulation, end connection if any | 6.00 | Job |  | 667.00 | 4002.00 | 800.00 | 4800.00 | 1250.00 | 7500.00 | 300.00 | 1800.00 | 1800.00 | ABHISHEK INTEGRATIONS LIMITED
82.00 | Testing and Calibration of following type AC meters by suitable method from Govt approved Test centre and submission of the calibration cerificate as per NABL norms. Multi Function Meter Model EM Conzerv 6400 | 25.00 | Job |  | 1222.00 | 30550.00 | 800.00 | 20000.00 | 4400.00 | 110000.00 | 300.00 | 7500.00 | 7500.00 | ABHISHEK INTEGRATIONS LIMITED
83.00 | Testing and Calibration of following type AC meters by suitable method from Govt approved Test centre and submission of the calibration cerificate as per NABL norms True RMS Ammeter of range 0 A - 30 A rms (30/1 A ) | 16.00 | Job |  | 667.00 | 10672.00 | 800.00 | 12800.00 | 2500.00 | 40000.00 | 300.00 | 4800.00 | 4800.00 | ABHISHEK INTEGRATIONS LIMITED
84.00 | Testing and Calibration of Clinometer make M/s AMA by suitable method from OEM and submission of the calibration certificate to AAI. The Job includes the charges for to and fro transportation of the equipment to the testing/calibration centre. | 4.00 | Job |  | 20996.00 | 83984.00 | 12500.00 | 50000.00 | 7000.00 | 28000.00 | 14850.00 | 59400.00 | 28000.00 | STERLING AND WILSON PRIVATE LIMITED
85.00 | Testing with suitable testing kit with government approved laboratory/test centre including trip circuit efficacy testing by end to end simulation from CT secondary to trip coil and corrections if any | 200.00 | Job |  | 333.00 | 66600.00 | 1250.00 | 250000.00 | 750.00 | 150000.00 | 330.00 | 66000.00 | 66000.00 | ABHISHEK INTEGRATIONS LIMITED
86.00 | Servicing of Honda make Generator Set of the following models from authorised service dealers: Model:EXK 2800 S-2KVA | 2.00 | Job |  | 2444.00 | 4888.00 | 2600.00 | 5200.00 | 5000.00 | 10000.00 | 1210.00 | 2420.00 | 2420.00 | ABHISHEK INTEGRATIONS LIMITED
87.00 | Servicing of Honda make Generator Set of the following models from authorised service dealers: Model:EK 1000-650VA | 2.00 | Job |  | 2444.00 | 4888.00 | 2600.00 | 5200.00 | 5000.00 | 10000.00 | 935.00 | 1870.00 | 1870.00 | ABHISHEK INTEGRATIONS LIMITED
88.00 | Clearing of Grass/vegetation around street light poles, HT yard and other electrical installations by mechanical means like grass cutting machine, disposal of cut grass including Man Power etc complete as required and as per instructions from Engineer In Charge. | 1500.00 | sqm |  | 17.00 | 25500.00 | 5.30 | 7950.00 | 14.00 | 21000.00 | 5.00 | 7500.00 | 7500.00 | ABHISHEK INTEGRATIONS LIMITED
89.00 | Painting of electrical panels, bus ducts, transformers, pipelines etc with synthetic enamel paint of required colour , approved brand ( 2 or more coats ). - By hand brush/roller | 75.00 | sqm |  | 389.00 | 29175.00 | 80.00 | 6000.00 | 160.00 | 12000.00 | 150.00 | 11250.00 | 6000.00 | MPC ELECTRICALS AND ENGINEERS
90.00 | Painting of exhaust pipes etc with heat resistant paint 400 deg. C or more of required colour of approved brand. ( 2 or more coats ). | 175.00 | sqm |  | 555.00 | 97125.00 | 116.00 | 20300.00 | 320.00 | 56000.00 | 300.00 | 52500.00 | 20300.00 | MPC ELECTRICALS AND ENGINEERS
91.00 | Painting of electrical panels, bus ducts, transformers, pipelines etc with polyruthene enamel paint of required colour , approved brand ( 2 or more coats ). - By Spray paint | 600.00 | sqm |  | 443.00 | 265800.00 | 92.00 | 55200.00 | 161.00 | 96600.00 | 200.00 | 120000.00 | 55200.00 | MPC ELECTRICALS AND ENGINEERS
92.00 | Painting of double pole structures, street light poles along with supporting structures, anywhere in the airport premises with polyruthene enamel paint of required colour, approved brand.(1 pole=1 job) | 500.00 | Job |  | 999.00 | 499500.00 | 710.00 | 355000.00 | 300.00 | 150000.00 | 250.00 | 125000.00 | 125000.00 | ABHISHEK INTEGRATIONS LIMITED
93.00 | Re-lettering on panels/earth pits using enamel painting with suitable colour as per the direction of Engineer In Charge (1 Job = 1 letter of 3 cm height) | 2000.00 | Job |  | 56.00 | 112000.00 | 11.00 | 22000.00 | 28.00 | 56000.00 | 20.00 | 40000.00 | 22000.00 | MPC ELECTRICALS AND ENGINEERS
94.00 | Numbering of runway light fixtures using suitable paint/ using stencil with yellow background and black letters complete as required. (1 Job = 1 llight fixture) | 550.00 | Job |  | 400.00 | 220000.00 | 80.00 | 44000.00 | 28.00 | 15400.00 | 25.00 | 13750.00 | 13750.00 | ABHISHEK INTEGRATIONS LIMITED
95.00 | Numbering of runway light fixture CI box using suitable paint/ using stencil with black letters complete as required.(1 Job = 1 CI box) | 1450.00 | Job |  | 220.00 | 319000.00 | 35.00 | 50750.00 | 32.00 | 46400.00 | 20.00 | 29000.00 | 29000.00 | ABHISHEK INTEGRATIONS LIMITED
96.00 | Supply and fixing of Earth fault relay equivalent to Type SC14S, Make: L&T | 6.00 | No. |  | 13886.00 | 83316.00 | 2600.00 | 15600.00 | 14900.00 | 89400.00 | 10360.00 | 62160.00 | 15600.00 | MPC ELECTRICALS AND ENGINEERS
97.00 | Supply and fixing of Over/under voltage relay equibvalent toType MV12 , Make:L&T | 9.00 | No. |  | 13331.00 | 119979.00 | 12500.00 | 112500.00 | 17000.00 | 153000.00 | 10360.00 | 93240.00 | 93240.00 | ABHISHEK INTEGRATIONS LIMITED
98.00 | Preparing Effluclean Activated Effective Microorganism solution(5 litr) from EM stock solution, water and Jagger as mentioned in the tender for treating the sewage. The Job includes the supply of required Jagger and EM solution for preparing 5 litre Effluclean Activated Microorganism solution. The treatment shall be done by operator. | 250.00 | Job |  | 369.00 | 92250.00 | 206.00 | 51500.00 | 600.00 | 150000.00 | 160.00 | 40000.00 | 40000.00 | ABHISHEK INTEGRATIONS LIMITED
99.00 | Servicing of both A1 Blowers (MODEL-A1-67M) and motor (MODEL K2147436) including complete servicing of blower, clearance check, timing setting and cleaning of filter overhauling of motor, replacing the gland packing etc as required including transportation charges and any other incidental charges complete as required.(1 job= 1 servicing once a year) | 2.00 | Job |  | 8887.00 | 17774.00 | 8000.00 | 16000.00 | 30000.00 | 60000.00 | 9677.00 | 19354.00 | 16000.00 | MPC ELECTRICALS AND ENGINEERS
100.00 | Servicing of following pumps at STP installed at Airport School including overhauling, replacing the gland packing etc as required(1 job= servicing of all pumps below once in a year ) a) Sewage Pump – 5HP, make : Kirloskar – 2 Nos b) Filter Feed Pump – 5HP, make : Kirloskar – 2 Nos c) Sludge Pump – 3HP, make : Kirloskar – 2 Nos d) self-priming Sludge Effluent Transfer Pump-10HP, Make : ABB-2 Nos e) Treated Water Pump (NIAB) - 20HP, Make : ABB - 2 Nos | 2.00 | Job |  | 15552.00 | 31104.00 | 12500.00 | 25000.00 | 30000.00 | 60000.00 | 13037.00 | 26074.00 | 25000.00 | MPC ELECTRICALS AND ENGINEERS
101.00 | Supply of SODIUM HYPO CHLORITE WITH 10% CHLORINE (120 GPL) and disinfection of treated water with mixture of Sodium Hypo Chlorite with 10% Chlorine (120gpl) per day to get 0.1 ppm Residual Free Chlorine (Approximate Requirement for Chlorination per day as per STP Consultant is 50 Kg/day, 1 Job Requirement for Chlorination per day as per STP Consultant is 50 Kg/day, 1 job = 50 Kg) | 500.00 | Job |  | 1574.00 | 787000.00 | 710.00 | 355000.00 | 1080.00 | 540000.00 | 1750.00 | 875000.00 | 355000.00 | MPC ELECTRICALS AND ENGINEERS
102.00 | Supply of Polyelectrolyte Anion Powder and mixing with water for treatment of slugde tank (Approximate Requirement for Anion Powder per day as per STP Consultant is 2 Kg/day mixed with 198L Water, 1 Job = 2Kg) | 200.00 | Job |  | 1083.00 | 216600.00 | 800.00 | 160000.00 | 500.00 | 100000.00 | 677.00 | 135400.00 | 100000.00 | STERLING AND WILSON PRIVATE LIMITED
103.00 | Servicing of following make air blower motor set including complete servicing of blower, clearance check, timing setting cleaning of filter, overhauling of motor, replacing the gland packing etc as required including transportation charges and any other incidental charges complete as required.(1 job= 1 servicing once a year) Everest Blower (Model 1450) and Crompton Greaves Motor ( Model 1542J) | 2.00 | Job |  | 6665.00 | 13330.00 | 2000.00 | 4000.00 | 10000.00 | 20000.00 | 6774.00 | 13548.00 | 4000.00 | MPC ELECTRICALS AND ENGINEERS
104.00 | Servicing of following make air blower motor set including complete servicing of blower, clearance check, timing setting cleaning of filter, overhauling of motor, replacing the gland packing etc as required including transportation charges and any other incidental charges complete as required.(1 job= 1 servicing once a year) ABL Blower (Model 1450) and Kirloskar Motor ( Model 1542J) | 2.00 | Job |  | 6665.00 | 13330.00 | 2000.00 | 4000.00 | 12000.00 | 24000.00 | 7742.00 | 15484.00 | 4000.00 | MPC ELECTRICALS AND ENGINEERS
105.00 | Servicing of following pumps at STP installed at CISF Barrack including overhauling, replacing the gland packing etc as required(1 job= servicing of all pumps below once in a year ) a) Sewage Pump – 1HP, make : Kirloskar – 2 Nos b) Filter Feed Pump – 1HP, make : Kirloskar – 2 Nos d) Back Wash Pump - 1HP, Make : Kirloskar – 2 Nos e) Treated Water Pump - 0.75HP, Make : ATEXON - 1 Nos | 2.00 | Job |  | 15552.00 | 31104.00 | 7100.00 | 14200.00 | 9000.00 | 18000.00 | 9194.00 | 18388.00 | 14200.00 | MPC ELECTRICALS AND ENGINEERS
106.00 | Replacement of media for pressure sand filter ( Capacity :1000 LPH @ 2-3.5 kg/Sq.m), MOC of which is FRP, top opening type of dia 330 mm and height 1380 mm including, removing the old media, shifting the same to a location not more than 50 metres away, as directed by AAI, dismantling of the existing pressure sand filter from the said location after removing all pipe line connections, re-fixing the same after filling new media ( sand and silex up to70% of total height) , making all necessary piping inter connection as before, replacement of strainer, testing and commissioning of the filter to the satisfaction of the Engineer - In -Charge, AAI. | 1.00 | Job |  | 35548.00 | 35548.00 | 17000.00 | 17000.00 | 30000.00 | 30000.00 | 39183.00 | 39183.00 | 17000.00 | MPC ELECTRICALS AND ENGINEERS
107.00 | Replacement of media for pressure carbon filter ( Capacity :1000 LPH @ 2-3.5 kg/Sq.m), MOC of which is FRP, top opening type of dia 330 mm and height 1380 mm including, removing the old media, shifting the same to a location not more than 50 metres away, as directed by AAI, dismantling of the existing pressure sand filter from the said location after removing all pipe line connections, re-fixing the same after filling new media ( Activated carbon with an Iodine vlaue ≥1000, 70% of total height) , making all necessary piping inter connection as before, replacement of strainer, testing and commissioning of the filter to the satisfaction of the Engineer - In -Charge, AAI. | 1.00 | Job |  | 25550.00 | 25550.00 | 11600.00 | 11600.00 | 50000.00 | 50000.00 | 50000.00 | 50000.00 | 11600.00 | MPC ELECTRICALS AND ENGINEERS
108.00 | Supply of dosing pump of capacity 6 ltr/hr at a working pressure of 4kg/m2 with tubing connections and all accessories. | 2.00 | Job |  | 9885.00 | 19770.00 | 7100.00 | 14200.00 | 6600.00 | 13200.00 | 7473.00 | 14946.00 | 13200.00 | STERLING AND WILSON PRIVATE LIMITED
109.00 | Supply,Installation, testing and commissioning of filter feed pump of capacity 20m3/hr, 5HP, 34 meter head, monoblock type, three phase (Kirloskar/ equivalent make) at STP near airport school complete as required. | 1.00 | Job |  | 35132.00 | 35132.00 | 35000.00 | 35000.00 | 40000.00 | 40000.00 | 24126.00 | 24126.00 | 24126.00 | ABHISHEK INTEGRATIONS LIMITED
110.00 | SITC of 3 HP, three phase, submerssible type sludge pump cutter type having discharge 15m3/hr and head 34 meter with float for automatic switching ON of pump at CISF barrack STP plant complete as required. | 1.00 | Job |  | 81325.00 | 81325.00 | 53000.00 | 53000.00 | 17000.00 | 17000.00 | 84623.00 | 84623.00 | 17000.00 | STERLING AND WILSON PRIVATE LIMITED
111.00 | SITC of sewage pump 5HP, three phase, monoblock type,self priming of capacity 20 m3/hr and head 14 meter at STP near airport school complete as required as per specifications. | 2.00 | Job |  | 48448.00 | 96896.00 | 44000.00 | 88000.00 | 32000.00 | 64000.00 | 34413.00 | 68826.00 | 64000.00 | STERLING AND WILSON PRIVATE LIMITED
112.00 | Checking of following parameters through Kerala PCB enlisted agency with calibrated test equipment, including submission of test reports for the same etc. complete as required (relevant calibration certificate of equipment to be submitted) Checking exhaust emission of DG (for 7 Nos of DGs twice in a year) | 28.00 | Job |  | 1666.00 | 46648.00 | 1250.00 | 35000.00 | 1700.00 | 47600.00 | 880.00 | 24640.00 | 24640.00 | ABHISHEK INTEGRATIONS LIMITED
113.00 | Checking of following parameters through Kerala PCB enlisted agency with calibrated test equipment, including submission of test reports for the same etc. complete as required (relevant calibration certificate of equipment to be submitted) Noise level of DG ( for 7 Nos of DGs twice in a year) | 28.00 | Job |  | 2222.00 | 62216.00 | 125.00 | 3500.00 | 600.00 | 16800.00 | 250.00 | 7000.00 | 3500.00 | MPC ELECTRICALS AND ENGINEERS
114.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. ( GROUP C) | 15.00 | Each |  | 1666.00 | 24990.00 | 1070.00 | 16050.00 | 1300.00 | 19500.00 | 1089.00 | 16335.00 | 16050.00 | MPC ELECTRICALS AND ENGINEERS
115.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required a)2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 150.00 | meter |  | 273.00 | 40950.00 | 170.00 | 25500.00 | 150.00 | 22500.00 | 187.00 | 28050.00 | 22500.00 | STERLING AND WILSON PRIVATE LIMITED
116.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required a) 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 150.00 | meter |  | 283.00 | 42450.00 | 224.00 | 33600.00 | 180.00 | 27000.00 | 231.00 | 34650.00 | 27000.00 | STERLING AND WILSON PRIVATE LIMITED
117.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required a) 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 150.00 | meter |  | 352.00 | 52800.00 | 260.00 | 39000.00 | 235.00 | 35250.00 | 263.00 | 39450.00 | 35250.00 | STERLING AND WILSON PRIVATE LIMITED
118.00 | Supplying and fixing following size/ modules, PVC box alongwith modular base & cover plate for modular switches in recess etc as required. 3 Module (100mmX75mm) | 40.00 | Each |  | 259.00 | 10360.00 | 290.00 | 11600.00 | 390.00 | 15600.00 | 121.00 | 4840.00 | 4840.00 | ABHISHEK INTEGRATIONS LIMITED
119.00 | Supplying and fixing following size/ modules, PVC box alongwith modular base & cover plate for modular switches in recess etc as required. 4 Module (125mmX75mm) | 5.00 | Each |  | 318.00 | 1590.00 | 290.00 | 1450.00 | 525.00 | 2625.00 | 143.00 | 715.00 | 715.00 | ABHISHEK INTEGRATIONS LIMITED
120.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required 5/6 A switch | 25.00 | Each |  | 93.00 | 2325.00 | 143.00 | 3575.00 | 110.00 | 2750.00 | 35.00 | 875.00 | 875.00 | ABHISHEK INTEGRATIONS LIMITED
121.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required 3 Pin 5/6 A Socket Outlet | 25.00 | Each |  | 156.00 | 3900.00 | 170.00 | 4250.00 | 160.00 | 4000.00 | 81.00 | 2025.00 | 2025.00 | ABHISHEK INTEGRATIONS LIMITED
122.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 15/16 A Switch | 15.00 | Each |  | 156.00 | 2340.00 | 206.00 | 3090.00 | 190.00 | 2850.00 | 90.00 | 1350.00 | 1350.00 | ABHISHEK INTEGRATIONS LIMITED
123.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 6 pin 15/16 amp socket outlet | 15.00 | Each |  | 247.00 | 3705.00 | 260.00 | 3900.00 | 210.00 | 3150.00 | 142.00 | 2130.00 | 2130.00 | ABHISHEK INTEGRATIONS LIMITED
124.00 | Supplying and fixing piano type switch on the existing switch box/ cover including connections etc. as required 5/6A switch | 10.00 | Each |  | 84.00 | 840.00 | 44.00 | 440.00 | 150.00 | 1500.00 | 13.00 | 130.00 | 130.00 | ABHISHEK INTEGRATIONS LIMITED
125.00 | Supplying and fixing piano type switch on the existing switch box/ cover including connections etc. as required 15/16A switch | 10.00 | Each |  | 149.00 | 1490.00 | 62.00 | 620.00 | 200.00 | 2000.00 | 69.00 | 690.00 | 620.00 | MPC ELECTRICALS AND ENGINEERS
126.00 | Supplying and fixing stepped type electronic fan regulator one module on the existing switch box including connections but excluding modular plate etc. as required. | 20.00 | Each |  | 389.00 | 7780.00 | 260.00 | 5200.00 | 220.00 | 4400.00 | 187.00 | 3740.00 | 3740.00 | ABHISHEK INTEGRATIONS LIMITED
127.00 | Supply and fixing of SMC loop in loop out box of inside dimension 240 X 130 X 95 ( equivalent to Sintex make model No.GS-JB-2817) including suitable 20 A 4 way connector and din rail etc, including making required interconnections as required. | 35.00 | Each |  | 1639.00 | 57365.00 | 620.00 | 21700.00 | 1100.00 | 38500.00 | 2306.00 | 80710.00 | 21700.00 | MPC ELECTRICALS AND ENGINEERS
128.00 | Supplying and fixing of 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5.00 | Each |  | 1801.00 | 9005.00 | 1520.00 | 7600.00 | 2500.00 | 12500.00 | 1388.00 | 6940.00 | 6940.00 | ABHISHEK INTEGRATIONS LIMITED
129.00 | Earthing with GI earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal and salt as required. | 6.00 | Each |  | 12983.00 | 77898.00 | 6200.00 | 37200.00 | 18000.00 | 108000.00 | 11704.00 | 70224.00 | 37200.00 | MPC ELECTRICALS AND ENGINEERS
130.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 100.00 | meter |  | 56.00 | 5600.00 | 26.00 | 2600.00 | 40.00 | 4000.00 | 26.00 | 2600.00 | 2600.00 | MPC ELECTRICALS AND ENGINEERS, ABHISHEK INTEGRATIONS LIMITED
131.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | meter |  | 221.00 | 11050.00 | 206.00 | 10300.00 | 170.00 | 8500.00 | 160.00 | 8000.00 | 8000.00 | ABHISHEK INTEGRATIONS LIMITED
132.00 | Supply of capacitor duty contactors suitable for 50 Kvar, 440 V 3 phase, 50 Hz with coil voltage 240 V 50 Hz equivalent to l&T make MO C50 model with cat,no, CS96324. | 5.00 | Each |  | 8887.00 | 44435.00 | 3500.00 | 17500.00 | 4400.00 | 22000.00 | 9434.00 | 47170.00 | 17500.00 | MPC ELECTRICALS AND ENGINEERS
133.00 | Supply of capacitor duty contactors suitable for 25 Kvar, 440 V 3 phase, 50 Hz with coil voltage 240 V 50 Hz equivalent to l&T make MO C25 model with cat,no, CS96322. | 5.00 | Each |  | 3333.00 | 16665.00 | 2300.00 | 11500.00 | 2800.00 | 14000.00 | 3421.00 | 17105.00 | 11500.00 | MPC ELECTRICALS AND ENGINEERS
134.00 | Excavation for cable trenches of depth upto 1.2 m in soft soil including getting out the excavated soil and disposal of surplus excavated soil as directed within a leadof 50 meters. | 100.00 | cum |  | 1540.00 | 154000.00 | 260.00 | 26000.00 | 950.00 | 95000.00 | 1337.00 | 133700.00 | 26000.00 | MPC ELECTRICALS AND ENGINEERS
135.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meters in width, and lift upto 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 20.00 | cum |  | 222.00 | 4440.00 | 920.00 | 18400.00 | 1400.00 | 28000.00 | 1337.00 | 26740.00 | 4440.00 | Blue Star Limited
136.00 | Providing and fixing following rating, breaking capacity and adjustable thermal setting MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. 3 pole, 100 Amp, 415V, 50Hz, 25KA | 1.00 | Each |  | 5999.00 | 5999.00 | 2600.00 | 2600.00 | 7000.00 | 7000.00 | 5445.00 | 5445.00 | 2600.00 | MPC ELECTRICALS AND ENGINEERS
137.00 | Providing and fixing following rating, breaking capacity and adjustable thermal setting MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. 3 pole, 32Amp, 415V, 50Hz, 10KA | 1.00 | Each |  | 2999.00 | 2999.00 | 1700.00 | 1700.00 | 3100.00 | 3100.00 | 3037.00 | 3037.00 | 1700.00 | MPC ELECTRICALS AND ENGINEERS
138.00 | Supply of Digital time switch ( Equivalent to L&T make CAT NO. 67DDT0 ) | 10.00 | Each |  | 1689.00 | 16890.00 | 1910.00 | 19100.00 | 2500.00 | 25000.00 | 2035.00 | 20350.00 | 16890.00 | Blue Star Limited
139.00 | Supplying, drawing following sizes of FR PVC insulated copper conductor, three core cable in the existing surface/ recessed steel/ PVC conduit/uderground pipe as required. 3 x 1.5 sq. mm | 200.00 | meter |  | 122.00 | 24400.00 | 80.00 | 16000.00 | 120.00 | 24000.00 | 79.00 | 15800.00 | 15800.00 | ABHISHEK INTEGRATIONS LIMITED
140.00 | Supplying, drawing following sizes of FR PVC insulated copper conductor, four core cable in the existing surface/ recessed steel/ PVC conduit/uderground pipe as required. 4 x 1.5 sq. mm | 100.00 | meter |  | 139.00 | 13900.00 | 116.00 | 11600.00 | 135.00 | 13500.00 | 96.00 | 9600.00 | 9600.00 | ABHISHEK INTEGRATIONS LIMITED
141.00 | Supplying, drawing following sizes of FR PVC insulated copper conductor, four core cable in the existing surface/ recessed steel/ PVC conduit/uderground pipe as required. 4 x 4 sq. mm | 200.00 | meter |  | 267.00 | 53400.00 | 206.00 | 41200.00 | 250.00 | 50000.00 | 207.00 | 41400.00 | 41200.00 | MPC ELECTRICALS AND ENGINEERS
142.00 | Supply, installation, testing and commissioning of Solar powered red & green colour blinking traffic lights of 4w,300 mm dia suitable for working 24 hours including for mounting on 1.5m pole including supplying ,installing, providing of pole, customized traffic light receiver controller, Long range transmitter, Button box, Battery set & Solar panel required capacity, having 2 day autonomy and connection including painting of pole including provision for wireless control for switching on & off for a distance of 1.5-2 km complete as required | 1.00 | Job |  | 31660.00 | 31660.00 | 161000.00 | 161000.00 | 30000.00 | 30000.00 | 32945.00 | 32945.00 | 30000.00 | STERLING AND WILSON PRIVATE LIMITED
143.00 | Supply, installation, testing and commissioning of Solar powered red colour blinking traffic lights of 4w,300 mm dia suitable for working 24 hours including for mounting on 1.5m pole including supplying ,installing, providing of pole, customized traffic light receiver controller, Button box, Battery set & Solar panel required capacity, having 2 day autonomy and connection including painting of pole complete as required | 1.00 | Job |  | 22695.00 | 22695.00 | 206000.00 | 206000.00 | 30000.00 | 30000.00 | 25465.00 | 25465.00 | 22695.00 | Blue Star Limited
144.00 | Locating the cable fault like earth fault, open circuit fault etc, by means of portable fault locator including excavation, rectifying the fault, refilling etc complete as required but excluding the cost of joining kit. | 4.00 | job |  | 37750.00 | 151000.00 | 35000.00 | 140000.00 | 30000.00 | 120000.00 | 16500.00 | 66000.00 | 66000.00 | ABHISHEK INTEGRATIONS LIMITED
145.00 | Providing and laying in position cement concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) including form work etc. as required. | 30.00 | cum |  | 9565.00 | 286950.00 | 6200.00 | 186000.00 | 7000.00 | 210000.00 | 8740.00 | 262200.00 | 186000.00 | MPC ELECTRICALS AND ENGINEERS
146.00 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on wall/ surface as required. Upto 35 Sq.mm | 50.00 | meter |  | 106.00 | 5300.00 | 35.00 | 1750.00 | 50.00 | 2500.00 | 25.00 | 1250.00 | 1250.00 | ABHISHEK INTEGRATIONS LIMITED
147.00 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on wall/ surface as required. Above 35 Sq mm upto 95 Sq mm (clamped with 25X3mm MS flat clamp) | 50.00 | meter |  | 122.00 | 6100.00 | 71.00 | 3550.00 | 75.00 | 3750.00 | 30.00 | 1500.00 | 1500.00 | ABHISHEK INTEGRATIONS LIMITED
148.00 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on wall/ surface as required. Above 95 Sq.mm upto 185 Sq.mm (clamped with 25/40 X3mm MS flat clamp) | 50.00 | meter |  | 167.00 | 8350.00 | 107.00 | 5350.00 | 130.00 | 6500.00 | 35.00 | 1750.00 | 1750.00 | ABHISHEK INTEGRATIONS LIMITED
149.00 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on wall/ surface as required. Above 185 Sq mm upto 400 Sq mm | 50.00 | meter |  | 222.00 | 11100.00 | 143.00 | 7150.00 | 150.00 | 7500.00 | 40.00 | 2000.00 | 2000.00 | ABHISHEK INTEGRATIONS LIMITED
150.00 | Laying of 1 No. XLPE/PVC insulated, PVC sheathed, armoured / unarmoured aluminum/copper conductor power cable of 1.1 KV / 5 KV grade following sizes in DWC/ HDPE /Hume/ RCC metal /stone ware pipe as required.(clamped with 1mm thick saddle) Upto 35 Sq.mm | 200.00 | Meter |  | 11.00 | 2200.00 | 26.00 | 5200.00 | 50.00 | 10000.00 | 25.00 | 5000.00 | 2200.00 | Blue Star Limited
151.00 | Laying of 1 No. XLPE/PVC insulated, PVC sheathed, armoured / unarmoured aluminum/copper conductor power cable of 1.1 KV / 5 KV grade following sizes in DWC/ HDPE /Hume/ RCC metal /stone ware pipe as required.(clamped with 1mm thick saddle) Above 35 Sq mm upto 95 Sq mm | 100.00 | Meter |  | 117.00 | 11700.00 | 35.00 | 3500.00 | 75.00 | 7500.00 | 30.00 | 3000.00 | 3000.00 | ABHISHEK INTEGRATIONS LIMITED
152.00 | Laying of 1 No. XLPE/PVC insulated, PVC sheathed, armoured / unarmoured aluminum/copper conductor power cable of 1.1 KV / 5 KV grade following sizes in DWC/ HDPE /Hume/ RCC metal /stone ware pipe as required.(clamped with 1mm thick saddle) Above 95 Sq.mm upto 185 Sq.mm | 300.00 | Meter |  | 133.00 | 39900.00 | 53.00 | 15900.00 | 130.00 | 39000.00 | 35.00 | 10500.00 | 10500.00 | ABHISHEK INTEGRATIONS LIMITED
153.00 | Laying of 1 No. XLPE/PVC insulated, PVC sheathed, armoured / unarmoured aluminum/copper conductor power cable of 1.1 KV / 5 KV grade following sizes in DWC/ HDPE /Hume/ RCC metal /stone ware pipe as required.(clamped with 1mm thick saddle) Above 185 Sq mm upto 400 Sq mm | 100.00 | Meter |  | 178.00 | 17800.00 | 80.00 | 8000.00 | 150.00 | 15000.00 | 40.00 | 4000.00 | 4000.00 | ABHISHEK INTEGRATIONS LIMITED
154.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/ XLPE Al conductor cable of 1.1kV grade as required 4 C x 25 sqmm | 5.00 | set |  | 2466.00 | 12330.00 | 1700.00 | 8500.00 | 2000.00 | 10000.00 | 847.00 | 4235.00 | 4235.00 | ABHISHEK INTEGRATIONS LIMITED
155.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/ XLPE Al conductor cable of 1.1kV grade as required 3.5 C x 50 sqmm | 2.00 | set |  | 3166.00 | 6332.00 | 1700.00 | 3400.00 | 2500.00 | 5000.00 | 1045.00 | 2090.00 | 2090.00 | ABHISHEK INTEGRATIONS LIMITED
156.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/ XLPE Al conductor cable of 1.1kV grade as required 3.5 C x 70 sqmm | 2.00 | set |  | 3444.00 | 6888.00 | 2060.00 | 4120.00 | 3300.00 | 6600.00 | 1155.00 | 2310.00 | 2310.00 | ABHISHEK INTEGRATIONS LIMITED
157.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/ XLPE Al conductor cable of 1.1kV grade as required 3.5 C x 185 sqmm | 15.00 | set |  | 4999.00 | 74985.00 | 3050.00 | 45750.00 | 5000.00 | 75000.00 | 1335.00 | 20025.00 | 20025.00 | ABHISHEK INTEGRATIONS LIMITED
158.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/ XLPE Al conductor cable of 1.1kV grade as required 3.5CX240 sq.mm | 2.00 | set |  | 6443.00 | 12886.00 | 3050.00 | 6100.00 | 10000.00 | 20000.00 | 1980.00 | 3960.00 | 3960.00 | ABHISHEK INTEGRATIONS LIMITED
159.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4C x 25sqmm | 15.00 | Set |  | 1333.00 | 19995.00 | 290.00 | 4350.00 | 900.00 | 13500.00 | 416.00 | 6240.00 | 4350.00 | MPC ELECTRICALS AND ENGINEERS
160.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 C x 50 Sq.mm | 2.00 | Set |  | 1333.00 | 2666.00 | 404.00 | 808.00 | 1400.00 | 2800.00 | 483.00 | 966.00 | 808.00 | MPC ELECTRICALS AND ENGINEERS
161.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C x 70 sqmm | 2.00 | Set |  | 1333.00 | 2666.00 | 404.00 | 808.00 | 1400.00 | 2800.00 | 410.00 | 820.00 | 808.00 | MPC ELECTRICALS AND ENGINEERS
162.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C x 185 sqmm | 10.00 | Set |  | 1655.00 | 16550.00 | 800.00 | 8000.00 | 1800.00 | 18000.00 | 583.00 | 5830.00 | 5830.00 | ABHISHEK INTEGRATIONS LIMITED
163.00 | Repairing of earth pits by dismantling the existing masonry enclosure and providing RCC enclosure of 1:2:4 grade (1 cement : 2 coarse sand : 4 graded stone) and reinforced with steel rods 8mm dia in a pattern approved by AAI, providing hinged MS cover of minimum 8 mm thickness with suitable locking system as per specifications including, painting the earth pit portion above ground and cover plate, numbering the same, providing and fixing suitable funnel, removing of debris etc. as per the direction of EIC. | 15.00 | Job |  | 6665.00 | 99975.00 | 2600.00 | 39000.00 | 14000.00 | 210000.00 | 3500.00 | 52500.00 | 39000.00 | MPC ELECTRICALS AND ENGINEERS
164.00 | Repairing of 11kV HT yard structure complete with the following works as required Supply and fixing of 11kV AB switch including dismantling the existing AB switch with required nut and bolts(1 job=1 set of AB switch) | 2.00 | job |  | 27994.00 | 55988.00 | 17000.00 | 34000.00 | 10000.00 | 20000.00 | 14000.00 | 28000.00 | 20000.00 | STERLING AND WILSON PRIVATE LIMITED
165.00 | Repairing of 11kV HT yard structure complete with the following works as required Supply and fixing of 11kV lightning arrestor including dismantling the existing lightning arrestor with required nut, bolts and jumpers(1 job=1 set of arrestors) | 2.00 | job |  | 3666.00 | 7332.00 | 3500.00 | 7000.00 | 5000.00 | 10000.00 | 3175.00 | 6350.00 | 6350.00 | ABHISHEK INTEGRATIONS LIMITED
166.00 | Repairing of 11kV HT yard structure complete with the following works as required Supply and fixing of 200 A Drop out fuse including dismantling the existing DO fuse with required jumpers(1 job=1 set of DO fuse) | 2.00 | job |  | 4444.00 | 8888.00 | 4400.00 | 8800.00 | 4000.00 | 8000.00 | 3450.00 | 6900.00 | 6900.00 | ABHISHEK INTEGRATIONS LIMITED
167.00 | Painting of HIRL/MIRL Light fittings installed at runway at Calicut Airport with PU paint of aviation yellow colour (2 coats) of approved brand as required after removing dirt and grease. | 500.00 | Job |  | 377.00 | 188500.00 | 62.00 | 31000.00 | 190.00 | 95000.00 | 100.00 | 50000.00 | 31000.00 | MPC ELECTRICALS AND ENGINEERS
168.00 | Painting of Approach Light fittings installed at runway at Calicut International Airport with PU paint of aviation yellow colour (2 coats), approved brand as required after removing dirt and grease. | 30.00 | Job |  | 450.00 | 13500.00 | 62.00 | 1860.00 | 200.00 | 6000.00 | 170.00 | 5100.00 | 1860.00 | MPC ELECTRICALS AND ENGINEERS
169.00 | Painting of PAPI Light fittings installed at runway at Calicut International Airport with PU paint of aviation yellow colour (2 coats), approved brand as required after removing dirt and grease. | 8.00 | Job |  | 533.00 | 4264.00 | 710.00 | 5680.00 | 1000.00 | 8000.00 | 150.00 | 1200.00 | 1200.00 | ABHISHEK INTEGRATIONS LIMITED
170.00 | Painting of Landing 'T' Light fittings installed at runway at Calicut International Airport with PU paint of aviation yellow colour (2 coats), approved brand as required after removing dirt and grease. | 1.00 | Job |  | 3340.00 | 3340.00 | 1520.00 | 1520.00 | 2000.00 | 2000.00 | 1700.00 | 1700.00 | 1520.00 | MPC ELECTRICALS AND ENGINEERS
171.00 | Supplying and installing following size of perforated painted with powder coating G.I. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 300 mm width x 50 mm depth x 1.6 mm thickness | 100.00 | meter |  | 1366.00 | 136600.00 | 920.00 | 92000.00 | 1100.00 | 110000.00 | 1619.00 | 161900.00 | 92000.00 | MPC ELECTRICALS AND ENGINEERS
172.00 | Hiring of Hydraulic Earth mover/Excavator complete with driver and fuel for levelling, digging and other earth work required for cabling etc. | 100.00 | hour |  | 1656.00 | 165600.00 | 1520.00 | 152000.00 | 1200.00 | 120000.00 | 900.00 | 90000.00 | 90000.00 | ABHISHEK INTEGRATIONS LIMITED
173.00 | Supply of ELANTAS compound of weight 25kg along with ELANTAS hardner (758) 1 Kg | 10.00 | Set |  | 11487.00 | 114870.00 | 12500.00 | 125000.00 | 14000.00 | 140000.00 | 14520.00 | 145200.00 | 114870.00 | Blue Star Limited
174.00 | Supply of AC Surge Protection Device AC SPD (Type 2),Make : GEHE voltage :690V Cartridge without base Part code 0926910483 suitable for Delta make Inverter | 10.00 | Each |  | 3219.00 | 32190.00 | 2600.00 | 26000.00 | 2800.00 | 28000.00 | 2691.00 | 26910.00 | 26000.00 | MPC ELECTRICALS AND ENGINEERS
175.00 | Supply of DC Surge Protection Device SPD (Type 2) Make : GEHE Voltage :1120V, Cartridge without base Part code 921022783 suitable for Delta make Inverter | 50.00 | Each |  | 3219.00 | 160950.00 | 2600.00 | 130000.00 | 3200.00 | 160000.00 | 2794.00 | 139700.00 | 130000.00 | MPC ELECTRICALS AND ENGINEERS
176.00 | Supply of Halogen lamp 150W (OSRAM, 64631 HLX-Z 150W-15 PK30D or equivalent) suitable for use in runway edge light fitting or equivalent in approved makes of AAI | 100.00 | Each |  | 1122.00 | 112200.00 | 1070.00 | 107000.00 | 1500.00 | 150000.00 | 1089.00 | 108900.00 | 107000.00 | MPC ELECTRICALS AND ENGINEERS
177.00 | Supply of Halogen lamp 200 W (OSRAM, 64382 HLX-C 200W 6.6A PK30D or equivalent, ) suitable for use in Runway Edge Light fitting or equivalent in approved makes of AAI | 100.00 | Each |  | 1122.00 | 112200.00 | 530.00 | 53000.00 | 1550.00 | 155000.00 | 1210.00 | 121000.00 | 53000.00 | MPC ELECTRICALS AND ENGINEERS
178.00 | Supply of 105 W, 6.6 A, halogen lamp used for runway edge inset type fittings ( Make : Osram Cat No. 64339C/ NARVA MODEL 6108 or equivalent in list of approved makes of AAI) | 60.00 | Each |  | 1122.00 | 67320.00 | 1520.00 | 91200.00 | 1070.00 | 64200.00 | 1018.00 | 61080.00 | 61080.00 | ABHISHEK INTEGRATIONS LIMITED
179.00 | Supply of 200 watts 20/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 5.00 | Each |  | 5366.00 | 26830.00 | 4400.00 | 22000.00 | 1200.00 | 6000.00 | 4400.00 | 22000.00 | 6000.00 | STERLING AND WILSON PRIVATE LIMITED
180.00 | Supply of 200 watts 6.6/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 5.00 | Each |  | 5097.00 | 25485.00 | 4400.00 | 22000.00 | 1200.00 | 6000.00 | 4400.00 | 22000.00 | 6000.00 | STERLING AND WILSON PRIVATE LIMITED
181.00 | Supply of 150 watts 20/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 10.00 | Each |  | 4829.00 | 48290.00 | 4400.00 | 44000.00 | 1000.00 | 10000.00 | 4345.00 | 43450.00 | 10000.00 | STERLING AND WILSON PRIVATE LIMITED
182.00 | Supply of 100 watts 6.6/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 5.00 | Each |  | 4152.00 | 20760.00 | 4400.00 | 22000.00 | 900.00 | 4500.00 | 3960.00 | 19800.00 | 4500.00 | STERLING AND WILSON PRIVATE LIMITED
183.00 | Supply of 65 watts 6.6/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 10.00 | Each |  | 3777.00 | 37770.00 | 3500.00 | 35000.00 | 800.00 | 8000.00 | 3905.00 | 39050.00 | 8000.00 | STERLING AND WILSON PRIVATE LIMITED
184.00 | Supply of 45watts, 20/6.6 amps rating, 5KV grade, 50 Hz isolating transformer series type encapsulated in polyester resin finally moulded in neoprene type rubber with primary & secondary connections and confirming to the enclosed particular specifications. | 5.00 | Each |  | 3363.00 | 16815.00 | 4400.00 | 22000.00 | 600.00 | 3000.00 | 2915.00 | 14575.00 | 3000.00 | STERLING AND WILSON PRIVATE LIMITED
185.00 | Supply of 180° inner perismatic lenses (filter) - for Ema make REL (R-2150) elevated Runway fitting a) Supply of Filter 180° - yellow | 10.00 | Each |  | 2166.00 | 21660.00 | 3230.00 | 32300.00 | 10500.00 | 105000.00 | 2448.00 | 24480.00 | 21660.00 | Blue Star Limited
186.00 | Supply of SCR Ruttonsha make model 250RK160 suitable for 30KW CCR. | 6.00 | Each |  | 2306.00 | 13836.00 | 3230.00 | 19380.00 | 2500.00 | 15000.00 | 2365.00 | 14190.00 | 13836.00 | Blue Star Limited
187.00 | Supply of EMCO make model EE301-E automatic voltage regulating relay suitable for on-load tap changer | 2.00 | Each |  | 19441.00 | 38882.00 | 11600.00 | 23200.00 | 10500.00 | 21000.00 | 15950.00 | 31900.00 | 21000.00 | STERLING AND WILSON PRIVATE LIMITED
| Total in Figures |  |  |  |  | 32087786.00 |  | 27038435.00 |  | 29950109.00 |  | 28346312.00
Lowest Amount Quoted BY: MPC ELECTRICALS AND ENGINEERS(27038435.00)

## BOQ Summary
BOQ Summary Details Tender Title: Facility Management of E and M Installations area at Calicut International Airport during 2024_2026 Tender ID: 2024_AAI_197477_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | MPC ELECTRICALS AND ENGINEERS | 27038435.00 | L1
| 2 | ABHISHEK INTEGRATIONS LIMITED | 28346312.00 | L2
| 3 | STERLING AND WILSON PRIVATE LIMITED | 29950109.00 | L3
| 4 | Blue Star Limited | 32087786.00 | L4