## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 08-Jul-2024 01:12 PM Tender Title: Miscellaneous Electrical Works at Maharana Pratap Airport, Udaipur Tender ID: 2024_AAI_197671_1
Tender Inviting Authority: SM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: Miscellaneous Electrical Works at Maharana Pratap Airport, Udaipur.
Contract No: AAI/UDR/ENGG(E)/2024-25/MISC
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | QUICK CONTROL (GSTN-24AEXPP3444E1Z9) BID ID -714031 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -714549 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -714823
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 3 phase , 415 V , double door compartmentalized type having IP 54 protection outdoor PTTA LT Panel made out of 2 mm thick CRCA sheet steel suitable for 415 V, 3 phase, 4 wire, 50 Hz AC supply system with following switchgears and accessories : 1. Incomer : MCCB - 150 A, 4 P, 25 kA, Icu = 100% Ics with ROH - 2 no. (Mechanically interlocked). 2. Out goings: MCB - 63 A , FP - 3 nos. MCB - 32 A , FP - 13 nos. MCB - 25 A , SP - 4 nos. Space provision for two nos. of 4P MCCBs 3. Al. Bus Bars 300 A - 1 Set 4. Contactor - Timer (Astronomical time switch) assembly of suitable rating for on/off of street lighting ,A/M selector switch , on/off push buttons for manual operation etc. - 1 Set. 5.Accessories - RYB indication lamps for i/c MCCB - 2 sets. 6. Miscellaneous - Neutral link and earth bar etc. [Job includes: dismantling old LT Panel and installing new LT Panel complete as required.] | 1.00 | Each | 0.00 | 385500.00 | 385500.00 | 125000.00 | 125000.00 | 220000.00 | 220000.00 | 125000.00 | Yash Energy Pvt. Ltd
2.00 | SITC of 3 phase , 415 V , double door compartmentalized type having IP 54 protection outdoor PTTA LT Panel made out of 2 mm thick CRCA sheet steel suitable for 415 V, 3 phase, 4 wire, 50 Hz AC supply system with following switchgears and accessories : 1. Incomer : MCCB - 150 A, FP, 25 kA, Icu = 100% Ics with ROH - 2 no. (Mechanically interlocked). 2. Out goings: MCB - 63 A , FP - 8 nos. MCB - 32 A , FP - 15 nos. Space provision for two nos. of 4P MCCBs 3. Al. Bus Bars 300 A - 1 Set 4.Contactor - Timer (Astronomical time switch) assembly of suitable rating for on/off of street lighting ,A/M selector switch , on/off push buttons for manual operation etc. - 1 Set. 5.Accessories - RYB indication lamps for i/c MCCB - 2 sets. 6. Miscellaneous - Neutral link and earth bar etc. [Job includes: dismantling old LT Panel and installing new LT Panel complete as required.] | 1.00 | Each | 0.00 | 395599.00 | 395599.00 | 120000.00 | 120000.00 | 150000.00 | 150000.00 | 120000.00 | Yash Energy Pvt. Ltd
3.00 | Supply of 4 x 10 sqmm, 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, aluminum conductor power cable conform to IS 7098 (part -1) with up to date amendments etc complete as required. | 200.00 | Meter | 0.00 | 174.00 | 34800.00 | 160.00 | 32000.00 | 180.00 | 36000.00 | 32000.00 | Yash Energy Pvt. Ltd
4.00 | Supply of 4 x 16 sqmm, 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, aluminum conductor power cable conform to IS 7098 (part -1) with up to date amendments etc complete as required. | 200.00 | Meter | 0.00 | 208.00 | 41600.00 | 200.00 | 40000.00 | 210.00 | 42000.00 | 40000.00 | Yash Energy Pvt. Ltd
5.00 | Supply of 4 x 25 sqmm, 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, aluminum conductor power cable conform to IS 7098 (part -1) with up to date amendments etc complete as required. | 100.00 | Meter | 0.00 | 255.00 | 25500.00 | 250.00 | 25000.00 | 240.00 | 24000.00 | 24000.00 | Manish Electricals
6.00 | Supply of flat 3 core 6 sqmm, 1.1 KV grade, PVC insulated, PVC sheathed, copper conductor flexible industrial cable for submersible pump motor conforms to IS 694 with up to date amendments etc. complete as required. | 250.00 | Meter | 0.00 | 340.00 | 85000.00 | 200.00 | 50000.00 | 280.00 | 70000.00 | 50000.00 | Yash Energy Pvt. Ltd
7.00 | Supplying and laying of 90 mm dia (OD-90 mm & ID-76 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 200.00 | Meter | 0.00 | 450.00 | 90000.00 | 250.00 | 50000.00 | 272.00 | 54400.00 | 50000.00 | Yash Energy Pvt. Ltd
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of size above 35 sq. mm and upto 95 sq. mm in the existing RCC/ HUME/ METAL / HDPE pipe as required. | 300.00 | Meter | 0.00 | 175.00 | 52500.00 | 50.00 | 15000.00 | 30.00 | 9000.00 | 9000.00 | Manish Electricals
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of size upto 35 sqmm on wall surface alongwith clamped with 1mm thick saddle complete as required. | 200.00 | Meter | 0.00 | 195.00 | 39000.00 | 40.00 | 8000.00 | 90.00 | 18000.00 | 8000.00 | Yash Energy Pvt. Ltd
10.00 | Supply of 2000 watt Fan circulator room heater with 2 heat settings and overheat protection and height adjustable stand suitable for operation on 220- 230 volt ± 10%, 50Hz single phase AC power supply complete as required. ( Make & Model : Bajaj Blow Warm Fan Room Heater or equivelent ) | 4.00 | Each | 0.00 | 3995.00 | 15980.00 | 2150.00 | 8600.00 | 4000.00 | 16000.00 | 8600.00 | Yash Energy Pvt. Ltd
11.00 | Supply of 2000 watt, 09 wave fins oil filled radiator PTC fan room heater with 3 Power Settings, thermostatic heat control and overheating safety protection suitable for operation on 230 volt ± 10%, 50Hz single phase AC power supply. ( Make & Model : Bajaj Majesty RH 9F Plus Room Heater or equivelent) | 6.00 | Each | 0.00 | 18800.00 | 112800.00 | 11000.00 | 66000.00 | 18000.00 | 108000.00 | 66000.00 | Yash Energy Pvt. Ltd
12.00 | Supply and fixing of 6.00-16 size solid tyre for existing portable DG set.(Job includes removal of existing tyre and fixing of new tyres.) | 4.00 | Each | 0.00 | 10500.00 | 42000.00 | 6500.00 | 26000.00 | 7000.00 | 28000.00 | 26000.00 | Yash Energy Pvt. Ltd
13.00 | SITC of MCCB of following capacity in existing panel having Breaking Capacity of 35~36kA and Ics=100%Icu [Job includes: removing old MCCB and installing new MCCB by alligning it with existing bus bar system, proper dressing of the cables/ wires etc. as required] 250 A, FP MCCB (Make: GE LM 250B ) | 1.00 | Each | 0.00 | 15000.00 | 15000.00 | 18000.00 | 18000.00 | 35000.00 | 35000.00 | 15000.00 | QUICK CONTROL
14.00 | SITC of MCCB of following capacity in existing panel having Breaking Capacity of 35~36kA and Ics=100%Icu [Job includes: removing old MCCB and installing new MCCB with proper dressing of the cables/ wires etc. as required] 63A, FP MCCB | 1.00 | Each | 0.00 | 13500.00 | 13500.00 | 11000.00 | 11000.00 | 8000.00 | 8000.00 | 8000.00 | Manish Electricals
15.00 | Supplying and replacement of Stainless Steel Wire Ropes (Set of 2 runs) for each existing Highmast having AISI 361, 7/19 construction, 6 mm diameter and breaking load capacity of 2 x 2350 kg under the supervision of OEM and submission of completion report by OEM. | 120.00 | Meter | 0.00 | 150.00 | 18000.00 | 300.00 | 36000.00 | 250.00 | 30000.00 | 18000.00 | QUICK CONTROL
16.00 | Supplying and replacement of 5 Core, 2.5 sqmm, ECR PCP Copper Cable for existing Highmast of height upto 20 meters. | 100.00 | Meter | 0.00 | 245.00 | 24500.00 | 300.00 | 30000.00 | 280.00 | 28000.00 | 24500.00 | QUICK CONTROL
17.00 | Supply, Installation, Testing and Commissioning of 3 Phase 415 V , 5.5 KW/7.5 HP, Vertical Multistage Centrifugal Motor pump set , Head - 98.5 m , Discharge 5.69 lps, IE3 efficiency suitable for existing hydro pneumatic general water supply system complete as per site requirement and technical specifications. (Make Grundfos , Model - CR 15-6 or equivalent) (Job includes dismantling of existing pump and installation of new pump and attachment with the existing hydro pneumatic general water supply system.) | 1.00 | Each | 0.00 | 147500.00 | 147500.00 | 125000.00 | 125000.00 | 75000.00 | 75000.00 | 75000.00 | Manish Electricals
18.00 | Supply, Installation, Testing and Commissioning of 3 Phase 415 V, 3 KW/4 HP, Vertical Multistage Centrifugal Motor pump set, Head-72.3 Mtr. , Discharge 2.7 lps IE3 efficiency suitable for existing hydro pneumatic drinking water supply system complete as required as per site requirement and technical specifications. (Make Grundfos , Model - CR 10-9 or equivalent) (Job includes dismantling of existing pump and installation of new pump and attachment with the existing hydro pneumatic general water supply system.) | 1.00 | Each | 0.00 | 115900.00 | 115900.00 | 100000.00 | 100000.00 | 52000.00 | 52000.00 | 52000.00 | Manish Electricals
19.00 | Supply, Installation, Testing and Commissioning of 3 Phase 415 V , 2.2 KW/3 HP, Vertical multistage Centrifugal Motor pump set , Head-57.2 Mtr. , Discharge 2.7 lps IE3 efficiency suitable for existing hydro pneumatic drinking water supply system complete as required as per site requirement and technical specifications. (Make Grundfos , Model - CR 10-7 or equivalent) (Job includes dismantling of existing pump and installation of new pump and attachment with the existing hydro pneumatic general water supply system.) | 1.00 | Each | 0.00 | 108800.00 | 108800.00 | 90000.00 | 90000.00 | 58000.00 | 58000.00 | 58000.00 | Manish Electricals
20.00 | Supply, Installation, Testing and Commissioning of 3 Phase 415 V , 5.5 kW (7.5 HP) , 50 Hz mono block pump set , Head : 34 metres, Discharge 10 lps suitable for water supply system along etc. complete as required as per site requirement and technical specifications. (Make Kirloskar, Model - KDI-837+ or equivalent) (Job includes dismantling of existing pump and installation of new pump) . | 3.00 | Each | 0.00 | 47000.00 | 141000.00 | 34000.00 | 102000.00 | 42000.00 | 126000.00 | 102000.00 | Yash Energy Pvt. Ltd
21.00 | Supply, Installation, Testing and Commissioning of 3 Phase 415 V , 2.2 kW (3 HP) , 50 Hz mono block pump set , Head : 22 metres, Discharge 6 lps suitable for water supply system along etc. complete as required as per site requirement and technical specifications. (Make Kirloskar, Model - KDS- 325++ or equivalent) (Job includes dismantling of existing pump and installation of new pump) . | 1.00 | Each | 0.00 | 21000.00 | 21000.00 | 24000.00 | 24000.00 | 25000.00 | 25000.00 | 21000.00 | QUICK CONTROL
22.00 | Supply, installation, testing and commissioning of 3 Phase 415 V , 5.5 kW (7.5 HP) three phase 415 V, 50 Hz open well submersible pump set, Head 52 Mtr, Discharge 2.5 lps, suitable for water supply system etc. as required as per site requirement and technical specifications. (Make Kirloskar, Model - KOS 852+ or equivalent) (Job includes dismantling of existing pump and installation of new pump) . | 2.00 | Each | 0.00 | 45000.00 | 90000.00 | 40000.00 | 80000.00 | 45000.00 | 90000.00 | 80000.00 | Yash Energy Pvt. Ltd
23.00 | Supply, installation, testing and commissioning of 3 Phase 415 V , 3.65 kW (5 HP) three phase 415 V, 50 Hz open well submersible pump set, Head 22 Mtr, Discharge 10 lps, suitable for water supply system etc. as required as per site requirement and technical specifications. (Make Kirloskar, Model - KOS-520+ or equivalent) (Job includes dismantling of existing pump and installation of new pump) . | 2.00 | Each | 0.00 | 33000.00 | 66000.00 | 32000.00 | 64000.00 | 35000.00 | 70000.00 | 64000.00 | Yash Energy Pvt. Ltd
24.00 | Supply, installation, testing and commissioning of 3 Phase 415 V , 7.5 (10 HP) three phase 415 V, 50 Hz open well submersible pump set, Head 15 Mtr, Discharge 40 lps, suitable for water supply system etc. as required as per site requirement and technical specifications. (Make Kirloskar, Model - KS-1012+ or equivalent). | 2.00 | Each | 0.00 | 49000.00 | 98000.00 | 60000.00 | 120000.00 | 50000.00 | 100000.00 | 98000.00 | QUICK CONTROL
25.00 | Supply of 3 Phase 415 V , 3.6 kW (5 HP) Stainless steel body water filled borewell submersible pumpset 6 stage suitable for 6' Dia. borewell and 2' Dia. discharge pipe for Minimum discharge of 5 lps against static head 34 Mtr. meters consisting of multistage pumps etc. as required as per technical specifications. (Make : Havells, Model : 50H6W6R6D50T or equivalent). | 1.00 | Each | 0.00 | 57000.00 | 57000.00 | 42000.00 | 42000.00 | 45000.00 | 45000.00 | 42000.00 | Yash Energy Pvt. Ltd
26.00 | Supply of 3 Phase 415 V , 5.5 kW (7.5 HP ) Stainless steel body water filled borewell submersible Motor pumpset 10 stage suitable for 6' Dia. borewell and 2' Dia. discharge pipe for Minimum discharge of 5 lps against static head 34 meters etc. as required as per technical specifications. (Make : Havells, Model : 50H6W10R6D75T or equivalent). | 3.00 | Each | 0.00 | 67000.00 | 201000.00 | 48000.00 | 144000.00 | 65000.00 | 195000.00 | 144000.00 | Yash Energy Pvt. Ltd
27.00 | Installation of upto 7.5 HP borewell Submersible pumpset including lifting of existing pumpset, lowering of new pumpset with suitable machinery up to the depth of 200 ft, Electrical connection ,Testing of pump, and submission of report to AAl etc complete as required. | 4.00 | Each | 0.00 | 9500.00 | 38000.00 | 12000.00 | 48000.00 | 4500.00 | 18000.00 | 18000.00 | Manish Electricals
28.00 | Supply, Installation, Testing and Commissioning of 5.5 kW (7.5 HP) 3 phase 415 V, 50 Hz mono block pump set , Head : 46 metres, Discharge 6 lps, suitable for sewerage water complete as required as per site requirement and technical specifications. (Job includes dismantling of existing pump and installation of new pump) (Make Kirloskar, Model - KDS-852++ or equivalent). | 2.00 | Each | 0.00 | 34000.00 | 68000.00 | 35000.00 | 70000.00 | 10500.00 | 21000.00 | 21000.00 | Manish Electricals
29.00 | Supply, Installation, Testing and Commissioning of 3 phase , 415 V, 2.2 kW (3 HP) , 50 Hz mono block pump set having pipe size (Suc. x Del.) 65 x 50 mm, head : 32 metres, Discharge 6 lps suitable for Sewerage treatment plant etc. as required as per site requirement and technical specifications. (Job includes dismantling of existing pump and installation of new pump) (Make Kirloskar, Model - KDS-325++ or equivalent). | 2.00 | Each | 0.00 | 21000.00 | 42000.00 | 27500.00 | 55000.00 | 15000.00 | 30000.00 | 30000.00 | Manish Electricals
30.00 | Supply, Installation, Testing and Commissioning of 2.2 kW (3.0 HP) three phase 415 V, 50 Hz, self-priming mono block pump set having pipe size (Suc. x Del.) 50 x 50 mm, solid handling size : 10.5 mm, head : 16.5 metres, Discharge 6 lps suitable for sewerage treatment plant etc. as required as per site requirement and techncial specifications. (Make Kirloskar, Model - SP 2HM or equivalent) (Job includes dismantling of existing pump and installation of new pump). | 4.00 | Each | 0.00 | 40500.00 | 162000.00 | 30000.00 | 120000.00 | 20000.00 | 80000.00 | 80000.00 | Manish Electricals
31.00 | Supply of Single Phase , 230 V , 50 Hz , 1.1 kW (2 HP) dewatering mud pump set.(Make : Kirloskar, Model : KDS 235+ or equivalent). | 2.00 | Each | 0.00 | 26000.00 | 52000.00 | 22500.00 | 45000.00 | 45000.00 | 90000.00 | 45000.00 | Yash Energy Pvt. Ltd
32.00 | Providing 50 mm dia threaded GI pipe ( Class C ) with socket and lowering in the borewell with suitable machinery for Submersible bore well pump sets. | 250.00 | Meter | 0.00 | 960.00 | 240000.00 | 550.00 | 137500.00 | 1050.00 | 262500.00 | 137500.00 | Yash Energy Pvt. Ltd
33.00 | Providing 50 mm dia threaded GI pipe ( Class C ) with sockets , bends and laying in PCC after cutting existing PCC 150 mm wide & 300 mm deep and making good the same etc. as per site requirement. | 20.00 | Meter | 0.00 | 950.00 | 19000.00 | 400.00 | 8000.00 | 950.00 | 19000.00 | 8000.00 | Yash Energy Pvt. Ltd
34.00 | Providing 50 mm dia threaded GI pipe ( Class C ) with sockets , bends and laying on surface with suitable MS clamp as per site requirement. | 30.00 | Meter | 0.00 | 940.00 | 28200.00 | 400.00 | 12000.00 | 950.00 | 28500.00 | 12000.00 | Yash Energy Pvt. Ltd
35.00 | Supply and fixing of Starter panel suitable for 415 V AC, 50 Hz for 7.5 HP bore well Submersible pump set including protection/prevention from single phasing & overload , push buttons for ON/OFF operation and control MCB etc complete as required with dust & vermin proof outdoor, IP 65, cubical box i/c providing suitable mounting arrangement of MS angles of required height and painted after applying red oxide , grouted in ground etc. complete as per site requirement. | 4.00 | Each | 0.00 | 18500.00 | 74000.00 | 14000.00 | 56000.00 | 10500.00 | 42000.00 | 42000.00 | Manish Electricals
36.00 | Supply and fixing of Star Delta Starter panel suitable for 415 V AC, 50 Hz for 10 HP Open well Submersible pump set including protection/prevention from single phasing & overload , push buttons for ON/OFF operation and control MCB etc complete as required with dust & vermin proof outdoor, IP 65, cubical box i/c providing suitable mounting arrangement of MS angles of required height and painted after applying red oxide , grouted in ground etc. complete as per site requirement. | 2.00 | Each | 0.00 | 25500.00 | 51000.00 | 24000.00 | 48000.00 | 8500.00 | 17000.00 | 17000.00 | Manish Electricals
37.00 | Supply and fixing of Star delta Starter panel suitable for 415 V AC, 50 Hz for 7.5 HP monoblock pump set with single phasing & overload protection, push buttons for ON/OFF operation and control MCB etc complete as required. | 2.00 | Each | 0.00 | 18500.00 | 37000.00 | 11000.00 | 22000.00 | 11000.00 | 22000.00 | 22000.00 | Yash Energy Pvt. Ltd, Manish Electricals
38.00 | Supply and fixing of DOL Starter panel suitable for 415 V AC, 50 Hz for upto 7.5 HP Mono block pumps/Openwell submersible pumps set with overload protection push buttons for ON/OFF operation and control MCB etc complete as required. | 12.00 | Each | 0.00 | 18500.00 | 222000.00 | 4000.00 | 48000.00 | 4000.00 | 48000.00 | 48000.00 | Yash Energy Pvt. Ltd, Manish Electricals
39.00 | Supply, installation, testing and commissioning of water cooler stainless steel tank 304 grade of 80 Litres storage capacity and 60 Litres cooling capacity with 3 stage purification to combine RO and UV technology with Cold & Normal options and mounting arrangement etc. complete as required as per technical specifiations. (Aquaguard Pro Pure Chill 80 SS RO + UV or equivalent). | 2.00 | Each | 0.00 | 60000.00 | 120000.00 | 85000.00 | 170000.00 | 85000.00 | 170000.00 | 120000.00 | QUICK CONTROL
40.00 | Supply, Installation, Testing and Commissioning of butterfly valve PN 1.6, with Bronze/Gunmetal seat duly ISI marked complete with Nuts, Bolts, washers, gaskets, conforming to IS 13095, of 50 mm dia sizes complete as required at site. | 10.00 | Each | 0.00 | 4800.00 | 48000.00 | 5000.00 | 50000.00 | 9000.00 | 90000.00 | 48000.00 | QUICK CONTROL
41.00 | Supply, Installation, Testing and Commissioning of Non - Return valve with duel plate of CI body SS plate vulcanized NBR seal flanged end & PN 1.6 pressure rating including insulation as specified complete as required at site. 50 mm dia. | 12.00 | Each | 0.00 | 9250.00 | 111000.00 | 2000.00 | 24000.00 | 9000.00 | 108000.00 | 24000.00 | Yash Energy Pvt. Ltd
42.00 | Supply installation testing and commissioning of industrial type RO water purifier consisting of raw water pump, particulate filter (10 Micron, 4"x20"), activated carbon block (4"x20"), Micron cartridge filter (5 Micron, 4"x20"), anti scalant dosing system, high pressure pump SS 304 - 1.1 kW, pressure tube, RO membrane 4040, Microprocessor based control panel with provision of high and low pressure safeties, water level sensors, CPVC piping, online Rota meter, Pressure guages PU coated MS powder coated skid including other minor accessories for raw water with TDS up to 3000 PPM i/c. attachment with existing water cooler. | 2.00 | Each | 0.00 | 42500.00 | 85000.00 | 150000.00 | 300000.00 | 15000.00 | 30000.00 | 30000.00 | Manish Electricals
43.00 | SITC of drinking Water fountain system consisting of dual bubbler and single bottle filler in SS 304 construction i/c pressure boosting unit for each bubbler complying with guidelines issued by DPEwD and confirming to technical specifications. (Make: OASIS, Model: MCRSBFY or equivalent). | 1.00 | Each | 0.00 | 135000.00 | 135000.00 | 155000.00 | 155000.00 | 18000.00 | 18000.00 | 18000.00 | Manish Electricals
44.00 | Supply & fixing of Grade 304 SS water tank made out of 2 mm thick sheet with threaded lid and storage capacity 500 ltr including Pressure switch and solenoid valve with suitable DC power supply to disconnect inlet water supply on tank filling, level indicator and locking arrangement etc. for treated water storage ect. complete as site requirement. | 2.00 | Each | 0.00 | 69500.00 | 139000.00 | 18000.00 | 36000.00 | 18000.00 | 36000.00 | 36000.00 | Yash Energy Pvt. Ltd, Manish Electricals
45.00 | Supply and fixing MS stand for raw water storage tank of suitable height with legs having height suitably above RO water purifier unit and suitable dimensions MS sheet of thickness not less than 2 mm etc. complete as required. | 2.00 | Each | 0.00 | 6500.00 | 13000.00 | 10000.00 | 20000.00 | 2000.00 | 4000.00 | 4000.00 | Manish Electricals
46.00 | Supply of Aluminum Economical Telescopic Wheeled Ladder of Closed height 12 ft. , Extended height 20 ft , sides made of Aluminum ‘I’ Shape Channel 75x35x3.5 mm and steps made of Aluminum 26 mm dia round corrugated tubing, having Pushing handle, 2 No. Wheels, Rubber shoes at bottom end and top & Side railing and fitted with safety ring and platform on the top ,etc. complete as required. (Make : Sumer or equivalent) | 1.00 | Each | 0.00 | 23500.00 | 23500.00 | 65000.00 | 65000.00 | 135000.00 | 135000.00 | 23500.00 | QUICK CONTROL
47.00 | Supply of Aluminum Stool type folding ladder (Heavy duty) of height 8 ft. ,sides - Al. Channel C shaped section 75x35x3.5 mm , Aluminum steps of size 63 mm wide, Platform size of 16"x12" on top , Botton end with non slippery rubber pad. (Make : Sumer or equivalent). | 1.00 | Each | 0.00 | 4450.00 | 4450.00 | 25000.00 | 25000.00 | 35000.00 | 35000.00 | 4450.00 | QUICK CONTROL
48.00 | Supply of platform type trolley of 1 ton capacity with 04 no. High quality rubber wheels of dia. 8" and safety lock , Platform length 5 ft. Platform width 3 ft.etc. complete as required. (Make : Sumer or equivalent). | 2.00 | Each | 0.00 | 43500.00 | 87000.00 | 16000.00 | 32000.00 | 30000.00 | 60000.00 | 32000.00 | Yash Energy Pvt. Ltd
49.00 | Supply of Box Trolley with Pushing handle of capacity 1 Ton with Platform length 5 ft, Platform width 3 ft., 4 no. high quality rubber wheels 8 ". (Make : Sumer or equivalent). | 1.00 | Each | 0.00 | 55000.00 | 55000.00 | 15000.00 | 15000.00 | 45000.00 | 45000.00 | 15000.00 | Yash Energy Pvt. Ltd
50.00 | Brick work with common burnt clay FPS (non modular) brickes of class designation 7.5 above for foundation of Pump sets at various locations as per requirement. | 5.00 | Cum | 0.00 | 10000.00 | 50000.00 | 3500.00 | 17500.00 | 16000.00 | 80000.00 | 17500.00 | Yash Energy Pvt. Ltd
| Total in Figures |  |  |  |  | 4341629.00 |  | 3130600.00 |  | 3201400.00
Lowest Amount Quoted BY: Yash Energy Pvt. Ltd(3130600.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Electrical Works at Maharana Pratap Airport, Udaipur Tender ID: 2024_AAI_197671_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Yash Energy Pvt. Ltd | 3130600.00 | L1
| 2 | Manish Electricals | 3201400.00 | L2
| 3 | QUICK CONTROL | 4341629.00 | L3