## BoQ1
Government eProcurement System Created By: Ambrish Singh Created Date/Time: 19-Jul-2024 11:29 AM Tender Title: Construction of ASR MSSR Building at LBSI Airport, Varanasi. SH- Substation and Allied Works. Tender ID: 2024_AAI_197932_1
Tender Inviting Authority: Asstt. General Manager (Engg.-E), LBSI Airport Varanasi.
Name of Work: Construction of ASR/MSSR Building at LBSI Airport, Varanasi. SH :- Substation and Allied Works.
Contract No: 2024_AAI_197932_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Naagar Infrastructure Pvt Ltd (GSTN-07AACCN7477R1ZJ) BID ID -714791 |  | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -715312 |  | Leo Air and Power Solution Pvt Ltd., (GSTN-07AABCL1931F1ZW) BID ID -715987 |  | SAURABH ENTERPRISES(GSTN-NA)--715508 |  | Shiva Enterprises(GSTN-NA)--716144
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I : SITC of T/F, DG sets, Shifting of DG set, HT Panel Supply, Installation, Testing & Commissioning of ONAN (Oil Immersed Natural Air Cooled)type, 250 KVA, 11 KV / 0.433 KV, 3 Phase, 50Hz, Dyn 11 vector group, copper wound class A insulation with winding temperature indicator, oil temperature indicator indoor type Transformer as per IS-1180 with up to date amendments. The transformer shall be provided with +5% to -10% in steps of 2.5 % each Off load tap changer on HT side, having cable end boxes on HV side suitable for 3C x 95 sq.mm. XLPE cable of 11 KV grade and 400 Amp.Cable box arrangement of LV side with neutral brought out separately including supplying and grouting of suitable MS channels with all accessories for mounting arrangement and confirming to relevant standard as amended up to date & as per specifications complete in all respects as required at site including any civil foundation, minor civil works as required for installation of transformer. | 2.00 | Job |  | 1430000.00 | 2860000.00 | 805000.00 | 1610000.00 | 960000.00 | 1920000.00 | 1100000.00 | 2200000.00 | 1470000.00 | 2940000.00 | 1610000.00 | DOSHI ELECTRIC ENGG. CO.
2.00 | Providing, Installation, Testing and Commissioning of CPCB IV compliant ‘Silent Type’ Diesel Generating set alongwith having Prime Power Rating of 160 kVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415V suitable for 50 Hz, 3 phase 4 wire system & for 0.85 Load Factor and consisting of the followings: Diesel Engine : Diesel engine of 4 stroke liquid cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 45 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. Engine mounted Instrument Panel fitted with and having digital display for following : (i) Start-stop switch with key. (ii) Water temperature indication. (iii) Lubrication oil pressure indication. (iv) Lubrication oil temperature indication. (v) RPM indication. (vi) Over speed indication. (vii) Low lub. Oil trip indication. (viii) Engine Hours indication. Alternator: Synchronous alternator rated at 160kVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 45 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self regulated through AVR conforming to IS:4722/BS 2613 suitable for tropical conditions and with class- F/H insulation. Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on existing cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. Fuel line work : Providing and Installing external service fuel tank of 990 Ltr. capacity fabricated out of 3mm thick MS sheet. Fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. up to 25 mtrs. Complete with valves, level indications & accessories as required as per specifications. Exhaust System : Dry exhaust manifold with residential exhaust silencer and catalytic convertor including exhaust piping up to 20 metres height with MS support structure with back pressure calculation etc. as per CPCB norms, lightening arrester vinial, and supplying and fixing of GI strip on MS support structure on insulated base up to base of structure. Starting System : 12V/24V DC starting system comprising of starter motors, voltage regulator and arrangement for initial excitation complete with suitable nos of batteries (150 AH capacity lead acid type) as required as per specifications. Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. Works includes complete SITC Job including required works as per O.E.M guidelines like providing & fixing C channel etc. complete in all respects as required at site. | 1.00 | Job |  | 1620000.00 | 1620000.00 | 2280000.00 | 2280000.00 | 1880000.00 | 1880000.00 | 1300000.00 | 1300000.00 | 1550000.00 | 1550000.00 | 1300000.00 | SAURABH ENTERPRISES
3.00 | Dismantling, shifting, installation, testing & commsissioning of existing 11 kV VCB breaker type HT panel of make - Megawin with 01 Incomer panel & 02 Nos. Outgoing panels including proper dismantling of panels, cable terminations, earth strips, etc. using suitable machinery as required & shifting to new location i.e. New MSSR Power House (inside operational area approx distance 1 km) by using sufficient size Hydra Machines i/c loading and unloading at designated place with all the required suitable tools/machinery, without any damages to HT panel and its components complete as required. The dismantling is to be done in such a way so the same equipments can be installed at New Location for proper utilization. Item also includes re-assembling, installation, testing & commissioning of the shifted HT panel at New MSSR Power House. The commissioning has to be carried out through OEM & as per OEM recommendations. | 1.00 | Job |  | 45000.00 | 45000.00 | 40000.00 | 40000.00 | 57500.00 | 57500.00 | 55000.00 | 55000.00 | 40000.00 | 40000.00 | 40000.00 | DOSHI ELECTRIC ENGG. CO., Shiva Enterprises
4.00 | Dismantling & shifting of existing silent type Greaves make 160 KVA DG set assembly including dismantling of canopy (enclosure), cable terminations, batteries, earth strips, silencer , exhaust piping, insulation, cladding of exhaust piping, fuel piping, fuel tank, MS support structure of exhaust pipe and diesel tank etc. using suitable machinery, cutting as required & shifting to new location i.e. New MSSR Power House (inside operational area approx distance 1 km) by using sufficient size Hydra Machines i/c loading and unloading at designated place with all the required suitable tools/machinery, without any damages to component & equipment as required. The dismantling is to be done in such a way so the same equipments can be installed at New Location for proper utilization. | 1.00 | Job |  | 30000.00 | 30000.00 | 10000.00 | 10000.00 | 46000.00 | 46000.00 | 35000.00 | 35000.00 | 23000.00 | 23000.00 | 10000.00 | DOSHI ELECTRIC ENGG. CO.
5.00 | Installation, testing & commissioning of the shifted Greaves make 160 KVA DG set at New MSSR Substation by assembling all the parts of the DG set i/c canopy, cable connection, replacement of all the Nuts Bolts, gaskets of suitable size as required, installation of shifted fuel tank and SITC of fuel line work with suitable size dia MS class 'C' pipe between fuel tank and diesel engine complete with valves & accessories including all the connection in the existing AMF panel complete as per site requirement, installation, testing and commissioning to be done as per OEM recommendation complete with load testing as per Special Conditions of Contract. | 1.00 | Job |  | 45000.00 | 45000.00 | 20000.00 | 20000.00 | 34500.00 | 34500.00 | 45000.00 | 45000.00 | 50000.00 | 50000.00 | 20000.00 | DOSHI ELECTRIC ENGG. CO.
6.00 | Fixing of existing shifted MS support structure alongwith making of foundation of grade 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) of suitable size for exhaust fume pipes from DG Sets for bottom support along horizontal and vertical runs upto the height required for exhaust pipe, including replacment of all the nuts, bolts, washers by cutting, welding etc. and applying two coats of red oxide and two coats of synthetic enamelled paint of colour and shade as per site requirement. The support structure shall be suitable for the exhaust pipe height . Work includes all necessary civil work as directed by the EIC and as per site requirement. | 1.00 | Job |  | 65000.00 | 65000.00 | 50000.00 | 50000.00 | 57500.00 | 57500.00 | 70000.00 | 70000.00 | 50000.00 | 50000.00 | 50000.00 | DOSHI ELECTRIC ENGG. CO., Shiva Enterprises
7.00 | Laying & fixing of existing shifted MS exhaust Piping for 160 kVA D.G. Sets for Exhaust system including the bends, reducers & supporting arrangement for attaching the pipe to existing RCC /MS structure by cutting/welding, painting etc., replacment of all the nuts, bolts, washers, gasket complete as per site requirement. Nothing will be paid for any replacement of damaged MS pipe required to complete the job. | 20.00 | Metre |  | 1100.00 | 22000.00 | 1000.00 | 20000.00 | 1093.00 | 21860.00 | 3000.00 | 60000.00 | 1200.00 | 24000.00 | 20000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Providing and fixing of 50mm thick mineralwool/ glasswool/Rockwool insulation (of 46 kg per cubic meter density) around the exhaust pipes, cladding with aluminium sheet of 0.63 mm thick complete as required as per site requirement. | 10.00 | Metre |  | 1200.00 | 12000.00 | 1500.00 | 15000.00 | 1390.00 | 13900.00 | 2000.00 | 20000.00 | 3000.00 | 30000.00 | 12000.00 | Naagar Infrastructure Pvt Ltd
9.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required including required excavation in soft soil, cemented soil etc. complete as required. | 8.00 | cum |  | 5500.00 | 44000.00 | 8000.00 | 64000.00 | 5000.00 | 40000.00 | 6500.00 | 52000.00 | 4800.00 | 38400.00 | 38400.00 | Shiva Enterprises
10.00 | SH II : SITC of LT Panel Main LT Panel : Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42, indoor LT panel - type tested assembly (TTA) as per IEC 61439-1&2, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design from 2 mm thick CRCA sheet, 3 mm thick for gland plates and 1.6 mm for doors, covers & partitions i/c cleaning & finishing, complete with 7 tank process for powder coating in approved shade, TPN Aluminium alloy bus bars of high conductivity, SMC / DMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size, at the rear end with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, interlocking, earth ing i/c providing following switchgears / accessories as per specifications.: A) Incomers & Bus coupler: (a) 400 A, 50 kA, Four Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/L & S/C Protection - 3 Sets (Incomer - 2 Nos. & Bus-Coupler - 1 No.) (b) Digital KWH meter and Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display with 03 Nos of CTs, 400/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection including data logging facility (block profile 15/30 min integration up to min. 30 days) - 2 Sets. (c) Set of R, Y, B Phase indicating lamps, LED type, with 2 Amp MCB for protection. - 3 Sets. (d) Set of Indication Lamps, LED type for MCCB 'ON' , 'OFF', 'TRIP' with 02 Amps MCB for protection - 3 Sets. e) Auxiliary contacts / contactors, auxiliary relays, shunt trip etc. for interlocking of the incomer MCCBs and bus coupler MCCB as required. - 1 Set. (f) 3 Phase 4 Wire kWh Meter, CT op base mounting, Class accuracy 0.5s with 03 Nos of CTs, 400/5, 15 VA, Class 1.0 - 2 Sets. (g) Surge Protection Device - Type 1+2, 3 Pole + NPE, Imax = 50 kA, Modular Type, conforming to EN/IEC 61643-11 with 32A, FP C-Series MCB including complete connection with copper flexible cable and as per technical specifications. (OBO - V50-3+NPE-320 / L&T AUSP123PN50 or similar) - 2 Sets B) Main Busbars: TPN, high conductivity Aluminium, both sides extensible type main bus bars of minimum of 630 Amps. capacity with heat shrinkable coloured sleeves and i/c DMC / SMC bus bars cross section supports & their spacing etc. For withstanding fault level of 50 kA capacity for 1 sec. - 1 Set C) Outgoings: (a) 200 A, 36 kA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets. (b) 100 A, 36 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 3 Sets.(c) 63 A, 25 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets. (d) 40 A, 25 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 3 Sets. NOTE: a) All MCCBs shall be provided with ON, OFF & TRIP indication lamps (LED type) with 2 Amp SP MCB for protection. b) All MCCBs shall be provided with rotary operating handle and spreader terminals. | 1.00 | Job |  | 512000.00 | 512000.00 | 840000.00 | 840000.00 | 790000.00 | 790000.00 | 650000.00 | 650000.00 | 760000.00 | 760000.00 | 512000.00 | Naagar Infrastructure Pvt Ltd
11.00 | Switch Room LT Panel Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42, indoor LT panel - partially type tested assembly (PTTA) as per IEC 61439-1&2, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design from 2 mm thick CRCA sheet, 3 mm thick for gland plates and 1.6 mm for doors, covers & partitions i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, TPN Aluminium alloy bus bars of high conductivity, SMC / DMC bus bar supports, with short circuit withstand capacity of 36 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size, at the rear end with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, interlocking, earthing i/c providing following switchgears / accessories as per specifications. Cable entry top/bottom should be as approved as per site requirement. A) Incomers & Bus coupler: (a) 200 A, 36 kA, Four Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/L & S/C Protection - 3 Sets (Incomer - 2 Nos. & Bus-Coupler - 1 No.) b) Digital KWH meter and Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, KWH, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display with 03 Nos of CTs, 400/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection including data logging facility (block profile 15/30 min integration up to min. 30 days) - 2 Sets. c) Set of R, Y, B Phase indicating lamps, LED type, with 2 Amp MCB for protection. - 3 Sets. d) Set of Indication Lamps, LED type for MCCB 'ON' , 'OFF', 'TRIP' with 02 Amps MCB for protection - 3 Sets. e) Auxiliary contacts / contactors, auxiliary relays, shunt trip etc. for positive interlocking of the incomer MCCBs and bus coupler MCCB as required. - 1 Set. f) Surge Protection Device - Type 1+2, 3 Pole + NPE, Imax = 50 kA, Modular Type, conforming to EN/IEC 61643-11 with 32A, FP C-Series MCB including complete connection with copper flexible cable and as per technical specifications. (OBO - V50-3+NPE-320 / L&T AUSP123PN50 or similar) - 2 Sets B) Main Busbars: TPN, high conductivity Aluminium, both sides extensible type main bus bars of minimum of 300 Amps. capacity with heat shrinkable coloured sleeves and i/c DMC / SMC bus bars cross section supports & their spacing etc. For withstanding fault level of 36 kA capacity for 1 sec. - 1 Set C) Outgoings: (a) 100 A, 36 kA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 4 Sets. (b) 40 A, 25 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets. NOTE: a) All MCCBs shall be provided with ON, OFF & TRIP indication lamps (LED type) with 2 Amp SP MCB for protection. b) All MCCBs shall be provided with rotary operating handle and spreader terminals. | 1.00 | Job |  | 205000.00 | 205000.00 | 470000.00 | 470000.00 | 562051.00 | 562051.00 | 400000.00 | 400000.00 | 395000.00 | 395000.00 | 205000.00 | Naagar Infrastructure Pvt Ltd
12.00 | AMF LT Panel Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42, indoor LT panel - partially type tested assembly (PTTA) as per relevant IEC/IS norms, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design from 2 mm thick CRCA sheet, 3 mm thick for gland plates and 1.6 mm for doors, covers & partitions i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, TPN Aluminium alloy bus bars of high conductivity, extensible on both sides, SMC / DMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size, at the rear end with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, interlocking, earthing i/c providing following switchgears / accessories as per specifications.: a) 250 A, 50 KA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection - 2 Sets. (b) 250 A, 4 Pole Power Contactor with Aux. Contacts - 2 Nos. (c) 250 A, 4 Pole Bypass Changeover Switch to bypass Mains / DG - 01 No. (d) Protection Relays - Over Current + Earth Fault, Over Voltage, Under Voltage (Each - 2 Nos.), Reverse Power (1 No.) with CTs of suitable range - 15VA, CL-5P10 accuracy for protection as applicable. (e) LED Indication lamps for RYB (2 Sets), Load on Mains, Load on DG, DC Control ON, Battery Charger ON etc. with 2 Amp MCB for protection. (f) Digital KWH meter and Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display - 2 Nos. + Digital Ammeter, RS 485, CL-1.0, with in-built selector switch with 2 Amps MCBs for controlling and protection - 2 Nos. + 3 Nos. CTs, 300/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection. (g) Microprocessor Based Advanced AMF Control Logic Relay with Built-In DG Protection suitable for installed DG set - 1 No. (h) 12/24 V DC Control Circuit, Voltage Monitoring Relay (2 Nos), Cranking Relay, Engine Starting Relay, Aux. Relays, Timers, Aux. Contactors, Selector Switches, Push Buttons, Emergency Stop Push Button, 2 A Control MCBs as required for control / interlocking / protection & Accessories etc. as required. - 1 Set. (i) 12/24 V DC Battery Charger as per the DG set to be installed, complete with transformer / rectifier, DC Voltmeter and DC Ammeter, Selector Switch for Trickle / Off / Boost with current adjustment - 1 Set (j) 8 Window Annunciator with Push Button for Test/Accept/Reset + Hooter for indication of High Water Temperature, High/Low Lube Oil Pressure, Engine Overspeed, Engine Fails to Start, Over Current, Under / Over Voltage, Reverse Power & Earth Fault Etc. as required. - 1 Set (k) Control Cabling with 12C x 2.5 Sqmm Cu. Arm. Cable between AMF Panel and DG Set Control Unit up to 30 metres as required. NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals. | 2.00 | Job |  | 465000.00 | 930000.00 | 360000.00 | 720000.00 | 611473.00 | 1222946.00 | 400000.00 | 800000.00 | 278000.00 | 556000.00 | 556000.00 | Shiva Enterprises
13.00 | Supply, installation, testing and commissioning of Four Pole, 250 Amp, Manual On Load Changeover switch for 02 incomer 01 outgoing configuration complete with SS or as per OEM enclosure, handle etc. as required. | 1.00 | Each |  | 22000.00 | 22000.00 | 35000.00 | 35000.00 | 34253.00 | 34253.00 | 45000.00 | 45000.00 | 24700.00 | 24700.00 | 22000.00 | Naagar Infrastructure Pvt Ltd
14.00 | SITC of Automatic Transfer Switch 4P, 125A, 415V, 3 phase, 50 Hz with Bypass mechanism, totally enclosed, wall mounted, dust & vermin proof, indoor type having 2 incomer & 1 Outgoing along with detachable gland plate complete as per site requirement. | 1.00 | Each |  | 38000.00 | 38000.00 | 50000.00 | 50000.00 | 51836.00 | 51836.00 | 45000.00 | 45000.00 | 20000.00 | 20000.00 | 20000.00 | Shiva Enterprises
15.00 | SH III : Supply & Laying of HDPE pipes, Cables, Termination & Joints Supply of 3C x 95 Sqmm. size, 11 KV grade, XLPE insulated & PVC sheathed armoured aluminium conductor HT(E) cable generally conforming to IS 7098 Part II-1985 with up to date amendments as required. | 1324.00 | Metre |  | 1000.00 | 1324000.00 | 900.00 | 1191600.00 | 756.00 | 1000944.00 | 700.00 | 926800.00 | 870.00 | 1151880.00 | 926800.00 | SAURABH ENTERPRISES
16.00 | Supplying of 1.1 kV grade multicore stranded Aluminium Conductor XLPE insulated galvanised steel strip armoured & overall PVC sheathed armoured power cables as per IS: 7098 Part-I complete as required. a)3.5 X 400 Sq.mm | 2772.00 | Metre |  | 2100.00 | 5821200.00 | 2000.00 | 5544000.00 | 1692.00 | 4690224.00 | 1600.00 | 4435200.00 | 1470.00 | 4074840.00 | 4074840.00 | Shiva Enterprises
17.00 | Supplying of 1.1 kV grade multicore stranded Aluminium Conductor XLPE insulated galvanised steel strip armoured & overall PVC sheathed armoured power cables as per IS: 7098 Part-I complete as required. a) 3.5C X 185 Sq.mm | 698.00 | Metre |  | 1030.00 | 718940.00 | 1100.00 | 767800.00 | 842.00 | 587716.00 | 800.00 | 558400.00 | 750.00 | 523500.00 | 523500.00 | Shiva Enterprises
18.00 | Supply and laying of double wall corrugated high density polyethylene (DWC HDPE pipe) pipe confirming to IS:14930 (part-2) with latest amendment, complete along with 4mm nylon rope with accessories like couplers, bends, tee etc. in the soil for GLF supply/power supply work upto 750 mm deep, back filling & making good the same as per site requirement as per the direction of engineer in charge. a) 120 mm dia (OD-120 mm & ID-103 mm nominal) | 2600.00 | Metre |  | 300.00 | 780000.00 | 230.00 | 598000.00 | 291.00 | 756600.00 | 250.00 | 650000.00 | 165.00 | 429000.00 | 429000.00 | Shiva Enterprises
19.00 | Supply and laying of double wall corrugated high density polyethylene (DWC HDPE pipe) pipe confirming to IS:14930 (part-2) with latest amendment, complete along with 4mm nylon rope with accessories like couplers, bends, tee etc. in the soil for GLF supply/power supply work upto 1200 mm deep, back filling & making good the same as per site requirement as per the direction of engineer in charge. a) 90 mm dia (OD-90 mm & ID-76 mm nominal) | 1240.00 | Metre |  | 270.00 | 334800.00 | 230.00 | 285200.00 | 317.00 | 393080.00 | 200.00 | 248000.00 | 158.00 | 195920.00 | 195920.00 | Shiva Enterprises
20.00 | Supply and laying of double wall corrugated high density polyethylene (DWC HDPE pipe) pipe confirming to IS:14930 (part-2) with latest amendment, complete along with 4mm nylon rope with accessories like couplers, bends, tee etc. in the soil for GLF supply/power supply work upto 750 mm deep, back filling & making good the same as per site requirement as per the direction of engineer in charge. a) 90 mm dia (OD-90 mm & ID-76 mm nominal) | 400.00 | Metre |  | 220.00 | 88000.00 | 200.00 | 80000.00 | 260.00 | 104000.00 | 225.00 | 90000.00 | 125.00 | 50000.00 | 50000.00 | Shiva Enterprises
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV (HT) grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. Upto 120 sq. mm | 1240.00 | Metre |  | 65.00 | 80600.00 | 70.00 | 86800.00 | 58.00 | 71920.00 | 40.00 | 49600.00 | 120.00 | 148800.00 | 49600.00 | SAURABH ENTERPRISES
22.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. a) Above 95 sqmm and upto 185 sqmm | 400.00 | Metre |  | 70.00 | 28000.00 | 50.00 | 20000.00 | 70.00 | 28000.00 | 40.00 | 16000.00 | 130.00 | 52000.00 | 16000.00 | SAURABH ENTERPRISES
23.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. a) Above 185 sqmm and upto 400 sqmm | 2600.00 | Metre |  | 100.00 | 260000.00 | 60.00 | 156000.00 | 70.00 | 182000.00 | 50.00 | 130000.00 | 120.00 | 312000.00 | 130000.00 | SAURABH ENTERPRISES
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV (HT) grade of following size in the existing masonry open duct as required. Upto 120 sq. mm | 20.00 | Metre |  | 45.00 | 900.00 | 50.00 | 1000.00 | 70.00 | 1400.00 | 40.00 | 800.00 | 120.00 | 2400.00 | 800.00 | SAURABH ENTERPRISES
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. a) Above 95 sqmm and upto 185 sqmm | 260.00 | Metre |  | 60.00 | 15600.00 | 60.00 | 15600.00 | 70.00 | 18200.00 | 50.00 | 13000.00 | 120.00 | 31200.00 | 13000.00 | SAURABH ENTERPRISES
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. a) Above 185 sqmm and upto 400 sqmm | 20.00 | Metre |  | 100.00 | 2000.00 | 65.00 | 1300.00 | 70.00 | 1400.00 | 50.00 | 1000.00 | 170.00 | 3400.00 | 1000.00 | SAURABH ENTERPRISES
27.00 | Providing and laying 6 SWG dia G.I. wire in/along with HDPE/RCC/ HUME/ METAL pipe/existing trench or along with cable for loop earthing etc complete as required. | 4560.00 | Metre |  | 35.00 | 159600.00 | 20.00 | 91200.00 | 25.00 | 114000.00 | 25.00 | 114000.00 | 25.00 | 114000.00 | 91200.00 | DOSHI ELECTRIC ENGG. CO.
28.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :. a) 3 X 95 Sq.mm | 2.00 | Set |  | 4200.00 | 8400.00 | 3000.00 | 6000.00 | 3763.00 | 7526.00 | 5000.00 | 10000.00 | 3200.00 | 6400.00 | 6000.00 | DOSHI ELECTRIC ENGG. CO.
29.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 400 Sq.mm | 12.00 | Set |  | 2500.00 | 30000.00 | 1000.00 | 12000.00 | 1512.00 | 18144.00 | 3000.00 | 36000.00 | 1400.00 | 16800.00 | 12000.00 | DOSHI ELECTRIC ENGG. CO.
30.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 185 Sq.mm | 24.00 | Set |  | 1200.00 | 28800.00 | 800.00 | 19200.00 | 1135.00 | 27240.00 | 2000.00 | 48000.00 | 1250.00 | 30000.00 | 19200.00 | DOSHI ELECTRIC ENGG. CO.
31.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :. a) 3 X 95 Sq.mm | 4.00 | Set |  | 8500.00 | 34000.00 | 7000.00 | 28000.00 | 7372.00 | 29488.00 | 6000.00 | 24000.00 | 3400.00 | 13600.00 | 13600.00 | Shiva Enterprises
32.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 400 Sq.mm | 6.00 | Set |  | 7100.00 | 42600.00 | 6000.00 | 36000.00 | 5035.00 | 30210.00 | 3500.00 | 21000.00 | 4700.00 | 28200.00 | 21000.00 | SAURABH ENTERPRISES
33.00 | Design, manufacture, supply, installation, testing and commissioning of outdoor type feeder pillar box as per latest IS of size 0.60 m X 0.75 m X 0.30 m with double door fabricated from 2 mm thick MS steel including TPN Bus bar of following rating with suitable equidistant arrangement for connection of 01 I/c and 02 Outgoing cables, cable entry from bottom, arranegment for earth connection, totally enclosed type with free standing floor mounted, dust & vermin proof etc including MS angle iron stand as per site requirement complete as required. a) 415 V, 400 AMP, 50 Hz | 6.00 | Job |  | 11500.00 | 69000.00 | 15000.00 | 90000.00 | 18573.00 | 111438.00 | 11500.00 | 69000.00 | 40000.00 | 240000.00 | 69000.00 | Naagar Infrastructure Pvt Ltd, SAURABH ENTERPRISES
34.00 | SH IV : Earthing Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 12000.00 | 72000.00 | 20000.00 | 120000.00 | 11598.00 | 69588.00 | 15000.00 | 90000.00 | 18300.00 | 109800.00 | 69588.00 | Leo Air and Power Solution Pvt Ltd.,
35.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre lonq etc. with charcoal/ coke and salt as required. | 18.00 | Set |  | 5500.00 | 99000.00 | 12000.00 | 216000.00 | 5210.00 | 93780.00 | 7000.00 | 126000.00 | 11000.00 | 198000.00 | 93780.00 | Leo Air and Power Solution Pvt Ltd.,
36.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 50.00 | Meter |  | 1000.00 | 50000.00 | 1200.00 | 60000.00 | 1149.00 | 57450.00 | 1150.00 | 57500.00 | 1230.00 | 61500.00 | 50000.00 | Naagar Infrastructure Pvt Ltd
37.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 76.00 | Meter |  | 220.00 | 16720.00 | 250.00 | 19000.00 | 174.00 | 13224.00 | 240.00 | 18240.00 | 160.00 | 12160.00 | 12160.00 | Shiva Enterprises
38.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut,bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Meter |  | 1200.00 | 72000.00 | 1600.00 | 96000.00 | 1579.00 | 94740.00 | 1550.00 | 93000.00 | 1450.00 | 87000.00 | 72000.00 | Naagar Infrastructure Pvt Ltd
39.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut,bolt, spring, washer excavation and re-filling etc. as required. | 98.00 | Meter |  | 450.00 | 44100.00 | 600.00 | 58800.00 | 603.00 | 59094.00 | 750.00 | 73500.00 | 420.00 | 41160.00 | 41160.00 | Shiva Enterprises
40.00 | SH V : Precision Air Conditioning Supply of 15 TR Floor Mounted, Bottom discharge, Top suction, Air Cooled DX type CRAC units for Equipments room application suitable to maintain equipment room temperature at 18°C ± 2°C, equipped with most advanced industry technology, guaranteeing precise control of Equipment room. Suitable for 415 Volts, 50 Hz, 3 Phase Power Supply. The units shall be selected on the basis of following parameters: i) Not Less then 15TR Gross Sensible Cooling Capacity @ min. 14500 CMH ii) Return Air Selection at : 24 Deg. C. / 40 % RH of return air. iii) Supply air in between 14-16 Deg C. or as suitable to maintain room temperature at 18°C ± 2°C iv) 45 Deg C of Design Ambient temperature v) Each unit shall have independent double circuit with double outdoor units The Indoor unit shall comprise of Variable capacity Digital Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, Thermostatic Expansion valves, Driers, EU4/G4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crank case heaters, infrared Humidifier, Heaters, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories. Each unit shall be BMS compatible and shall have inbuilt software to faciliate BMS connectivity through RS485 Modbus Protocol and Ethernet with Modbus Protocol and HTTP Protocol. Each unit shall have inbuilt sequential controller for operating unit in N+1 confguration. Microprocessor should have inbuilt features of Team Mode and cascade mode to be used incase required. Each unit shal have individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values etc. as per the specifications considered excluding initial gas charge. The Outdoor Condenser unit shall have IP 54 protection and shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminum fins), automatic Fan speed controller, Isolator switch.Complete as per OEMs specifications. Supply and Installation of factory integrated Motorized Return Air Damper to be placed at top/inlet of the machine. | 3.00 | Each |  | 1139000.00 | 3417000.00 | 1500000.00 | 4500000.00 | 1644500.00 | 4933500.00 | 1400000.00 | 4200000.00 | 1295000.00 | 3885000.00 | 3417000.00 | Naagar Infrastructure Pvt Ltd
41.00 | Installation, tensting and commisiooning of Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units (Indoor & Outdoor) for Equipment room application, including Lifting, shifting & positioning of Indoor and outdoor units, Pressure testing, Vacumzing, charging, communication cabling, integration, interfacing, sequential operation, testing Commissioning of the system by OEM engineer, including provision of suitable MS stand for Indoor and Outdoor units as per OEM, Initial charge of R-410A refrigerant gas, including minor civil work complete as per site requirement for guaranteeing precise temperature control of Equipment room. | 3.00 | Job |  | 90000.00 | 270000.00 | 20000.00 | 60000.00 | 57500.00 | 172500.00 | 100000.00 | 300000.00 | 170000.00 | 510000.00 | 60000.00 | DOSHI ELECTRIC ENGG. CO.
42.00 | Supply & fixing of 18 gauge Hard Drawn Copper Pipe Refrigerant piping duly complete with all insulation, supports, clamps, fittings, connections, sleevs etc fittings and finished with two coated of enamel paint of approved colour code including suitable thickness as per OEM closed cell elastromeric insulation with Class 'O' fire retardent properties for piping the air conditioned space. | 120.00 | Metre |  | 2600.00 | 312000.00 | 2000.00 | 240000.00 | 2494.00 | 299280.00 | 3000.00 | 360000.00 | 2450.00 | 294000.00 | 240000.00 | DOSHI ELECTRIC ENGG. CO.
43.00 | Supply & Installation of Electrical PVC INSULATED & FRLS MULTI CORE copper cable (as per IS 694) on surface, cable tray, pipe as per site requirement (Cable size-4x2.5 Sq.mm.). | 80.00 | Metre |  | 320.00 | 25600.00 | 300.00 | 24000.00 | 180.00 | 14400.00 | 350.00 | 28000.00 | 290.00 | 23200.00 | 14400.00 | Leo Air and Power Solution Pvt Ltd.,
44.00 | Supply & Installation of Electrical PVC INSULATED & FRLS MULTI CORE copper cable (as per IS 694) on surface, cable tray, pipe as per site requirement (Cable size-4 x 25 Sq.mm.). | 80.00 | Metre |  | 900.00 | 72000.00 | 1000.00 | 80000.00 | 1500.00 | 120000.00 | 1150.00 | 92000.00 | 1790.00 | 143200.00 | 72000.00 | Naagar Infrastructure Pvt Ltd
45.00 | Supplying and installing of 300 mm width X 50 mm depth X 1.6 mm thickness size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, oainting suspenders etc as required. | 60.00 | Metre |  | 800.00 | 48000.00 | 800.00 | 48000.00 | 789.00 | 47340.00 | 700.00 | 42000.00 | 505.00 | 30300.00 | 30300.00 | Shiva Enterprises
46.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays bends with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. 300 mm width X 50 mm depth X 1.6 mm thickness | 4.00 | Each |  | 1500.00 | 6000.00 | 2000.00 | 8000.00 | 998.00 | 3992.00 | 1500.00 | 6000.00 | 1780.00 | 7120.00 | 3992.00 | Leo Air and Power Solution Pvt Ltd.,
47.00 | Providing & fixing GI sheet cover over the cable trays on the cable trays of size 300 mm width X 50 mm depth by using 2 mm thick GI sheet including bending as per required size, fixing securely over the cable trays to give a finished look complete as required as per site requirement. | 40.00 | Metre |  | 390.00 | 15600.00 | 300.00 | 12000.00 | 870.00 | 34800.00 | 1000.00 | 40000.00 | 780.00 | 31200.00 | 12000.00 | DOSHI ELECTRIC ENGG. CO.
48.00 | Supply and fixing of 25 mm dia CPVC Pipe for humidifier inlet. Complete with fittings supports, valves, 6 mm thick nitrile rubber insulation as required. | 100.00 | Metre |  | 650.00 | 65000.00 | 800.00 | 80000.00 | 243.00 | 24300.00 | 700.00 | 70000.00 | 450.00 | 45000.00 | 24300.00 | Leo Air and Power Solution Pvt Ltd.,
49.00 | Supply and fixing of 40 mm dia CPVC Pipe for drain pipe. Complete with fittings supports, valves, 6 mm thick nitrile rubber insulation as required. | 60.00 | Metre |  | 700.00 | 42000.00 | 950.00 | 57000.00 | 383.00 | 22980.00 | 900.00 | 54000.00 | 615.00 | 36900.00 | 22980.00 | Leo Air and Power Solution Pvt Ltd.,
50.00 | SITC of powder coated extruded aluminium Air Tranfer Grills with Volume control damper for Supply Air(600mm X600mm) | 15.00 | sq.mtr. |  | 9600.00 | 144000.00 | 9000.00 | 135000.00 | 6377.00 | 95655.00 | 11000.00 | 165000.00 | 5950.00 | 89250.00 | 89250.00 | Shiva Enterprises
51.00 | Supply and Application of 19 mm thick thermal insulation of floor of Server Room & walls below false floor using closed cell nitrile rubber elastomeric insulation with class 'O' fire retardant using suitable adhesive. | 200.00 | sq.mtr. |  | 310.00 | 62000.00 | 400.00 | 80000.00 | 637.00 | 127400.00 | 500.00 | 100000.00 | 950.00 | 190000.00 | 62000.00 | Naagar Infrastructure Pvt Ltd
52.00 | Supply and Installation of Return Air Plenum of suitable height to provide air tight connection between PAC. Plenum should be factory fabricated double skin insulated from inside. The plenum should be powder coated with the colour matching with the PAC. | 30.00 | sq.mtr. |  | 1800.00 | 54000.00 | 3500.00 | 105000.00 | 2317.00 | 69510.00 | 5000.00 | 150000.00 | 11700.00 | 351000.00 | 54000.00 | Naagar Infrastructure Pvt Ltd
53.00 | SITC of 1.5 Ton 5 Star Invertor technology Split type Air-Conditioner unit fitted with hermetically sealed compressors operating on refrigerant R-410A or equivalent greem gas suitable for wall mounting and suitable for operating on 230V +_10%, 50Hz, Single Phase, AC Supply including providing suitable plug top, including 3 metre refrigrant piping, related civil works and providing & fixing of Iron stand for outdoor unit etc. complete as required. | 8.00 | Job |  | 37000.00 | 296000.00 | 50000.00 | 400000.00 | 41768.00 | 334144.00 | 50000.00 | 400000.00 | 52000.00 | 416000.00 | 296000.00 | Naagar Infrastructure Pvt Ltd
54.00 | Supply and installation of Digital Thermohygrometer Data logger for recording and displaying temperature and humidity in a room complete as per site requirement. | 3.00 | Each |  | 1100.00 | 3300.00 | 30000.00 | 90000.00 | 12190.00 | 36570.00 | 50000.00 | 150000.00 | 14000.00 | 42000.00 | 3300.00 | Naagar Infrastructure Pvt Ltd
55.00 | SH VI : Pump, Insulating Mat, Misc. Items Providing and lowering of three phase submersible pump set with 05 HP motor & suitable stage pump suitable for discharge rate of approx. 120 Litre per minute at approx 79 mtr head including supplying and fixing of PVC coated wire rope for pump support and safety complete as per site requirement. | 1.00 | Job |  | 41000.00 | 41000.00 | 45000.00 | 45000.00 | 56318.00 | 56318.00 | 40000.00 | 40000.00 | 50000.00 | 50000.00 | 40000.00 | SAURABH ENTERPRISES
56.00 | Providing and placing in position up to 50 mm dia GI column pipe with flange made out of Jindal medium class along with flange including nut, bolt, gasket, coupling complete as required | 30.00 | Metre |  | 710.00 | 21300.00 | 700.00 | 21000.00 | 771.00 | 23130.00 | 1000.00 | 30000.00 | 395.00 | 11850.00 | 11850.00 | Shiva Enterprises
57.00 | Providing and fixing of 3 core 4 sqmm submersible flat, copper Cable suitable for submersible pump. | 80.00 | Metre |  | 80.00 | 6400.00 | 100.00 | 8000.00 | 218.00 | 17440.00 | 125.00 | 10000.00 | 160.00 | 12800.00 | 6400.00 | Naagar Infrastructure Pvt Ltd
58.00 | Providing and fixing of fully automatic Star Delta starter Panel Board suitable for 5 HP motor pump made out of 14 SWG sheet for submersible pump fitted with Ammeter, Voltmeter, single phase preventer, MCB ,on /off switch push botton, indicating lamps etc. with all accessories as required. | 1.00 | Job |  | 7500.00 | 7500.00 | 10000.00 | 10000.00 | 6615.00 | 6615.00 | 7000.00 | 7000.00 | 10670.00 | 10670.00 | 6615.00 | Leo Air and Power Solution Pvt Ltd.,
59.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 11 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.5 mm +/- 10 % (Class-B). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 30.00 | Metre |  | 850.00 | 25500.00 | 700.00 | 21000.00 | 638.00 | 19140.00 | 1270.00 | 38100.00 | 700.00 | 21000.00 | 19140.00 | Leo Air and Power Solution Pvt Ltd.,
60.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 3.3 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.0 mm +/- 10 % (Class-A). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 65.00 | Metre |  | 550.00 | 35750.00 | 600.00 | 39000.00 | 464.00 | 30160.00 | 1360.00 | 88400.00 | 590.00 | 38350.00 | 30160.00 | Leo Air and Power Solution Pvt Ltd.,
61.00 | Supplying & erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg. Capacity Cartridge type conf. To IS: 15683-2006 Complete erected with necessary clamp made front 50x6 mm. M. S. flat with nut & bolts grouted in wall complete. | 5.00 | Each |  | 4500.00 | 22500.00 | 6000.00 | 30000.00 | 6300.00 | 31500.00 | 8000.00 | 40000.00 | 4500.00 | 22500.00 | 22500.00 | Naagar Infrastructure Pvt Ltd, Shiva Enterprises
62.00 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint ‘FIRE’ and mounted on MS angle iron frame with bracket of appropriate size & capacity I/c filling sand etc. | 2.00 | Sets |  | 5500.00 | 11000.00 | 5000.00 | 10000.00 | 5000.00 | 10000.00 | 1200.00 | 2400.00 | 2000.00 | 4000.00 | 2400.00 | SAURABH ENTERPRISES
| Total in Figures |  |  |  |  | 21633710.00 |  | 21926500.00 |  | 21824426.00 |  | 20088940.00 |  | 20700000.00
Lowest Amount Quoted BY: SAURABH ENTERPRISES(20088940.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of ASR MSSR Building at LBSI Airport, Varanasi. SH- Substation and Allied Works. Tender ID: 2024_AAI_197932_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES | 20088940.00 | L1
| 2 | Shiva Enterprises | 20700000.00 | L2
| 3 | Naagar Infrastructure Pvt Ltd | 21633710.00 | L3
| 4 | Leo Air and Power Solution Pvt Ltd., | 21824426.00 | L4
| 5 | DOSHI ELECTRIC ENGG. CO. | 21926500.00 | L5