## BoQ1
Government eProcurement System Created By: BHAITHI DEVARAJU Created Date/Time: 07-Nov-2024 05:45 PM Tender Title: Provision of Power Supply System to ATC Tower cum Technical Block at Vijayawada airport. SH SITC Tender ID: 2024_AAI_199995_2
Tender Inviting Authority: Asst. General Manager (Engg-E), Airports Authority of India, Vijayawada International Airport.
Name of Work: Provision of Power Supply System for ATC Tower Cum Technical Block at Vijayawada Airport. S.H: SITC of Sub-Station Equipments
Contract No: 2024_AAI_199995_2
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | shiv electric (GSTN-07AACFS2722H1ZF) BID ID -757044 |  | ASIATIC TRADERS (GSTN-NA) BID ID -757012 |  | sri sai leela electrical projects (GSTN-NA) BID ID -756657
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Internal Arc Type Tested 33 KV Switch Board of VCB Panel of of sheet steel, dust tight, vermin proof, totally enclosed cubicle type floor mounting horizontal drawout free standing extensible on both sides, suitable for indoor operation at 33 KV, 3 Phase, 50 Hz AC Power Supply System having 1500 MVA for 3 Second Rupturing Capacity complete with all accessories such as shunt trip coil suitable for 24V DC Power Supply, motorised and manually operated spring assisted closing mechanism, auxillary contacts, etc., interconnections, earthing etc., as required and comprising of following: (A) Two Nos. (Incomers) of 1250 Amps. rating VCB of 33 KV grade having PVC sleaved air insulated copper bus bars of 1250 Amps., capacity with suitable resin cast dual core CTs of ratio 150/75/5-5A with class 0.5 accuracy, resin cast PT of of ratio 33 KV/110 V with class 1 accuracy, complete with Microprocessor Based Relay of Schneider Make P5F30 Model/Equivalent, Digital Multi Function Meter of Schneider Make PM 5560/Equivalent, Individual Ammeter and Voltmeter with inbuilt Selector Switch, 7 LED Type ON/OFF/TRIP/Spring Indication Lamps, 7 LED Phase Indication Lamps, providing Mechanical and Electrical Interlock with Buscoupler and Incomers, Push Buttons and Incomers, ON/OFF/Trip Switch, Master Trip Relay, Thermostat Controlled Heaters, Hooter, Panel Lamp, Annunciation Window, cable entry provision for 3 X 300 Sq.mm,33KV grade HT XLPE cable etc., as required. (B) One Bus Coupler of 1250 Amps. rating VCB of 33 KV grade having PVC sleaved air insulated copper bus bars of 1250 Amps., capacity with 7 LED Type ON/OFF/Spring Indication Lamps, Push Buttons, ON/OFF/Trip Switch, Thermostat Controlled Heaters, Hooter, Panel Lamp, Annunciation Window, etc., as required. (C) 3 Nos. (Outgoings) 1250 Amps. rating VCB of 33 KV grade having PVC sleaved air insulated copper bus bars of 1250 Amps., capacity with suitable resin cast dual core CTs of ratio 100/50/5-5A with class 0.5 accuracy, complete with Microprocessor Based Relay of Schneider Make P5F30 Model/Equivalent, Auxillary Relays for WTI and OTI Alarm and Trip, Digital Meter of Schneider Make PM 5560/Equivalent, Individual Ammeter and Voltmeter with inbuilt Selector Switch, 7 LED Type ON/OFF/TRIP/Spring Indication Lamps, 7 LED Phase Indication Lamps, providing Mechanical Castle Lock for individual Breaker, Push Buttons, ON/OFF/Trip Switch, Master Trip Relay, Auxiliary Relays, Thermostat Controlled Heaters, Hooter, Panel Lamp, Annunciation Window, cable entry provision for 3 X 300 Sq.mm. XLPE cable etc., as required.
1.01 | All Above 1(A) - 1 (C) | 1.00 | Job | 100.00 | 6075000.00 | 6075000.00 | 9700000.00 | 9700000.00 | 8500000.00 | 8500000.00 | 6075000.00 | shiv electric
2.00 | SITC of 1600 KVA, 33/0.433 KV, 3 Phase, 50 Hz Step Down, Indoor Type, Delta/Star connected, Dy11, copper wound core type, Class H Insulated, K 20 Rated, E2 C2 F1 Compliant, Cast Resin DRY TYPE, air cooled transformer with ON LOAD Tap Changer in steps of 2.5% (Tap Range +7.5% to -10.0%) with Stanard Control Panel of OEM and complete with cable end box on HT side suitable for 3X300 Sq.mm. 33 KV XLPE cable and suitable for Bus Duct on LT side, provision of Palm Contacts at HT Side, earthing terminals, Provision of inbuilt CT/PT/Digital Meter of Class 0.5 Accuracy for measuring and monitoring Transformer Losses, Winding Temperature Display with required Sensors, Room Temperature Display, Door Safety Lock, lifting lugs etc., with all standard accessories conforming to IS 2026 Part 11/2021 and meeting ECBC Norms 2017 as amended upto date including locking of rollers, Supplying and Laying of Armoured Copper Control Cable/Power Cable from OLTC to Transformer, Door Safety (Interlock) to 33 KV Panel, Winding Temparature Digital Display to 33 KV Panel and (Individual Cable up-to a Length of 30 Mtr), Termination of Cables etc., as required. | 2.00 | Job | 100.00 | 6750000.00 | 13500000.00 | 4900000.00 | 9800000.00 | 6506000.00 | 13012000.00 | 9800000.00 | ASIATIC TRADERS
3.00 | SITC of 15 Nos. of 2 Volt, 100 AH Exide Batteries [Totalling to 30V] of Model “PLANTE" or Equivalent with Initial Charging including providing and fixing MS Stand for suitable size for accommodate to all Batteries and connecting strips / loop cables, Numbering to the batteries etc. as required. | 1.00 | Job | 10.00 | 202500.00 | 202500.00 | 100000.00 | 100000.00 | 200000.00 | 200000.00 | 100000.00 | ASIATIC TRADERS
4.00 | SITC of 30V, 20 Amps, DC Battery Charger with Thyristor Based Rectifier suitable to operate in 230V, 50Hz, single phase AC Power Supply with charging arrangement for Trickle/Boost including with suitable range Digital Meter for both AC/DC for measuring Current and Voltage, Regulator, Selector Switches, Indication Lamps etc. for operating Batteries associated with 33 KV HT Panel, as required. | 1.00 | Job | 10.00 | 141750.00 | 141750.00 | 100000.00 | 100000.00 | 180000.00 | 180000.00 | 100000.00 | ASIATIC TRADERS
5.00 | Supply, Installation, Testing and Commissioning of Prime Rated 1500 KVA DG Set along with Acoustic enclosure including minor Civil Works if required, meeting CPCB Pollution Norms up to date ammendments as applicable on the Day of submission of Tender and comprising of following: (A) 01 No. Alternator suitable for generating 1200 KW/1500 KVA at 415 V, 3 Phase, 50 Hz, 0.8 PF, 1500 RPM, Self Ventilated, Self Regulated and Self Excited with Brushless Type with Class H Insulation, PMG Exciter Voltage Regulator etc., conforming to IS 4722 as specified and as required. (B) 01 No. Multi Cylinder, 4 Stroke, Turbo Charged After Cooled Diesel Engine developing Break Mean Effective Power not less than 1910 kPa at 1500 RPM suitable for above mentioned Alternator and Complete with all accessories such as Base Frame, AVM Pads, Batteries, All Types of Filters (Including Air Filter of Heavy Duty), Coupling, Starter, Attenuation Critical Silencer, Exhaust Piping (with Thermal Insulation and Aluminum Cladding) upto 60 cm horizontal outside the DG Room , Automatic Electronic Speed Governing Mechanism, Compact Radiator, etc., and conforming to relevant IS with up to date amendments as specified and as required. (C) Integrated Microprocessor based Generator Set Control System providing Digital Voltage Regulation, Engine Protection, Alternator Protection, Isochronous Governing, AMF Function, Battery Monitoring, Operator Interface, Communication Interface etc., as specified and as required. (D) 1 No. Integral Contro/Isolator Panel made of 2mm thick CRCA Sheet, comprising of DG Controller (as mentioned above atc.), Copper Bus Bars of capacity not less than 3000 Amps with incoming/outgolng terminals, Indicating Lamps for 'Load ON' and 'Set Running', Instrument Fuses duly wired and ferruled, 4P EDO ACB of 2500 Amps 65 KA rating with Overload, Short Circuit and Earth Fault Protections of Microprocessor Based as required. (E) 1 No. Fuel Tank of Capacity 990 Ltrs., Complete with connecting Pipes, Valves, Fuel Level Indicators etc., as specified and as required. (F) Provision and Fixing of all accessories and carrying out all associated Works inside DG Room as required. (G) Acoustic Enclosure : Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. (H) The work should be as per Central Electrical Authority / Pollution control board standards. (DG Foundation will be provided by AAI)
5.01 | All Above 5(A) - 5 (H) | 1.00 | Job | 100.00 | 12200000.00 | 12200000.00 | 12400000.00 | 12400000.00 | 11689500.00 | 11689500.00 | 11689500.00 | sri sai leela electrical projects
6.00 | Design, IIT/NIT/Reputed engineering College Vetting, Fabrication, Supply, Installation, Testing and Commissioning of Exhaust System comprising of suitable size (i.e. 2 Nos. of 10" and 1 No of 14" or as per OEM Standard) MS C Class, 5mm thick Pipe conforming to IS 3589 upto 30 Mtr Height above FFL, jointing with existing DG Exhaust Line of Item No. 5 as above, including providing necessary Bends, Clamps, Supports with suitable Angle Frame Structure with RCC Foundation as per Design to hold Load of Pipe upto 30 Mtr and Wind Pressure as per IS 875 Part 3 2015 with upto date amendments, provision of anti vibration mountings, thermal insulation with 50mm thick rockwool/mineral wool of density 120kg/cu mtr, wiremeshing, aluminium cladding with 1 mm thick aluminium sheet, provision of cleaning chamber at bottom with locking arrangement, providing rain water protection at top, providing 2 Nos. of AOL including providing cabling, wiring, connection of AOL etc., as required | 1.00 | Job | 10.00 | 1750000.00 | 1750000.00 | 1500000.00 | 1500000.00 | 1600000.00 | 1600000.00 | 1500000.00 | ASIATIC TRADERS
7.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. Thickness 1.25 mm sheet | 48.00 | Sqm | 10.00 | 1500.00 | 72000.00 | 2150.00 | 103200.00 | 7500.00 | 360000.00 | 72000.00 | shiv electric
8.00 | Supplying, installing by suspension on ceiling, testing and commissioning of 3200 Amps, 175 KA (RMS), Indoor Sandwich Type Bus Trunking for use on 3 Phase 4 Wire, 415 Volts, 50 Hz A C, with metal clad enclosure made of 1.6mm thick GI Sheet duly powder coated in convenient Sections complete with 4 Nos. of Aluminium Bus Bars of same rating with multi-layer Class F Insulation, necessary joints, elbow joints & expansion joints and bends, adopter box and Copper Flexible for Joints, continuous earthing with 2 Nos. of aluminium strip of 50X6 mm size (one on each side) including GI clamping brackets, suspenders, angle iron bracket, fasteners, connecting to earthing system etc., as required. | 75.00 | Mtr | 10.00 | 40000.00 | 3000000.00 | 20000.00 | 1500000.00 | 52150.00 | 3911250.00 | 1500000.00 | ASIATIC TRADERS
9.00 | Supplying, installing by suspension on ceiling, testing and commissioning of 2500 Amps, 175 KA (RMS), Indoor Sandwich Type Bus Trunking for use on 3 Phase 4 Wire, 415 Volts, 50 Hz A C, with metal clad enclosure made of 1.6mm thick GI Sheet duly powder coated in convenient Sections complete with 4 Nos. of Aluminium Bus Bars of same rating with multi-layer Class F Insulation, necessary joints, elbow joints & expansion joints and bends, adopter box and Copper Flexible for Joints, continuous earthing with 2 Nos. of aluminium strip of 50X6 mm size (one on each side) including GI clamping brackets, suspenders, angle iron bracket, fasteners, connecting to earthing system etc., as required. | 50.00 | Mtr | 10.00 | 34000.00 | 1700000.00 | 17000.00 | 850000.00 | 40750.00 | 2037500.00 | 850000.00 | ASIATIC TRADERS
10.00 | Fabrication, SITC of Essential cum AMF MV Switch Board panel of TTA Type, made out of 2 mm thick CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, extensible on both side and suitable for indoor operation at 433V, 3 phase, 4 wire, 50Hz, A.C. system complete with all accessories, interconnection, connection, earthing, painting, alignment with the bus ducts etc., as required and comprising of following: (A) Two Nos. 2500 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as INCOMERs (Transformer Supply) with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps, ON OFF Push Buttons and Phase Indication Lamps, Electrical Interlocking Facility with EB/DG Incomers and Buscoupler as required. (B) Two Nos. 2500 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as INCOMERs (DG Supply) with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps, ON OFF Push Buttons and Phase Indication Lamps, Electrical Interlocking Facility with EB/DG Incomers and Buscoupler as required. (C) One No. 2500 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as Bus Coupler with LED Type ON/OFF Indication Lamps, Push Buttons, etc., as required. (D) Two Nos. 2000 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as Outgoings with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps and ON OFF Push Buttons etc., as required. (E) Two Nos. 1250 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as Outgoings with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps and ON OFF Push Buttons etc., as required. (F) Two Nos. 800 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as Outgoings with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps and ON OFF Push Buttons etc., as required.
10.01 | (G) Two Nos. 630 A, 60 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter (EM 6459 of Schneider/Equivalent) and ON/OFF/TRIP Indication Lamps etc., as required. (H) Two Nos. 400 A, 50 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter (EM 6459 of Schneider/Equivalent) and ON/OFF/TRIP Indication Lamps etc., as required. (I) Two Nos. 250 A, 50 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter (EM 6459 of Schneider/Equivalent) and ON/OFF/TRIP Indication Lamps etc., as required. (J) 2 Nos. of 24 V Battery Charger (Each One for Two DG Sets) consisting of transformer, rectifier, DC/AC Ammeter, DC/AC Volt Meter and charge rate selector switch with position OFF/Trickle/OFF/Boost for charging capacity of 24 Volts lead acid battery ( 2 Nos each of 12 volts, 25 plates 180 AH in two steps i.e. trickle/boost charging), Rheostat etc., as required. (K) Two Nos. of 8 Display Temperatue Scanner for BTD and RTD of Alternator. (L) Two Sets of Selector Swiches for Auto/Manual/Test/Off Operation and One Set of Push Button for Start/Stop/Reset etc. (M) Two Sets of 5 mm, 3 LED Display for indicating Performance of DG Set and One Hooter to alarm the abnormality of DG Set. (N) PLC System for AMF Operation , Monitoring and controlling of 2 Nos.ACBs of DG Sets and 2 Nos ACBs of EB Supply and Bus Coupler including interlinking with DG Controller, Programming, Operation of DG Set- II in case of DG Set-I fails to start and vice versa etc., as required. (O) One Set of Aluminium Bus Bars of 3500 A Capacity including Neutral and with 50X10 mm size Al. Earth Bus Bar as required. (P) Surge protection devices shall be provided for In Comers as per the technical specifications. (Q) All accessories such as fuses, auxiliary contactors, auxiliary switches, push buttons MCBs, etc., as required. All Above 10 (A) to 10.01 (Q) - 1 Job | 1.00 | Job | 100.00 | 5500000.00 | 5500000.00 | 5500000.00 | 5500000.00 | 9000000.00 | 9000000.00 | 5500000.00 | ASIATIC TRADERS, shiv electric
11.00 | SITC of 500 KVAR APFC MV Panel of depth not less than 900 mm made of 2 mm thick CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type, mountable on angle frame support, suitable for indoor operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. system complete with all accessories, interconnection, connection, termination of interconnecting flexi-wires with suitable copper lugs, earthing, painting etc. as required and comprising of following: (A) One No. 800 A, 65 KA, 4P EDO type Modular ACB (L&T 'U Power'/Equivalent) as Incomer with inbuilt Metering & Protection with Microprocessor Based Releases having Communication Facility and provided with separate Resin Cast CTs with Digital Meter (EM 6400 of Schneider/Equivalent), separate CT operated 3 Phase Digital Protective Relay, ON/OFF/TRIP Indication Lamps and ON OFF Push Buttons etc., as required. (B) One No. of 14 Steps APFC Relay with VA Sensors of (2500/5) Amps Resin Cast CT at appropriate Transformer's Secondary Circuit i/c supplying, laying/fixing of 7C X 2.5 Sq.mm. PVC insulated PVC sheatherd armourned, copper conductor Control Cabling from Transformer Secondary to APFC Panel (for length up-to 30 Mtr), providing Auto/Manual Facility as required. (C) Four Nos. Cooling Fan suitable for 230 V, 1 Ph. Operation. (D) Two Nos. of each 100 KVAR, 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 400 A 3P, 36 KA, TMR MCCBs, 2 Runs of 50 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps. (E) Four Nos. of each 50 KVAR, 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 200 A 3P, 36 KA, TMR MCCBs, 50 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps. (F) Three Nos. of each 25 KVAR, 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 100 A 3P, 36 KA, TMR MCCBs, 25 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps. (G) Two Nos. of each 10 KVAR, 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 63 A, 3P, 15 KA, MCBs, 10 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps.
11.01 | (H) One No. 5 KVAR, 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 40 A, 3P, 15 KA, MCBs, 10 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps. (I) One set of busbars of 1000 Amps capacity with at par neutral. (J) Two Empty Cubicle each to accommodate 25 KVAR Capacitor, 7% Detuned Reactors, Capacitor Duty Contactor, MCCB, Push Button, ON/OFF Indication Lamps (ONLY CUBICLE / No Switch Gear) (K) All accessories such as fuses, auxillary contactors, auxillary switches/MCBs etc., as required. All Above 11 (A) to 11.01 (K) - 1 Job | 2.00 | Job | 100.00 | 1400000.00 | 2800000.00 | 1400000.00 | 2800000.00 | 1500000.00 | 3000000.00 | 2800000.00 | ASIATIC TRADERS, shiv electric
12.00 | Supply of 33 KV garde, 3 Core x 300 Sq.mm, compact circular stranded Alluminium conductor provided with conductor screening of semi-conducting compound XLPE insulated provided with insulation screening over individual cores, consisting of extruded semi-conducting compound followed by lapped semi-conducting copper tapes, cores laid together with suitable fillers, in the interscripes covered with inner sheath by extrusion, galvanized flat steel strip armoured and overall PVC sheathed cable, suitable for 33 KV (E) System conforming to IS 7098 (Part-II) 2011 as amended upto date as required. | 3000.00 | Mtr | 10.00 | 2535.00 | 7605000.00 | 2200.00 | 6600000.00 | 3250.00 | 9750000.00 | 6600000.00 | ASIATIC TRADERS
13.00 | Laying of one number PVC / XLPE insulated and PVC sheathed power cable of 33 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 120 sq. mm and upto 400 sq. mm | 2400.00 | Mtr | 10.00 | 350.00 | 840000.00 | 80.00 | 192000.00 | 300.00 | 720000.00 | 192000.00 | ASIATIC TRADERS
14.00 | Laying of one number PVC / XLPE insulated and PVC sheathed power cable of 33 KV grade of following size in the existing masonry open duct as required. Above 120 sq. mm and upto 400 sq. mm | 400.00 | Mtr | 10.00 | 350.00 | 140000.00 | 60.00 | 24000.00 | 250.00 | 100000.00 | 24000.00 | ASIATIC TRADERS
15.00 | Laying and Fixing of one number PVC/XLPE insulated and PVC sheathed power cable of 33 KV grade of of following size on Surface with 5mm Thick MS Flats C Clamps as required. Above 120 sq. mm and upto 400 sq. mm | 200.00 | Mtr | 10.00 | 300.00 | 60000.00 | 150.00 | 30000.00 | 350.00 | 70000.00 | 30000.00 | ASIATIC TRADERS
16.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for 3 Core x 300 Sq.mm XLPE aluminium conductor cable of 33 KV grade as required | 4.00 | Each | 10.00 | 23400.00 | 93600.00 | 20000.00 | 80000.00 | 70900.00 | 283600.00 | 80000.00 | ASIATIC TRADERS
17.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 Core x 300 SQ. MM, XLPE Aluminium Conductor cable of 33 KV grade as required | 10.00 | Each | 10.00 | 10400.00 | 104000.00 | 8000.00 | 80000.00 | 23240.00 | 232400.00 | 80000.00 | ASIATIC TRADERS
18.00 | Supply of 3.5 Core x 300 Sq.mm, XLPE insulated and PVC sheathed armoured aluminium conductor power cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date ammendments etc., complete as required. | 500.00 | Mtr | 10.00 | 1373.00 | 686500.00 | 1300.00 | 650000.00 | 1700.00 | 850000.00 | 650000.00 | ASIATIC TRADERS
19.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm in the existing RCC/ HUME/ METAL / HDPE / DWC pipe as required. | 100.00 | Mtr | 10.00 | 200.00 | 20000.00 | 60.00 | 6000.00 | 300.00 | 30000.00 | 6000.00 | ASIATIC TRADERS
20.00 | Laying of one number PVC / XLPE insulated and PVC sheathed power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 300.00 | Mtr | 10.00 | 200.00 | 60000.00 | 60.00 | 18000.00 | 250.00 | 75000.00 | 18000.00 | ASIATIC TRADERS
21.00 | Laying and fixing of one number PVC / XLPE insulated and PVC sheathed power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm GI flat clamp) on cable tray as required | 100.00 | Mtr | 10.00 | 200.00 | 20000.00 | 120.00 | 12000.00 | 200.00 | 20000.00 | 12000.00 | ASIATIC TRADERS
22.00 | Supplying and making end termination with brass double compression gland and aluminium lugs for 3.5 X 300 sq. mm (70mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 16.00 | Each | 10.00 | 1800.00 | 28800.00 | 1500.00 | 24000.00 | 3500.00 | 56000.00 | 24000.00 | ASIATIC TRADERS
23.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 16.00 | Set | 10.00 | 8500.00 | 136000.00 | 8500.00 | 136000.00 | 20000.00 | 320000.00 | 136000.00 | ASIATIC TRADERS, shiv electric
24.00 | Earthing with copper earth plate 600 mm X 600 mm X 5 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | Set | 10.00 | 13500.00 | 135000.00 | 18000.00 | 180000.00 | 35000.00 | 350000.00 | 135000.00 | shiv electric
25.00 | Supplying and laying 50 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection / terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 60.00 | Mtr | 10.00 | 2860.00 | 171600.00 | 1500.00 | 90000.00 | 3230.00 | 193800.00 | 90000.00 | ASIATIC TRADERS
26.00 | Supplying and laying 50 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 110.00 | Mtr | 10.00 | 260.00 | 28600.00 | 300.00 | 33000.00 | 395.00 | 43450.00 | 28600.00 | shiv electric
27.00 | Providing and fixing 50 mm X 5 mm copper strip in 80 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required | 48.00 | Mtr | 10.00 | 4030.00 | 193440.00 | 2000.00 | 96000.00 | 4500.00 | 216000.00 | 96000.00 | ASIATIC TRADERS
28.00 | Providing and fixing 50 mm X 5 mm G.I. strip in 80 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 88.00 | Mtr | 10.00 | 1450.00 | 127600.00 | 700.00 | 61600.00 | 1665.00 | 146520.00 | 61600.00 | ASIATIC TRADERS
29.00 | Providing and fixing 50 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 144.00 | Mtr | 10.00 | 2860.00 | 411840.00 | 1500.00 | 216000.00 | 3230.00 | 465120.00 | 216000.00 | ASIATIC TRADERS
30.00 | Providing and fixing 50 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 264.00 | Mtr | 10.00 | 2808.00 | 741312.00 | 250.00 | 66000.00 | 395.00 | 104280.00 | 66000.00 | ASIATIC TRADERS
31.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
31.01 | 300 mm (W) X 62.5 mm (D) X 2.0 mm Thickness | 100.00 | Mtr | 10.00 | 1200.00 | 120000.00 | 600.00 | 60000.00 | 1320.00 | 132000.00 | 60000.00 | ASIATIC TRADERS
31.02 | 600 mm (W) X 75.0 mm (D) X 2.0 mm Thickness | 150.00 | Mtr | 10.00 | 1850.00 | 277500.00 | 1100.00 | 165000.00 | 1940.00 | 291000.00 | 165000.00 | ASIATIC TRADERS
32.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
32.01 | 300 mm width X 62.5 mm depth X 2.0 mm thickness | 12.00 | Each | 10.00 | 2351.00 | 28212.00 | 1800.00 | 21600.00 | 2480.00 | 29760.00 | 21600.00 | ASIATIC TRADERS
32.02 | 600 mm width X 75 mm depth X 2.0 mm thickness | 12.00 | Each | 10.00 | 3900.00 | 46800.00 | 2900.00 | 34800.00 | 4400.00 | 52800.00 | 34800.00 | ASIATIC TRADERS
33.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
33.01 | 300 mm width X 62.5 mm depth X 2.0 mm thickness | 6.00 | Each | 10.00 | 2779.00 | 16674.00 | 2500.00 | 15000.00 | 2525.00 | 15150.00 | 15000.00 | ASIATIC TRADERS
33.02 | 600 mm width X 75 mm depth X 2.0 mm thickness | 6.00 | Each | 10.00 | 4706.00 | 28236.00 | 3500.00 | 21000.00 | 4460.00 | 26760.00 | 21000.00 | ASIATIC TRADERS
34.00 | Supply & Installation of 600 mm width X 100 mm depth X 2.0 mm thickness GI Ladder type cable Trays.The cable tray shall be fixed to the ceiling / wall with suitable size of GI clamp, appropriate dia threaded rod & 35mmx2mm thick GI slotted 'C' channel Patti OR suitable size of MS angle support (MS support to be painted with two coats of red oxide & two coats of enamelled paint). Supports to be provided at an interval of 1 meter or lesser depending upon the location. Including horizontal & vertical bends, reducers, tees, cross members & other accessories, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required | 150.00 | Mtr | 10.00 | 1139.00 | 170850.00 | 900.00 | 135000.00 | 1500.00 | 225000.00 | 135000.00 | ASIATIC TRADERS
35.00 | Supply and fixing of nominal 3.0 mm thick (Width 1 Mtr) PVC synthetic, electric insulated mats conforming to IS 15652-2006 having Dielectric strength of 65 KV along-with suitable adhesive / chemibound, PU resin, waterproofing compound and celing material as per recommendation of the manufacturer and as per specifications and high insulation resistance (Minimum 1,00,000 M Ω on wet condition with 5 KV meggar) etc., as required. | 204.00 | Sqm | 10.00 | 1300.00 | 265200.00 | 800.00 | 163200.00 | 2000.00 | 408000.00 | 163200.00 | ASIATIC TRADERS
36.00 | Supply and fixing of nominal 2.0 mm thick (Width 1 Mtr) PVC synthetic, electric insulated mats conforming to IS 15652-2006 having Dielectric strength of 30 KV along-with suitable adhesive / chemibound, PU resin, waterproofing compound and celing material as per recommendation of the manufacturer and as per specifications and high insulation resistance (Minimum 1,00,000 M Ω on wet condition with 5 KV meggar) etc., as required. | 120.00 | Sqm | 10.00 | 1200.00 | 144000.00 | 500.00 | 60000.00 | 1800.00 | 216000.00 | 60000.00 | ASIATIC TRADERS
37.00 | Providing Single Line Diagram for entaire sub-station on 5mm thick Aluminium sheet in A0 Size duly laminated.as per IS Standard. | 1.00 | Each | 10.00 | 10000.00 | 10000.00 | 3500.00 | 3500.00 | 18000.00 | 18000.00 | 3500.00 | ASIATIC TRADERS
38.00 | Providing Single Line Diagram for entaire sub-station on 5mm thick Aluminium sheet in A1 Size duly laminated.as per IS Standard. | 1.00 | Each | 10.00 | 10000.00 | 10000.00 | 2500.00 | 2500.00 | 15000.00 | 15000.00 | 2500.00 | ASIATIC TRADERS
39.00 | Providing Single Line Diagram for each panel (i.e. HT Panel, Non-Essential panel, Essential Panel, AMF Panels, APFC Panels etc.) as per IS Standard on A1 Size good quality paper with duly laminated and display at each individual panels and soft copy submitted to AAI as required. | 2.00 | Set | 10.00 | 1500.00 | 3000.00 | 1000.00 | 2000.00 | 10000.00 | 20000.00 | 2000.00 | ASIATIC TRADERS
40.00 | Provision of double sided, caution board with electro cut computerised automated self-adhesive translucent colored vinyl on unbreakable polycarbonate 5mm thick sheet printed in signal red "Man on Line, Don’t switch on" as required. | 4.00 | Each | 10.00 | 4000.00 | 16000.00 | 600.00 | 2400.00 | 1000.00 | 4000.00 | 2400.00 | ASIATIC TRADERS
41.00 | Supplying of three phase, highly Insulated FRP static earth ground discharge stick suitable voltage discharge up to 33 KV as per IS Standard as required. | 2.00 | Set | 10.00 | 10500.00 | 21000.00 | 5000.00 | 10000.00 | 8500.00 | 17000.00 | 10000.00 | ASIATIC TRADERS
42.00 | Supply and fixing of Safety Instruction Chart of size 24"x36" (in words) in Telugu, Hindi & English duly framed with 5mm thick glass complete as required. | 7.00 | Each | 10.00 | 5000.00 | 35000.00 | 500.00 | 3500.00 | 2500.00 | 17500.00 | 3500.00 | ASIATIC TRADERS
43.00 | Providing & fixing of Carbon-dioxide (CO2) Type fire extinguishers conforming to IS 2878-1976 and cylinder fully charged of 4.5 Kg capacity at each location of HT Room and RTTC Room as required. | 5.00 | Each | 10.00 | 5850.00 | 29250.00 | 12000.00 | 60000.00 | 8000.00 | 40000.00 | 29250.00 | shiv electric
44.00 | Providing & fixing of ABC Type fire extinguishers conforming to IS 2878-1976 and cylinder fully charged of 6 Kg capacity at each location of LT panel Room and DG Set Room as required. | 7.00 | Each | 10.00 | 3000.00 | 21000.00 | 5000.00 | 35000.00 | 8000.00 | 56000.00 | 21000.00 | shiv electric
45.00 | Supply and fixing of Foam type fire extinguishers [Portable Type of 9 Litre Capacity] at location of Transformer as required. | 6.00 | Each | 10.00 | 3000.00 | 18000.00 | 6000.00 | 36000.00 | 10500.00 | 63000.00 | 18000.00 | shiv electric
46.00 | Providing & fixing a set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour and written with white paint 'Fire' and mounted on MS angle iron frame with bracket of appropriate size and capacity including filling sand complete as required. | 3.00 | Each | 10.00 | 4500.00 | 13500.00 | 2000.00 | 6000.00 | 4500.00 | 13500.00 | 6000.00 | ASIATIC TRADERS
47.00 | Providing & fixing of First Aid Box as approved by St. John Ambulance Brigade/Indian Red Cross conforming to IS 2217-1963 as required. | 1.00 | Each | 10.00 | 2500.00 | 2500.00 | 1500.00 | 1500.00 | 2000.00 | 2000.00 | 1500.00 | ASIATIC TRADERS
48.00 | Supplying and laying of 2X300 mm dia non-pressure NP3 class (Medium duty) RCC pipe with collars jointed with stiff cement mortor i/c demolishing cement concrete/bituminous road, excavation of trench of required (900 mm) width for pipe, depth upto 1200 mm, providing and laying cement concrete of 1:4:8 ratio at bottom (100 mm) of pipe, refilling the trench with soil, ramming, watering, making the surface to original finish with CC of 1:3:6 ratio on top (150 mm) of CC of ratio 1:4:8 (100 mm) etc. as required. | 1200.00 | Mtr | 10.00 | 5980.00 | 7176000.00 | 2300.00 | 2760000.00 | 1250.00 | 1500000.00 | 1500000.00 | sri sai leela electrical projects
49.00 | Constructing brick masonary manhole in cement mortar 1:4 (1 cement: 4 coarse sand) RCC topslab with 1:1.5:3 mix (1 cement: 1.5 coarse sand: 3 graded stone aggregate 20mm nominal size) foundation concrete 1:4:8 mix (1cement:4 coarse sand:8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 (1 cement:3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement:4 coarse sand:4 graded stone aggregate 20mm nominal size) finsihed with a floating coat of neat cement complete as required. (as per standard design) Inside size 120x120 cm and 120 cm deep including RCC cover plate with MS Angle frame etc., with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 40.00 | Job | 10.00 | 12000.00 | 480000.00 | 18000.00 | 720000.00 | 22000.00 | 880000.00 | 480000.00 | shiv electric
50.00 | Fabrication, Supply and Fixing of 8mm thick, Heavy duty, anti corrosive blue coated, FRP / SMC Chequered plates including providing and fixing 40mmx40mmx5mm MS Angle supports in all side and diagonal of Chequered plates for strengthening by Aluminium by screwing, providing lifting hook etc., as required. | 300.00 | Sqm | 10.00 | 6500.00 | 1950000.00 | 3000.00 | 900000.00 | 2800.00 | 840000.00 | 840000.00 | sri sai leela electrical projects
51.00 | Excavation for cable trenches in soft soil, depth up to 1.2 m and (Size 1.5m x 1.5m) including dressing of sides getting out the excavated soil, refilling with sand and or good soil after laying of cable / pipe etc., in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as per direction of E-I-C as required. | 200.00 | Cum | 10.00 | 200.00 | 40000.00 | 500.00 | 100000.00 | 600.00 | 120000.00 | 40000.00 | shiv electric
52.00 | Providing and fixing of advanced conventional type lighting protection system with lightning conductor finial, made of 25 mm dia 300 mm long, Copper tube, having single prong at top, with 85 mm dia 6 mm thick copper base plate including holes etc. complete as required. | 8.00 | Each | 10.00 | 4725.00 | 37800.00 | 2000.00 | 16000.00 | 14000.00 | 112000.00 | 16000.00 | ASIATIC TRADERS
53.00 | Jointing of copper tape (with another copper tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 8.00 | Each | 10.00 | 100.00 | 800.00 | 200.00 | 1600.00 | 2500.00 | 20000.00 | 800.00 | shiv electric
54.00 | Providing and fixing copper strip 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For Vertical, horizontal etc.) | 508.00 | Mtr | 10.00 | 675.00 | 342900.00 | 400.00 | 203200.00 | 860.00 | 436880.00 | 203200.00 | ASIATIC TRADERS
55.00 | Providing and fixing testing joint, made of 20 mm X 3 mm thick copper strip, 125 mm long, with 4 nos. of SS bolts, nuts, chuck nuts and spring washers etc. complete as required. | 8.00 | Each | 10.00 | 800.00 | 6400.00 | 200.00 | 1600.00 | 1000.00 | 8000.00 | 1600.00 | ASIATIC TRADERS
56.00 | Providing and fixing 30 mm X 6 mm Copper strip in 65 mm dia G.I. pipe from earth electrode including connection with SS Nut, bolt, spring, washer excavation and re-filling etc. as required. | 12.00 | Mtr | 10.00 | 2652.00 | 31824.00 | 2500.00 | 30000.00 | 2500.00 | 30000.00 | 30000.00 | sri sai leela electrical projects, ASIATIC TRADERS
57.00 | Supply of 4Core x 25 Sq.mm, XLPE insulated and PVC sheathed armoured Aluminium conductor power cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date ammendments etc., complete as required. | 200.00 | Mtr | 10.00 | 204.00 | 40800.00 | 175.00 | 35000.00 | 220.00 | 44000.00 | 35000.00 | ASIATIC TRADERS
58.00 | Supplying and making end termination with brass double compression gland and aluminium lugs for 4 X 25 sq. mm (28mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 8.00 | Each | 10.00 | 500.00 | 4000.00 | 300.00 | 2400.00 | 650.00 | 5200.00 | 2400.00 | ASIATIC TRADERS
59.00 | Supplying and fixing of 8 way (4 + 24), Double door, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 4.00 | Each | 10.00 | 10000.00 | 40000.00 | 3500.00 | 14000.00 | 7980.00 | 31920.00 | 14000.00 | ASIATIC TRADERS
60.00 | Supplying and fixing of 63A, FP, 415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 4.00 | Each | 10.00 | 1815.00 | 7260.00 | 1000.00 | 4000.00 | 2155.00 | 8620.00 | 4000.00 | ASIATIC TRADERS
61.00 | Supplying and fixing of 63A, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 4.00 | Each | 10.00 | 1815.00 | 7260.00 | 3000.00 | 12000.00 | 3275.00 | 13100.00 | 7260.00 | shiv electric
62.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of single pole in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 96.00 | Each | 10.00 | 168.00 | 16128.00 | 150.00 | 14400.00 | 255.00 | 24480.00 | 14400.00 | ASIATIC TRADERS
63.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 70.00 | Points | 10.00 | 1563.00 | 109410.00 | 1200.00 | 84000.00 | 1275.00 | 89250.00 | 84000.00 | ASIATIC TRADERS
64.00 | Wiring for circuit/ submain wiring alongwith earth wire with 2 X 2.5 Sq. mm + 1 X 2.5 Sq. mm earth wire of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. | 500.00 | Mtr | 10.00 | 312.00 | 156000.00 | 300.00 | 150000.00 | 220.00 | 110000.00 | 110000.00 | sri sai leela electrical projects
65.00 | Wiring for light / power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit alongwith 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 500.00 | Mtr | 10.00 | 283.00 | 141500.00 | 500.00 | 250000.00 | 285.00 | 142500.00 | 141500.00 | shiv electric
66.00 | Supplying and fixing of 20mm dia., of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. | 60.00 | Mtr | 10.00 | 188.00 | 11280.00 | 100.00 | 6000.00 | 120.00 | 7200.00 | 6000.00 | ASIATIC TRADERS
67.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required.
67.01 | 4 Module (125mmX75mm) | 6.00 | Each | 10.00 | 290.00 | 1740.00 | 200.00 | 1200.00 | 205.00 | 1230.00 | 1200.00 | ASIATIC TRADERS
67.02 | 6 Module (200mmX75mm) | 30.00 | Each | 10.00 | 340.00 | 10200.00 | 300.00 | 9000.00 | 285.00 | 8550.00 | 8550.00 | sri sai leela electrical projects
68.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
68.01 | 5/6 A switch | 12.00 | Each | 10.00 | 87.00 | 1044.00 | 100.00 | 1200.00 | 115.00 | 1380.00 | 1044.00 | shiv electric
68.02 | 15/16 A switch | 60.00 | Each | 10.00 | 132.00 | 7920.00 | 200.00 | 12000.00 | 225.00 | 13500.00 | 7920.00 | shiv electric
68.03 | Multi pin 5/6 A socket outlet | 12.00 | Each | 10.00 | 103.00 | 1236.00 | 150.00 | 1800.00 | 180.00 | 2160.00 | 1236.00 | shiv electric
68.04 | Multi pin 15/16 A socket outlet | 60.00 | Each | 10.00 | 163.00 | 9780.00 | 250.00 | 15000.00 | 345.00 | 20700.00 | 9780.00 | shiv electric
69.00 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 10.00 | Each | 10.00 | 499.00 | 4990.00 | 500.00 | 5000.00 | 685.00 | 6850.00 | 4990.00 | shiv electric
70.00 | Supplying and fixing extra down rod of suitable length of G.I. pipe, 20 mm dia, heavy gauge including fixings arrangements, painting etc. as required. | 10.00 | Each | 10.00 | 660.00 | 6600.00 | 200.00 | 2000.00 | 4500.00 | 45000.00 | 2000.00 | ASIATIC TRADERS
71.00 | Supply and fixing of wrinkle free bend, 40mm dia., 1.5 Meter length, Medium class GI Pipe with all arrangement for fixing of pipe on wall surface / GI Pole suitable for installation of LED Street light fitting. Job include fabrication, pipe cutting, bending, welding etc. complete as per site requirement. | 12.00 | Job | 10.00 | 810.00 | 9720.00 | 500.00 | 6000.00 | 14000.00 | 168000.00 | 6000.00 | ASIATIC TRADERS
72.00 | Supply of LED Street light fitting with wattage of 60W with high power LEDs, system efficay not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 4kV surge suppressor, fitting made up of high pressure die-cast aluminium housing with suitable thermal management arrangement, toughned glass with IP 66 protection, suitable to operate on single phase AC supply, inline with technical specifications etc., complete as required. | 16.00 | Each | 10.00 | 2700.00 | 43200.00 | 2000.00 | 32000.00 | 4500.00 | 72000.00 | 32000.00 | ASIATIC TRADERS
73.00 | Supply of 20W, 4 feet, Energy efficient, surface mounting, batten type LED luminaries with aluminium housing and integrated electronic driver with operating voltage range (120 - 270V AC) with colour temperature 5700K range. LED having minimum 20,000 burning hours with minimum 70% lumen maintained, system consumption should be less than 20W and especially designed for commercial use etc., complete as required. Make: Philips, Model: Essential SmartBright Batten BN170C | 50.00 | Each | 10.00 | 518.00 | 25900.00 | 400.00 | 20000.00 | 1700.00 | 85000.00 | 20000.00 | ASIATIC TRADERS
74.00 | Supply of LED Highbay light fitting with Wattage of maximum 80W with high power LEDs, system efficacy not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 4kV surge suppressor, fitting made up of high pressure die-cast aluminum housing with suitable thermal management arrangement, toughened glass with IP 65 protection suitable to operate on single phase AC supply complete as required. | 50.00 | Each | 10.00 | 3915.00 | 195750.00 | 3000.00 | 150000.00 | 5500.00 | 275000.00 | 150000.00 | ASIATIC TRADERS
75.00 | Supply of 1200mm Sweep, High speed, 230 m3/min air delivery, ceiling fan complete with fan blades, top and bottom canopy with all accessories suitable for operation on 230V AC supply etc., as required. | 10.00 | Each | 10.00 | 1687.00 | 16870.00 | 2500.00 | 25000.00 | 5000.00 | 50000.00 | 16870.00 | shiv electric
76.00 | Supply of 600mm Sweep, High speed, 300CFM Air delivery, 1400 RPM, Heavy duty, metal body Air Circulator with wide oscillating aerodynamic metal blades, 100% copper motor for longer performance, regulator based speed control for easy operations, easy tilting with unique pivot arrangement with all accessories suitable for operation on 230V AC supply etc., as required. | 18.00 | Each | 10.00 | 14175.00 | 255150.00 | 10000.00 | 180000.00 | 3500.00 | 63000.00 | 63000.00 | sri sai leela electrical projects
77.00 | Supply of 600mm Sweep, 900RPM, Industrial, Heavy duty, High speed, metal body, oil and dust lacquer, 100% copper motor for longer performance, Exhaust fan with fan blade complete with with all accessories suitable for operation on 230V AC supply etc., as required. | 12.00 | Each | 10.00 | 10000.00 | 120000.00 | 8000.00 | 96000.00 | 4000.00 | 48000.00 | 48000.00 | sri sai leela electrical projects
78.00 | Installation testing commissioning of all type of LED luminaries, ceiling fans, exhust fans, air circulators etc., including all necessary accessories / clamp / washers / metal chain on recess / surface / nut & bolts / wall bracket / Wall mounted of height up to 10 mtrs etc., as required. | 145.00 | Job | 10.00 | 100.00 | 14500.00 | 300.00 | 43500.00 | 900.00 | 130500.00 | 14500.00 | shiv electric
79.00 | Design, Fabrication and SITC of 2 x 10 KVA, 3 Ph - 3 Ph, 50Hz, in Parallel Redundant Configuration Online UPS System in dust and vermin proof cubicle panel duly painted and with ventillation ducts, floor mounted comprising a set of SMF 12V batteries of suitable capacity arranged in racks with terminal and all accessories, forced air cooling, back up time minimum 60 minutes and capable of giving desired output and suitable to operate inductive loads and building lighting and as per the particular specifications of contract complete as required. | 1.00 | Set | 10.00 | 1006512.00 | 1006512.00 | 970000.00 | 970000.00 | 650000.00 | 650000.00 | 650000.00 | sri sai leela electrical projects
80.00 | Supply of single mode, 6 Core Fiber, multitude, wide range of armoured Optical Fiber Cable including all dielectric with self suporting, primary coated with double UV Curved acrylate, conforming to IEC-794, ITU-T, TC-55-2000 with upto date ammendments etc., complete as required. | 7500.00 | Mtr | 10.00 | 36.00 | 270000.00 | 40.00 | 300000.00 | 120.00 | 900000.00 | 270000.00 | shiv electric
81.00 | Supply of 10Core x 2.5 Sq.mm XLPE insulated and PVC sheathed copper conductor armoured control cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date amendments etc.,complete as required. | 1000.00 | Mtr | 10.00 | 400.00 | 400000.00 | 300.00 | 300000.00 | 485.00 | 485000.00 | 300000.00 | ASIATIC TRADERS
82.00 | Making horizontal boring of suitable dia. by using suitable mechanical arrangement, Sensor operated, Minimum 2.5Mtr Depth, horizontal bore well suitable for inserting of 03Nos of 40mm dia. HDPE Pepes. Job including supplying and laying of 3 Nos., 40mm dia. PE-100 Grade, PN-8, HDPE Pipe in borewell hole including jointing, molding cutting, bending etc. of pipes in boring hole and soil excavation for boring as per site condition complete is required | 1800.00 | Mtr | 10.00 | 600.00 | 1080000.00 | 400.00 | 720000.00 | 2600.00 | 4680000.00 | 720000.00 | ASIATIC TRADERS
83.00 | Making horizontal boring of dia. not less than 75mm by using suitable mechanical arrangement, Sensor operated, Minimum 2.5Mtr Depth, horizontal bore well suitable for inserting of 90mm dia., HDPE Pipes. Job including supplying and laying of 90mm dia. PE-100 Grade, PN-8, HDPE Pipe in borewell hole including jointing, molding cutting, bending, etc. of pipes in boring hole and soil excavation for boring as per site condition complete is required. | 850.00 | Mtr | 10.00 | 648.00 | 550800.00 | 250.00 | 212500.00 | 3000.00 | 2550000.00 | 212500.00 | ASIATIC TRADERS
84.00 | Laying of one number PVC insulated and PVC sheathed, armoured control cable / OFC Cable / Power cable of 1.1 KV grade of following size in the existing RCC / HUME / METAL / DWC / HDPE pipe as required. Up to 35 sq.mm | 7000.00 | Mtr | 10.00 | 30.00 | 210000.00 | 20.00 | 140000.00 | 50.00 | 350000.00 | 140000.00 | ASIATIC TRADERS
85.00 | Laying of one number HDPE Pipe for laying of PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Up to 35 sq.mm | 400.00 | Mtr | 10.00 | 100.00 | 40000.00 | 30.00 | 12000.00 | 80.00 | 32000.00 | 12000.00 | ASIATIC TRADERS
86.00 | Supplying and making end termination with brass double compression gland and copper lugs for 10 Core x 2.5 Sq.mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each | 10.00 | 800.00 | 1600.00 | 300.00 | 600.00 | 600.00 | 1200.00 | 600.00 | ASIATIC TRADERS
87.00 | Supply, Installation, Testing and Commissioning of latest model, upgraded features, Touch Monitoring system at new ATC tower which is 3KM away from the existing CCR Hall for control and monitoring the CCRs/AFLs etc with IPC Software license and programming system suitable for operation of existing NASU Make Airfied lighting control monitoring system (ALCMS) complete with all respect as per site condition as required. Note: The Touch Monitor shall be dell make of 23.8'' and the IPC shall be Nasu systems Make. The IPC shall be suitable with pre-loaded ALCMS software so as to integrate with the existing ALCMS system. IPS shall have i7 processor, 16GB ram and minimum 500GB SSD. | 2.00 | Job | 10.00 | 910000.00 | 1820000.00 | 750000.00 | 1500000.00 | 250000.00 | 500000.00 | 500000.00 | sri sai leela electrical projects
88.00 | Supply, Installation, Testing and Commissioning of Networtk adaptor with configuration and networking system in the new ATC Tower suitable for operation of existing NASU Make Airfied lighting control monitoring system (ALCMS) complete with all respect as per site condition as required. Note: Network adapter shall be Nasu Systems Make. The network adapter shall be compatible to communicate with existing ALCMS system of Nasu make which is 3KM away from the New ATC Tower. The network adapter shall have dual power supply for redundancy | 2.00 | Job | 10.00 | 286000.00 | 572000.00 | 280000.00 | 560000.00 | 125000.00 | 250000.00 | 250000.00 | sri sai leela electrical projects
89.00 | Integartion of above Touch monitoring system and network adaptor with existing ALCMS System etc., as required. | 1.00 | Job | 10.00 | 552000.00 | 552000.00 | 450000.00 | 450000.00 | 75000.00 | 75000.00 | 75000.00 | sri sai leela electrical projects
90.00 | Design, Supplying, Installation, Testing and Commissioning of 20KL M.S Tank for capacity fuel storage, fabricated out of 6mm thick M.S Plate with bracing's inside for providing strength to sheet metal work, complete with all standard apparatus / mountings like manhole of 600mm dia and cover duly hinged, access ladders, lifting lugs, earthing bolts etc. Dish ends of 8mm thick M.S sheet, fuel fill pipe 80mm dia with locking arrangement, vent pipe, outlet pipe Brass dip stick, with calibrator chart (As per IS Code 10987 – 1992 Tank fabricated from MS sheet of 6mm thickness and two level indicators. The tank shall be duly painted with two coats of tank mastic and two coats of Tar Plastic paints outside of tank and any other treatment required for corrosioin resistance as per standard practice and requirement. Tank shall be provided with level switches High / Low with required electrical wiring,,control and control gears. The rates quoted shall be complete with connected civil work including excavation, half round RCC foundation as required, completes with foundation bolts and strappings duly anchored to foundations, sand fill, disposal of surplus earth, debris as required for installation of tank including firefighting system, security fencing, etc. as required liassioning and obtaining explosive Certificate from PESO with concerned Govt. Authorities and NOC local Authorities getting permission shall be contractors responsibility. Tank to be hydraulically tested to meet requisite standard / 3m water columns head whichever is higher. Certificate to the above affect is required. Any other functional requirement as per site condition shall also deem to have been included in the scope of this item. | 1.00 | Job | 10.00 | 1690000.00 | 1690000.00 | 1000000.00 | 1000000.00 | 950000.00 | 950000.00 | 950000.00 | sri sai leela electrical projects
91.00 | Supply, installation, testing and commissioning of 2HP, Flame proof, high efficiency, balanced rotating parts, prevent over loading, Automatic air release designed centrifugal Selfpriming / Monoblock pump set for fuel (diesel) transmission with 40mm delivery size consisting of oil filled squirrel cage motor with IP-65 protection, suitable for operation on 415V, 50Hz, 3 Phase AC Supply with impellers, oil lubricated bearings, tie-bars on studs bolts for connecting the pumps together suitale length suction pipe (MS Pipe), foot valve sleeve coupling to connect motor shaft to the pump shaft along with all accessories to give a minimum discharge of 150 LPM at a total head of 30 Meters complete as required. | 2.00 | Each | 10.00 | 100000.00 | 200000.00 | 25000.00 | 50000.00 | 14000.00 | 28000.00 | 28000.00 | sri sai leela electrical projects
92.00 | Fabrication, supply, installation, testing and commissioning of indoor type pre-wired pump control panel with double door with locking arrangement made out of 3mm thick outer sheet and 2mm thick inner sheet steel, dust tight, vermin proof, totally enclosed, cubicle type panel box suitable for operation of 3 phase, Monoblock / selfpriming pump sets up to 2HP, complete with DOL Starter, 32A 3P MCB/MCCB, Overload relay, push button, Power Contactor, connectors, multifunction meter, Indication lamps, Internal wiring along with suitable length (i.e. pump to control panel) of 4Sq.mm copper conductor flat cable and laying in PVC Pipe with all accessories, interconnection, connection, earthing termination, painting, cable entry provision etc. as required. | 2.00 | Job | 10.00 | 40000.00 | 80000.00 | 5000.00 | 10000.00 | 10000.00 | 20000.00 | 10000.00 | ASIATIC TRADERS
93.00 | Fabrication, supply, erection, installation, testing and commissioning of 40 mm dia., 6mm Thick, M.S. Black Heavy-duty Pipe (Class-C) IS Marked 1239, Part-1, IS :3589 Including cutting, welding / threading with accessories like tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts etc., including providing and fixing of 4mm thick multilayer pypkote anti corrosive tar coal based insulation coating and wrapping for pipe protection, with tar coal based primer pipe coating for underground pipes and painting with two coats of synthetic enamel paint after primer coat for open pipe, adequately supported on rigid supports / concealed on floor as per specification etc., complete in all respects. | 50.00 | Mtr | 10.00 | 1000.00 | 50000.00 | 500.00 | 25000.00 | 2000.00 | 100000.00 | 25000.00 | ASIATIC TRADERS
94.00 | Supply, installation, testing & commissioning of Calibrated HSD buffer / service tank, rectangular MS (IS:226) construction with 990 liters capacity complete with flanged inlet & outlet, overflow, drain, vent, mechanical level indicator, 450mm dia Access hole on top with cover, flame arrestor. Tank will be made out of 6mm MS sheet and will be provided with structural support to keep tank base at (3Mtr) above FFL with access ladder arrangement, painting etc. complete as required. | 1.00 | Job | 10.00 | 75000.00 | 75000.00 | 30000.00 | 30000.00 | 50000.00 | 50000.00 | 30000.00 | ASIATIC TRADERS
95.00 | Supply, installation, testing and commissioning of following accessories suitable for 40mm dia. MS Pipe complete as required.
95.01 | 40mm dia. Forged brass ball valve with PN-16 Pressure Rating, | 4.00 | Each | 10.00 | 5000.00 | 20000.00 | 2000.00 | 8000.00 | 1250.00 | 5000.00 | 5000.00 | sri sai leela electrical projects
95.02 | 40mm dia., PN-16 pressure rating, SS Body, SS Disc, lever operated, butterfly valves | 4.00 | Each | 10.00 | 8000.00 | 32000.00 | 3000.00 | 12000.00 | 2500.00 | 10000.00 | 10000.00 | sri sai leela electrical projects
95.03 | 40mm dia., IS: 5312, DI Body, SS Disc, Non-return valves | 2.00 | Each | 10.00 | 7500.00 | 15000.00 | 1500.00 | 3000.00 | 6500.00 | 13000.00 | 3000.00 | ASIATIC TRADERS
95.04 | 40mm dia., C.I / SS Body, Y Strainer with Flanged end epoxy caoted with SS Screen. | 2.00 | Each | 10.00 | 10530.00 | 21060.00 | 2000.00 | 4000.00 | 7500.00 | 15000.00 | 4000.00 | ASIATIC TRADERS
96.00 | Fabrication, supply, erection, installation, testing and commissioning of 25 mm dia., 6mm Thick, M.S. Black Heavy-duty Pipe (Class-C) IS Marked 1239, Part-1, IS :3589 Including cutting, welding / threading with accessories like tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts etc., including providing and fixing of 4mm thick multilayer pypkote anti corrosive tar coal based insulation coating and wrapping for pipe protection, with tar coal based primer pipe coating for underground pipes and painting with two coats of synthetic enamel paint after primer coat for open pipe, adequately supported on rigid supports / concealed on floor as per specification etc., complete in all respects. | 30.00 | Mtr | 10.00 | 541.00 | 16230.00 | 350.00 | 10500.00 | 1300.00 | 39000.00 | 10500.00 | ASIATIC TRADERS
97.00 | Supply, installation, testing and commissioning of following accessories suitable for 25mm dia. MS Pipe complete as required.
97.01 | 25mm dia. Forged brass ball valve with PN-16 Pressure Rating, | 3.00 | Each | 10.00 | 2500.00 | 7500.00 | 1000.00 | 3000.00 | 3200.00 | 9600.00 | 3000.00 | ASIATIC TRADERS
97.02 | 25mm dia., PN-10 pressure rating, SG Iron, lever operated, butterfly valves | 3.00 | Each | 10.00 | 4000.00 | 12000.00 | 1000.00 | 3000.00 | 3500.00 | 10500.00 | 3000.00 | ASIATIC TRADERS
98.00 | Providing and laying in position cement concrete 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation / road crossing etc., including form work etc as required. | 6.00 | Cum | 10.00 | 8000.00 | 48000.00 | 10000.00 | 60000.00 | 9500.00 | 57000.00 | 48000.00 | shiv electric
99.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand). Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels as required. | 24.00 | Sqm | 10.00 | 7000.00 | 168000.00 | 5000.00 | 120000.00 | 4500.00 | 108000.00 | 108000.00 | sri sai leela electrical projects
100.00 | Supply, Installation, Testing & Commissioning of Two Loop Panel UL / EN listed (latest version) Modular Microprocessor based expandable intellegent Addressable Type Fire Alarm Control Panel of following loops, with minimum 320 character graphics / LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM) ,The panel should be equiped with loop capacity to take minimum 240 intellegent addressable detectors/ devices (In any combination ) in one loop. 230 volts, 50 Hz AC power supply, automatic battery charger, 24 volts sealed maintenance free lead acid batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency / fault conditions along with battery stand as required. The panel shall have facility for seamless integration. The panel shall be compatible for Building Management System with open protocol BACNET / MODBUS / Auto Dialler etc. as per specification, complete as required. | 1.00 | Each | 10.00 | 214500.00 | 214500.00 | 380000.00 | 380000.00 | 284031.00 | 284031.00 | 214500.00 | shiv electric
101.00 | Supplying, installation, testing & commissioning of intelligent analogue addressable Multi criteria detector complete with mounting base complete as required. | 60.00 | Each | 10.00 | 3575.00 | 214500.00 | 3500.00 | 210000.00 | 2800.00 | 168000.00 | 168000.00 | sri sai leela electrical projects
102.00 | Supplying, installation, testing & commissioning of addressable manual call point complete as required. | 5.00 | Each | 10.00 | 5005.00 | 25025.00 | 7500.00 | 37500.00 | 4500.00 | 22500.00 | 22500.00 | sri sai leela electrical projects
103.00 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required. | 3.00 | Each | 10.00 | 4575.00 | 13725.00 | 4500.00 | 13500.00 | 3750.00 | 11250.00 | 11250.00 | sri sai leela electrical projects
104.00 | Supplying & laying of 2Cx1.5 Sq.mm fire alarm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLSH outer sheath on existing wall / in pipe / surface etc., complete as required. | 700.00 | Mtr | 10.00 | 100.00 | 70000.00 | 300.00 | 210000.00 | 100.00 | 70000.00 | 70000.00 | sri sai leela electrical projects, shiv electric
105.00 | Fabrication, supply, erection, installation, testing and commissioning of 150 mm dia., 6mm Thick, M.S. Black Heavy-duty Pipe (Class-C) IS Marked 1239, Part-1, IS :3589 Including cutting, welding / threading with accessories like tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts etc., including providing and fixing of 4mm thick multilayer pypkote anti corrosive tar coal based insulation coating and wrapping for pipe protection, with tar coal based primer pipe coating for above ground pipes and painting with one coat of primer and two or more coats of synthetic enamel red paint of approved brand including preparation of base surface as per recommendations of manufacturer to make clean the surface fire hydrant line adequately supported to provision of PCC foundation supports at every 3 meter for open pipe line per specification etc., complete in all respects. | 150.00 | Mtr | 10.00 | 3000.00 | 450000.00 | 1500.00 | 225000.00 | 2520.00 | 378000.00 | 225000.00 | ASIATIC TRADERS
106.00 | Fabrication, supply, erection, installation, testing and commissioning of 80 mm dia., 6mm Thick, M.S. Black Heavy-duty Pipe (Class-C) IS Marked 1239, Part-1, IS :3589 Including cutting, welding / threading with accessories like tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts etc., including providing and fixing of 4mm thick multilayer pypkote anti corrosive tar coal based insulation coating and wrapping for pipe protection, with tar coal based primer pipe coating for above ground pipes and painting with one coat of primer and two or more coats of synthetic enamel red paint of approved brand including preparation of base surface as per recommendations of manufacturer to make clean the surface fire hydrant line adequately supported to provision of PCC foundation supports at every 3 meter for open pipe line per specification etc., complete in all respects. | 24.00 | Mtr | 10.00 | 1800.00 | 43200.00 | 500.00 | 12000.00 | 1900.00 | 45600.00 | 12000.00 | ASIATIC TRADERS
107.00 | Fabrication, supply, erection, installation, testing and commissioning of double door type fire hydrant hose box (Size 1000MM x 600MM x 450MM) made of 16 Gauge, M.S. Sheet having central opening with powder coated fire red paint, Glass fronted doors with locks with two keys provided separate compatment with brekable glass recess for keys in same box. The hydrant hose box is suitable to accommodate 1 No. of 15mtr lengths of (Type-A) delivery house and 01 no. branch pipe. Job including provision of suitable support / stand for house box etc. The entire system painted with one coat of primer and two or more coats of synthetic enamel red paint of approved brand including preparation of base surface as per recommendations of manufacturer to make clean the surface of box complete as required. | 4.00 | Job | 10.00 | 6075.00 | 24300.00 | 10000.00 | 40000.00 | 15000.00 | 60000.00 | 24300.00 | shiv electric
108.00 | Supply, installation, testing and commissining of 150mm dia., PN-16 pressure rating, C.I Body, SS Disc, lever and streering operated, Nitrile / EPDM Rubber lining butterfly valves complete with flanges, SS Boltings, nuts, washers, gaskets etc. complete as required. | 3.00 | Each | 10.00 | 7500.00 | 22500.00 | 5000.00 | 15000.00 | 8000.00 | 24000.00 | 15000.00 | ASIATIC TRADERS
109.00 | Supply, installation, testing and commissining of 80mm dia., PN-16 pressure rating, C.I Body, SS Disc, lever and streering operated, Nitrile / EPDM Rubber lining butterfly valves complete with flanges, SS Boltings, nuts, washers, gaskets etc. complete as required. | 4.00 | Each | 10.00 | 3191.00 | 12764.00 | 3000.00 | 12000.00 | 7500.00 | 30000.00 | 12000.00 | ASIATIC TRADERS
110.00 | Supply and fixing of single headed, stainless steel hydrant valve, oblique type 63mm dia with flanged inlet with blank cap and chain as per IS 5290 with ISI mark as required. | 4.00 | Each | 10.00 | 5670.00 | 22680.00 | 7500.00 | 30000.00 | 8500.00 | 34000.00 | 22680.00 | shiv electric
111.00 | Supply of and fixing of 63mm 15 mtr. Long, synthetic fiber circular woven jacketed, EPDM non percolating RRL fire hose pipe with 63 mm dia. with male & female gunmetal couplings as per specifications conforming to bearing IS 636-1988 Type-A as required. | 8.00 | Each | 10.00 | 6075.00 | 48600.00 | 7000.00 | 56000.00 | 7000.00 | 56000.00 | 48600.00 | shiv electric
112.00 | Supply and prividing of single headed, SS Jet nozile for hydrant system suitable to adequate 63mm dia fire hose pipe coupler as per IS 5290 with ISI mark as required. | 4.00 | Each | 10.00 | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 5000.00 | 20000.00 | 8000.00 | shiv electric
| Total in Figures |  |  |  |  | 81252722.00 |  | 67444300.00 |  | 87684591.00
Lowest Amount Quoted BY: ASIATIC TRADERS(67444300.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Power Supply System to ATC Tower cum Technical Block at Vijayawada airport. SH SITC Tender ID: 2024_AAI_199995_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ASIATIC TRADERS (BID ID -757012) | 67444300.00 | L1
| 2 | shiv electric (BID ID -757044) | 81252722.00 | L2
| 3 | sri sai leela electrical projects (BID ID -756657) | 87684591.00 | L3