## BoQ1
Government eProcurement System Created By: Narender Kumar Created Date/Time: 20-Sep-2024 03:11 PM Tender Title: Augmentation of Power Supply at Old Area Safdarjung Airport. Tender ID: 2024_AAI_201536_1
Tender Inviting Authority: Sr. Mgr., Airports Authority of India, Safdarjung Airport, New Delhi-110003.
Name of Work: Augmentation of Power Supply at Old Area Safdarjung Airport.
Contract No: AAI/SAP/Engg.(E)/OA/PS Augmentation/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -731649 |  | HIMALAYA GENERATORS (GSTN-09AEDPA0988G1ZL) BID ID -732054 |  | Leo Air and Power Solution Pvt Ltd., (GSTN-07AABCL1931F1ZW) BID ID -732291 |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)--731614 |  | Shiva Enterprises(GSTN-NA)--732572
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I:- SITC of DG Set & LT Panels
2.00 | Supplying, Installing, Testing and Commissioning of Silent Type diesel generating set alongwith having prime power rating of 625 KVA, 415 Volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz., 3-Phase system and for 0.85 Load factor and as per latest (CPCB-IV+ compliant norms) and consisting of the followings : (a) Diesel Engine : Diesel Engine 4 Stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at NTP conditions and conforming to latest IS / BS Version covering BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted completed with all the required accessories. (b) Engine mounted Instrument Panel fitted with and having digital display for following : (i) Start-Sop switch with key. (ii) Water temperature indication (iii) Lubrication oil pressure indication. (iv) Lubrication oil temperature indication. (v) Battery charging indication. (vi) RPM indication. (vii) Over speed indication. (viii) Low Lub.oil trip indication. (ix) Engine Hours indication. (Note:- Above indications may be incorporated multifunction units mounted on DG Set) (c) Alternator : Synchronous, alternator rated at 625 KVA, 415 Volts at 1500 RPM, 3-Phase 50 Hz., AC Supply with 0.8 lagging power factor at NTP condition. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class-H insulation. (d) Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendation of OEM, etc. complete as required at site (Including making of foundation as per OEM specification). (e) Fuel Tank : Separate Daily Service Fuel tank of 990 liters capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications and accessories as required as per specifications. (f) Exhaust System : Dry exhaust mainfold with hospital exhaust silencer and catalytic convertor. (g) Starting System : (h) 12V/24V DC starting system comprising of starter motors: Voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries as per OEM standard as required as per specifications. (e) Accoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine and alternator, extraction, discharging hot air into the atmosphere as per specifications. | 2.00 | Each | 100.00 | 8500000.00 | 17000000.00 | 7950000.00 | 15900000.00 | 6034107.00 | 12068214.00 | 9000000.00 | 18000000.00 | 6500000.00 | 13000000.00 | 12068214.00 | Leo Air and Power Solution Pvt Ltd.,
3.00 | Supplying and fixing of exhaust gas piping of suitable dia. for 625 KVA D.G. Set welded black MS, B (medium) Class pipe conforming to IS: 3589 cut to required lengths and installed with necessary bends, clamps, anti-vibration mountings, insulation of exhaust system with 50 mm thick Loosely bound resin (LBR) mattress/ mineral wool / Rockwool having density not less than 120 Kg / Cucm, wiremesh & cladding with 0.6 mm thick aluminum sheet etc. as required as per specifications. | 30.00 | Mtr | 100.00 | 8600.00 | 258000.00 | 9200.00 | 276000.00 | 6396.00 | 191880.00 | 7000.00 | 210000.00 | 9063.00 | 271890.00 | 191880.00 | Leo Air and Power Solution Pvt Ltd.,
4.00 | STRUCTURE FOR EXHAUST PIPING: Providing & fixing for MS support structure including civil foundation for exhaust fume pipes of DG Sets (Exhaust pipe to be measured and paid for separately) along horizontal and vertical runs and monkey ladder upto the height (as per CPCB norms) including cutting, welding etc and applying two coats of red oxide and two coats of synthetic enameled paint of colour and shade as directed by AAI. The design of the support structure shall be done by the contractor and shall be as per CPCB norms. Design and drawings shall be got vetted from IIT / REC before execution as per specifications as required. | 4500.00 | Kg | 10.00 | 170.00 | 765000.00 | 165.00 | 742500.00 | 132.00 | 594000.00 | 500.00 | 2250000.00 | 157.00 | 706500.00 | 594000.00 | Leo Air and Power Solution Pvt Ltd.,
5.00 | Supplying & fixing Stainless Steel Expansion Joints, Corrugated bellows for 625 KVA DG Sets to fit in exhaust pipe. | 10.00 | Nos | 10.00 | 6500.00 | 65000.00 | 14500.00 | 145000.00 | 5750.00 | 57500.00 | 2000.00 | 20000.00 | 3021.00 | 30210.00 | 20000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | ESSENTIAL PANEL (CRSD) Supply, Installation, Testing and Commissioning of cubicle type LT panel (TTA) indoor type , IP54 protection , 50 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor , cable alleys, cable gland plates in two half, i/c providing following switch gears :- | 1.00 | Nos | 10.00 | 2880000.00 | 2880000.00 | 2825000.00 | 2825000.00 | 2670900.00 | 2670900.00 | 2200000.00 | 2200000.00 | 1730000.00 | 1730000.00 | 1730000.00 | Shiva Enterprises
6.01 | (A) INCOMER i) 2 Nos 1000A, 4 Pole, 50KA, EDO, Microprocessor based release having short circuit, overload & Earth Fault protection ACB as Incomer for City Supply ii) 2 Nos 1000A, 4 Pole, 50KA, EDO, Microprocessor based release having short circuit, overload & Earth Fault protection ACB as Incomer for DG Supply Each ACB above shall be provided with i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection ii) 1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-800A) with CTs & SS for 3-Phase 4-Wire System with 2A SP MCB for Protection. iii) Breaker Control Switch 25A, 1P, Spring Return 1-T 2-CL 0-N iv) 1-Set of ON/OFF/Trip Indicating Lights with 2A SP MCB for Protection v) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. vi) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port
6.02 | (B) Bus Bars 4 Nos 1500A Electrolytic Aluminium Bus-Bars of equal cross-section. (C) BUS COUPLER i) 1 Nos 1000A, 4 Pole, 50KA, EDO, Thermal magnetic release ACB as Bus Coupler with LSIG Trip. ii) Breaker Control Switch 25A, 1P, Spring Return 1-T 2-CL 0-N iii) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection.
6.03 | (D) ACCESSORIES FOR ELECTRICAL INTERLOCKING. i) Electrical interlocking arrangement as per drawing and specifications among 2 nos. Incomers from City Supply, 02 nos. incomers from DG Supply and 1 nos. Bus coupler including interconnections etc. as required. (E) OUTGOINGS I: 4 Nos. MCCB, 400A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). I: 2 Nos. MCCB, 250A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). II: 01 Nos. MCCB, 100A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). III: 01 Nos. MCCB, 63A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each Outgoing MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port. ii) OFF/ON/Trip indicating LED lights with 2A SP MCB iii) 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs.
6.04 | (F) DG AMF LOGIC AMF ENGINE CONTROL RELAY AUX 8-36VDC, ANNUNCIATOR 04 WINDOWS 24V DC WITH P.B. HOOTER 220V AC DELCON 1 BATT CHR 230V AC 24V DC 10A W 3 INDICATION & 1 PROTECTION AMMETER ANALOG 15A DC DIRECT 96 SQMM VOLTMETER 30V DC DIRECT 96 SQMM 04 nos. AUX RELAY 220/240VAC 4C/O PUSH BUTTON RED WITH 1NC PUSH BUTTON GREEN WITH 1NO EM STOP PUSH BUTTON RED TURN TO RELEASE INDICATING LIGHT RED 220V AC 22.5MM DIA INDICATING LIGHT GREEN 220V AC 22.5MM DIA AUX CONTROL RELAY WITH 2NO+2NC 220V AC TIMER MULTIFUNCTION 2C/O 0.1SEC-10HR 24-240VAC/DC GIC 1 04 no.s MCB SP 2A 10KA C-CURVE
7.00 | NON- ESSENTIAL PANEL (CRSD SUB-STATION) Supply, Installation, Testing and Commissioning of cubicle type LT panel (TTA) indoor type , IP54 protection , 50 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor , cable alleys, cable gland plates in two half, i/c providing following switch gears :- | 1.00 | Nos | 10.00 | 2540000.00 | 2540000.00 | 2750000.00 | 2750000.00 | 2471728.00 | 2471728.00 | 2000000.00 | 2000000.00 | 2020000.00 | 2020000.00 | 2000000.00 | JCC ENGINEERS PRIVATE LIMITED
7.01 | (A) INCOMER i) 2 Nos 1250A, 4 Pole, 50KA, EDO,Microprocessor based release having short circuit, overload & Earth Fault protection ACB as Incomer for City Supply Each ACB above shall be provided with i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection ii) 1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-800A) with CTs & SS for 3-Phase 4-Wire System with 2A SP MCB for Protection. iii) Breaker Control Switch 25A, 1P, Spring Return 1-T 2-CL 0-N iv) 1-Set of ON/OFF/Trip Indicating Lights with 2A SP MCB for Protection v) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. vi) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port
7.02 | (B) Bus Bars 4 Nos 1500A Electrolytic Aluminium Bus-Bars of equal cross-section. (C) BUS COUPLER i) 1 Nos 1250A, 4 Pole, 50KA, EDO, Thermal magnetic release ACB as Bus Coupler with LSIG Trip. ii) Breaker Control Switch 25A, 1P, Spring Return 1-T 2-CL 0-N iii) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. (D) ACCESSORIES FOR ELECTRICAL INTERLOCKING. i) Electrical interlocking arrangement as per drawing and specifications among 2 nos. Incomers from City Supply and 1 nos. Bus coupler including interconnections etc. as required.
7.03 | (E) OUTGOINGS i) 2 Nos 1000A, 4 Pole, 50KA, EDO, Microprocessor based release having short circuit, overload & Earth Fault protection ACB, ii) 3 Nos. MCCB, 400A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). iii) 04 Nos. MCCB, 100A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). iv) 01 Nos. MCCB, 63A, 35/36 kA, Four Pole, with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each Outgoing MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port ii) OFF/ON/Trip indicating LED lights with 2A SP MCB iii) Breaker Control Switch 25A, 1P, Spring Return (1-T 2-CL 0-N) for ACB only iv) 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs.
8.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel indoor type , IP54 protection , 35/36 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 35/36 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor , cable alleys, cable gland plates in two half, i/c providing following switch gears :- (A) INCOMER i) 21 Nos. MCCB, 100A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each incomer above shall be provided with i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection ii) 1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-100A) with CTs & SS for 3-Phase 4-Wire System with 2A SP MCB for Protection. iii) 1-Set of ON/OFF/Trip Indicating Lights with 2A SP MCB for Protection iv) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. v) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port (B) Bus Bars 4 Nos 100A Electrolytic Aluminium Bus-Bars of equal cross-section. (C) BUS COUPLER i) 5 Nos. 63, 4 Pole, MCCB having Thermal Magnetic release Each Outgoing MCCB above shall be provided with; i) OFF/ON/Trip indicating LED lights with 2A SP MCB ii) 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. | 2.00 | Nos | 10.00 | 175000.00 | 350000.00 | 325000.00 | 650000.00 | 203148.00 | 406296.00 | 125000.00 | 250000.00 | 156000.00 | 312000.00 | 250000.00 | JCC ENGINEERS PRIVATE LIMITED
9.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel indoor type , IP54 protection , 35/36 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 35/36 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor , cable alleys, cable gland plates in two half, i/c providing following switch gears :- (A) INCOMER i) 1 Nos. MCCB, 160A, 35/36 kA, Four Pole , with microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each incomer above shall be provided with i) 1-No, 96 mm sq. Flush pattern Digital Voltmeter( 0-500V) with SS for 3-Phase 4-Wire System with 2A HRC Fuses for Protection ii) 1-No, 96 mm sq. Flush pattern Digital Type Ammeter ( 0-100A) with CTs & SS for 3-Phase 4-Wire System with 2A SP MCB for Protection. iii) 1-Set of ON/OFF/Trip Indicating Lights with 2A SP MCB for Protection iv) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. v) 16 Parameter Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,HZ,P.F & THD etc. The MFM to be duly equipped with RS-485 Port (B) Bus Bars 4 Nos 200A Electrolytic Aluminium Bus-Bars of equal cross-section. (C) OUTGOINGS i) 8 Nos. 63, 4 Pole, MCCB having Thermal Magnetic release Each Outgoing MCCB above shall be provided with; i) OFF/ON/Trip indicating LED lights with 2A SP MCB ii) 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. | 1.00 | Nos | 10.00 | 290000.00 | 290000.00 | 275000.00 | 275000.00 | 267030.00 | 267030.00 | 150000.00 | 150000.00 | 165000.00 | 165000.00 | 150000.00 | JCC ENGINEERS PRIVATE LIMITED
10.00 | SH-II: Supply Cables & Laying
11.00 | Supply of following sizes of Copper Power Cables,multi stranded conductor, XLPE Insulated, cores laid up, PVC tape Inner sheathed for Multicore cables, Armoured, ,650/1100V grade as per IS 7098(Part 1) 1988.
11.01 | 4C x 10 sqmm armoured | 150.00 | Mtr | 10.00 | 610.00 | 91500.00 | 600.00 | 90000.00 | 476.00 | 71400.00 | 1000.00 | 150000.00 | 577.00 | 86550.00 | 71400.00 | Leo Air and Power Solution Pvt Ltd.,
11.02 | 12C x 2.5 sqmm Armoured | 350.00 | Mtr | 10.00 | 465.00 | 162750.00 | 610.00 | 213500.00 | 401.00 | 140350.00 | 800.00 | 280000.00 | 468.00 | 163800.00 | 140350.00 | Leo Air and Power Solution Pvt Ltd.,
12.00 | Supply of following size of 1.1 kv grade multicore aluminium conductor, XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
12.01 | 4 core, 10 Sq.mm. | 50.00 | Mtr | 10.00 | 140.00 | 7000.00 | 175.00 | 8750.00 | 112.00 | 5600.00 | 300.00 | 15000.00 | 138.00 | 6900.00 | 5600.00 | Leo Air and Power Solution Pvt Ltd.,
12.02 | 4 core, 16 Sq.mm. | 100.00 | Mtr | 10.00 | 150.00 | 15000.00 | 185.00 | 18500.00 | 122.00 | 12200.00 | 400.00 | 40000.00 | 165.00 | 16500.00 | 12200.00 | Leo Air and Power Solution Pvt Ltd.,
12.03 | 3½ core, 25 Sq.mm. | 50.00 | Mtr | 10.00 | 190.00 | 9500.00 | 265.00 | 13250.00 | 168.00 | 8400.00 | 500.00 | 25000.00 | 192.00 | 9600.00 | 8400.00 | Leo Air and Power Solution Pvt Ltd.,
12.04 | 3½ core, 35 Sq.mm. | 100.00 | Mtr | 10.00 | 240.00 | 24000.00 | 310.00 | 31000.00 | 193.00 | 19300.00 | 650.00 | 65000.00 | 236.00 | 23600.00 | 19300.00 | Leo Air and Power Solution Pvt Ltd.,
12.05 | 3½ core, 50 Sq.mm. | 100.00 | Mtr | 10.00 | 325.00 | 32500.00 | 385.00 | 38500.00 | 256.00 | 25600.00 | 700.00 | 70000.00 | 317.00 | 31700.00 | 25600.00 | Leo Air and Power Solution Pvt Ltd.,
12.06 | 3½ core x 70 Sq.mm | 10.00 | Mtr | 10.00 | 430.00 | 4300.00 | 495.00 | 4950.00 | 343.00 | 3430.00 | 800.00 | 8000.00 | 430.00 | 4300.00 | 3430.00 | Leo Air and Power Solution Pvt Ltd.,
12.07 | 3½ core x 95 Sq.mm | 10.00 | Mtr | 10.00 | 545.00 | 5450.00 | 625.00 | 6250.00 | 377.00 | 3770.00 | 1000.00 | 10000.00 | 536.00 | 5360.00 | 3770.00 | Leo Air and Power Solution Pvt Ltd.,
12.08 | 3½ core X 120 Sq.mm. | 100.00 | Mtr | 10.00 | 680.00 | 68000.00 | 750.00 | 75000.00 | 465.00 | 46500.00 | 1200.00 | 120000.00 | 1256.00 | 125600.00 | 46500.00 | Leo Air and Power Solution Pvt Ltd.,
12.09 | 3½ core X 300 Sq.mm. | 900.00 | Mtr | 10.00 | 1560.00 | 1404000.00 | 1950.00 | 1755000.00 | 1107.00 | 996300.00 | 2900.00 | 2610000.00 | 1534.00 | 1380600.00 | 996300.00 | Leo Air and Power Solution Pvt Ltd.,
13.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
13.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 10.00 | Mtr | 10.00 | 1100.00 | 11000.00 | 1200.00 | 12000.00 | 695.00 | 6950.00 | 1000.00 | 10000.00 | 483.00 | 4830.00 | 4830.00 | Shiva Enterprises
13.02 | 450 mm width X 50 mm depth X 2.0 mm thickness | 10.00 | Mtr | 10.00 | 1680.00 | 16800.00 | 1500.00 | 15000.00 | 1276.00 | 12760.00 | 1500.00 | 15000.00 | 725.00 | 7250.00 | 7250.00 | Shiva Enterprises
13.03 | 900 mm width X 62.5 mm depth X 2.0 mm thickness | 30.00 | Mtr | 10.00 | 3220.00 | 96600.00 | 2750.00 | 82500.00 | 2088.00 | 62640.00 | 2500.00 | 75000.00 | 965.00 | 28950.00 | 28950.00 | Shiva Enterprises
14.00 | Earthing
15.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 10.00 | 10000.00 | 20000.00 | 7800.00 | 15600.00 | 6135.00 | 12270.00 | 7500.00 | 15000.00 | 10876.00 | 21752.00 | 12270.00 | Leo Air and Power Solution Pvt Ltd.,
16.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 10.00 | 21000.00 | 84000.00 | 13800.00 | 55200.00 | 12748.00 | 50992.00 | 18000.00 | 72000.00 | 19300.00 | 77200.00 | 50992.00 | Leo Air and Power Solution Pvt Ltd.,
17.00 | Supply, Installation, Testing and Commissioning of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 250 microns of copper plating, UL listed. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min, Approvals- Tested acc. IEC / EN 62561-2, UL 467, 20 kg backfilled compound, - Material Carbon based backfill/earthing compound, Resistivity- < 0.12 ΩM, Complying Standard- IEC 62561-7 , Testing Approvals Certified from- NABL accredited Laboratories, StSt 316 grade clamp to terminate the load on earth electrode, Poly plastic pit cover of material- Polymer Body & Cover. | 6.00 | Nos | 10.00 | 14000.00 | 84000.00 | 8000.00 | 48000.00 | 9258.00 | 55548.00 | 25000.00 | 150000.00 | 6040.00 | 36240.00 | 36240.00 | Shiva Enterprises
18.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm). | 20.00 | Mtr | 10.00 | 1450.00 | 29000.00 | 1300.00 | 26000.00 | 1045.00 | 20900.00 | 1000.00 | 20000.00 | 1230.00 | 24600.00 | 20000.00 | JCC ENGINEERS PRIVATE LIMITED
19.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm). | 20.00 | Mtr | 10.00 | 420.00 | 8400.00 | 120.00 | 2400.00 | 162.00 | 3240.00 | 150.00 | 3000.00 | 280.00 | 5600.00 | 2400.00 | HIMALAYA GENERATORS
20.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtr | 10.00 | 2000.00 | 20000.00 | 1700.00 | 17000.00 | 1405.00 | 14050.00 | 1500.00 | 15000.00 | 1450.00 | 14500.00 | 14050.00 | Leo Air and Power Solution Pvt Ltd.,
21.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtr | 10.00 | 900.00 | 9000.00 | 400.00 | 4000.00 | 522.00 | 5220.00 | 600.00 | 6000.00 | 580.00 | 5800.00 | 4000.00 | HIMALAYA GENERATORS
22.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 5.00 | Mtr | 10.00 | 1380.00 | 6900.00 | 1300.00 | 6500.00 | 1022.00 | 5110.00 | 1000.00 | 5000.00 | 1200.00 | 6000.00 | 5000.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 5.00 | Mtr | 10.00 | 360.00 | 1800.00 | 120.00 | 600.00 | 139.00 | 695.00 | 200.00 | 1000.00 | 253.00 | 1265.00 | 600.00 | HIMALAYA GENERATORS
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
24.01 | Upto 35 sq. mm | 15.00 | Mtr | 10.00 | 520.00 | 7800.00 | 200.00 | 3000.00 | 236.00 | 3540.00 | 250.00 | 3750.00 | 54.00 | 810.00 | 810.00 | Shiva Enterprises
24.02 | Above 185 sq. mm and upto 400 sq. mm | 30.00 | Mtr | 10.00 | 550.00 | 16500.00 | 250.00 | 7500.00 | 354.00 | 10620.00 | 300.00 | 9000.00 | 180.00 | 5400.00 | 5400.00 | Shiva Enterprises
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/PVC pipe as required
25.01 | Upto 35 sq. mm | 200.00 | Mtr | 10.00 | 58.00 | 11600.00 | 50.00 | 10000.00 | 58.00 | 11600.00 | 50.00 | 10000.00 | 36.00 | 7200.00 | 7200.00 | Shiva Enterprises
25.02 | Above 185 sq. mm and upto 400 sq. mm | 600.00 | Mtr | 10.00 | 70.00 | 42000.00 | 60.00 | 36000.00 | 81.00 | 48600.00 | 70.00 | 42000.00 | 145.00 | 87000.00 | 36000.00 | HIMALAYA GENERATORS
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
26.01 | Upto 35 sq. mm | 50.00 | Mtr | 10.00 | 57.00 | 2850.00 | 40.00 | 2000.00 | 47.00 | 2350.00 | 50.00 | 2500.00 | 36.00 | 1800.00 | 1800.00 | Shiva Enterprises
26.02 | Above 35 sq. mm and upto 95 sq. mm | 10.00 | Mtr | 10.00 | 70.00 | 700.00 | 45.00 | 450.00 | 59.00 | 590.00 | 50.00 | 500.00 | 48.00 | 480.00 | 450.00 | HIMALAYA GENERATORS
26.03 | Above 95 sq. mm and upto 185 sq. mm | 10.00 | Mtr | 10.00 | 80.00 | 800.00 | 50.00 | 500.00 | 71.00 | 710.00 | 70.00 | 700.00 | 96.00 | 960.00 | 500.00 | HIMALAYA GENERATORS
26.04 | Above 185 sq. mm and upto 400 sq. mm | 30.00 | Mtr | 10.00 | 92.00 | 2760.00 | 60.00 | 1800.00 | 83.00 | 2490.00 | 80.00 | 2400.00 | 120.00 | 3600.00 | 1800.00 | HIMALAYA GENERATORS
27.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
27.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 120.00 | Mtr | 10.00 | 80.00 | 9600.00 | 40.00 | 4800.00 | 92.00 | 11040.00 | 100.00 | 12000.00 | 48.00 | 5760.00 | 4800.00 | HIMALAYA GENERATORS
27.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 10.00 | Mtr | 10.00 | 92.00 | 920.00 | 45.00 | 450.00 | 127.00 | 1270.00 | 110.00 | 1100.00 | 48.00 | 480.00 | 450.00 | HIMALAYA GENERATORS
27.03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 10.00 | Mtr | 10.00 | 105.00 | 1050.00 | 50.00 | 500.00 | 150.00 | 1500.00 | 150.00 | 1500.00 | 72.00 | 720.00 | 500.00 | HIMALAYA GENERATORS
27.04 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 60.00 | Mtr | 10.00 | 115.00 | 6900.00 | 60.00 | 3600.00 | 173.00 | 10380.00 | 150.00 | 9000.00 | 96.00 | 5760.00 | 3600.00 | HIMALAYA GENERATORS
28.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
28.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 85.00 | Mtr | 10.00 | 75.00 | 6375.00 | 40.00 | 3400.00 | 92.00 | 7820.00 | 100.00 | 8500.00 | 48.00 | 4080.00 | 3400.00 | HIMALAYA GENERATORS
28.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 15.00 | Mtr | 10.00 | 86.00 | 1290.00 | 45.00 | 675.00 | 127.00 | 1905.00 | 110.00 | 1650.00 | 72.00 | 1080.00 | 675.00 | HIMALAYA GENERATORS
28.03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 153.00 | Mtr | 10.00 | 100.00 | 15300.00 | 50.00 | 7650.00 | 150.00 | 22950.00 | 150.00 | 22950.00 | 110.00 | 16830.00 | 7650.00 | HIMALAYA GENERATORS
28.04 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 60.00 | Mtr | 10.00 | 110.00 | 6600.00 | 60.00 | 3600.00 | 173.00 | 10380.00 | 150.00 | 9000.00 | 145.00 | 8700.00 | 3600.00 | HIMALAYA GENERATORS
29.00 | Supplying and fixing cable route marker with 10cmx10cmx 5 mm thick GI Plate with inscription thereon , bolted/ welded to 35x35x6 mm angle iron of 60 cm long and fixing the same in ground as required. | 4.00 | Each | 10.00 | 570.00 | 2280.00 | 450.00 | 1800.00 | 522.00 | 2088.00 | 500.00 | 2000.00 | 1200.00 | 4800.00 | 1800.00 | HIMALAYA GENERATORS
30.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required.
30.01 | 4 core, 10 Sq. mm | 11.00 | Each | 10.00 | 460.00 | 5060.00 | 300.00 | 3300.00 | 414.00 | 4554.00 | 200.00 | 2200.00 | 420.00 | 4620.00 | 2200.00 | JCC ENGINEERS PRIVATE LIMITED
30.02 | 4 core, 16 Sq. mm | 1.00 | Each | 10.00 | 520.00 | 520.00 | 300.00 | 300.00 | 534.00 | 534.00 | 250.00 | 250.00 | 500.00 | 500.00 | 250.00 | JCC ENGINEERS PRIVATE LIMITED
30.03 | 3½ core, 25 Sq.mm. | 14.00 | Each | 10.00 | 575.00 | 8050.00 | 360.00 | 5040.00 | 606.00 | 8484.00 | 300.00 | 4200.00 | 500.00 | 7000.00 | 4200.00 | JCC ENGINEERS PRIVATE LIMITED
30.04 | 3½ core, 35 Sq.mm. | 21.00 | Each | 10.00 | 630.00 | 13230.00 | 360.00 | 7560.00 | 654.00 | 13734.00 | 400.00 | 8400.00 | 570.00 | 11970.00 | 7560.00 | HIMALAYA GENERATORS
30.05 | 3½ core, 50 Sq.mm. | 2.00 | Each | 10.00 | 690.00 | 1380.00 | 421.00 | 842.00 | 759.00 | 1518.00 | 500.00 | 1000.00 | 620.00 | 1240.00 | 842.00 | HIMALAYA GENERATORS
30.06 | 3½ core x 70 Sq.mm | 2.00 | Each | 10.00 | 750.00 | 1500.00 | 480.00 | 960.00 | 814.00 | 1628.00 | 550.00 | 1100.00 | 652.00 | 1304.00 | 960.00 | HIMALAYA GENERATORS
30.07 | 3½ core x 95 Sq.mm | 9.00 | Each | 10.00 | 800.00 | 7200.00 | 480.00 | 4320.00 | 881.00 | 7929.00 | 600.00 | 5400.00 | 712.00 | 6408.00 | 4320.00 | HIMALAYA GENERATORS
30.08 | 3½ core X 120 Sq.mm. | 2.00 | Each | 10.00 | 860.00 | 1720.00 | 540.00 | 1080.00 | 940.00 | 1880.00 | 700.00 | 1400.00 | 920.00 | 1840.00 | 1080.00 | HIMALAYA GENERATORS
30.09 | 3½ core X 150 Sq.mm. | 2.00 | Each | 10.00 | 920.00 | 1840.00 | 600.00 | 1200.00 | 881.00 | 1762.00 | 1000.00 | 2000.00 | 990.00 | 1980.00 | 1200.00 | HIMALAYA GENERATORS
30.10 | 3½ core X 300 Sq.mm. | 3.00 | Each | 10.00 | 1265.00 | 3795.00 | 900.00 | 2700.00 | 1374.00 | 4122.00 | 1500.00 | 4500.00 | 1790.00 | 5370.00 | 2700.00 | HIMALAYA GENERATORS
31.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
31.01 | 4 core, 16 Sq. mm | 2.00 | Each | 10.00 | 2300.00 | 4600.00 | 1500.00 | 3000.00 | 1236.00 | 2472.00 | 1000.00 | 2000.00 | 4640.00 | 9280.00 | 2000.00 | JCC ENGINEERS PRIVATE LIMITED
31.02 | 3½ core, 25 Sq.mm. | 1.00 | Each | 10.00 | 2415.00 | 2415.00 | 3000.00 | 3000.00 | 1396.00 | 1396.00 | 1500.00 | 1500.00 | 4640.00 | 4640.00 | 1396.00 | Leo Air and Power Solution Pvt Ltd.,
31.03 | 3½ core, 35 Sq.mm. | 1.00 | Each | 10.00 | 2530.00 | 2530.00 | 3600.00 | 3600.00 | 1396.00 | 1396.00 | 1500.00 | 1500.00 | 5093.00 | 5093.00 | 1396.00 | Leo Air and Power Solution Pvt Ltd.,
31.04 | 3½ core, 50 Sq.mm. | 1.00 | Each | 10.00 | 2645.00 | 2645.00 | 4200.00 | 4200.00 | 1704.00 | 1704.00 | 1500.00 | 1500.00 | 5090.00 | 5090.00 | 1500.00 | JCC ENGINEERS PRIVATE LIMITED
31.05 | 3½ core x 70 Sq.mm | 1.00 | Each | 10.00 | 2760.00 | 2760.00 | 4200.00 | 4200.00 | 1704.00 | 1704.00 | 2000.00 | 2000.00 | 5093.00 | 5093.00 | 1704.00 | Leo Air and Power Solution Pvt Ltd.,
31.06 | 3½ core x 95 Sq.mm | 1.00 | Each | 10.00 | 2875.00 | 2875.00 | 4200.00 | 4200.00 | 1704.00 | 1704.00 | 2000.00 | 2000.00 | 5093.00 | 5093.00 | 1704.00 | Leo Air and Power Solution Pvt Ltd.,
31.07 | 3½ core X 120 Sq.mm. | 1.00 | Each | 10.00 | 2990.00 | 2990.00 | 4800.00 | 4800.00 | 1704.00 | 1704.00 | 2500.00 | 2500.00 | 6875.00 | 6875.00 | 1704.00 | Leo Air and Power Solution Pvt Ltd.,
31.08 | 3½ core X 150 Sq.mm. | 1.00 | Each | 10.00 | 3100.00 | 3100.00 | 4800.00 | 4800.00 | 1704.00 | 1704.00 | 3000.00 | 3000.00 | 6875.00 | 6875.00 | 1704.00 | Leo Air and Power Solution Pvt Ltd.,
32.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
32.01 | 3½ core X 300 Sq.mm. | 2.00 | Each | 10.00 | 5750.00 | 11500.00 | 7800.00 | 15600.00 | 3445.00 | 6890.00 | 5000.00 | 10000.00 | 7800.00 | 15600.00 | 6890.00 | Leo Air and Power Solution Pvt Ltd.,
33.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 1.50 | Cum | 10.00 | 5170.00 | 7755.00 | 6000.00 | 9000.00 | 6900.00 | 10350.00 | 8000.00 | 12000.00 | 5400.00 | 8100.00 | 7755.00 | DOSHI ELECTRIC ENGG. CO.
34.00 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels. | 5.00 | Sqm | 10.00 | 2875.00 | 14375.00 | 360.00 | 1800.00 | 230.00 | 1150.00 | 400.00 | 2000.00 | 2660.00 | 13300.00 | 1150.00 | Leo Air and Power Solution Pvt Ltd.,
35.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc. as required
35.01 | 100 mm dia | 30.00 | Mtr | 10.00 | 2200.00 | 66000.00 | 900.00 | 27000.00 | 1124.00 | 33720.00 | 1500.00 | 45000.00 | 785.00 | 23550.00 | 23550.00 | Shiva Enterprises
36.00 | Supply & Laying of following sizes DWC HDPE pipe ISI marked conforming to IS 14930, Part-II along with all acessories like socket, bend, couplers etc complete with fitting and cutting, jointing etc direct in ground (75 cm below ground level) including excavation & refilling the trench with same excavated earth but excluding sand cushioning and protective covering etc. , complete as required.
36.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 300.00 | Mtr | 10.00 | 240.00 | 72000.00 | 250.00 | 75000.00 | 180.00 | 54000.00 | 300.00 | 90000.00 | 126.00 | 37800.00 | 37800.00 | Shiva Enterprises
36.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 600.00 | Mtr | 10.00 | 360.00 | 216000.00 | 350.00 | 210000.00 | 225.00 | 135000.00 | 400.00 | 240000.00 | 171.00 | 102600.00 | 102600.00 | Shiva Enterprises
37.00 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable upto 3.3 KV, fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | 10.00 | Mtr | 10.00 | 870.00 | 8700.00 | 800.00 | 8000.00 | 986.00 | 9860.00 | 1500.00 | 15000.00 | 1270.00 | 12700.00 | 8000.00 | HIMALAYA GENERATORS
38.00 | SH-III APFC PANEL & OTHER EQUIPMENTS
39.00 | Design, supply, installation, testing & commissioning of cubicle type semi compartementalized floor mounted free standing type with configration of Static Var Generator and Active harmonic filter (300Kvar+150Amp), 415V, 50HZ, 3 phase 4 wire supply, moisture, dust and vermin proof IP-42 with cooling intrinsic design of voltage sourced IGBT based technology with multi modular design for parallel operation, intelligent 3-Level topology with 12 IGBT Hybrid PFC panel with Programmable Microprocessor controller to maintain Power Factor, Harmonics & Unbalancing duly housed in epoxy powder coated 2mm thick CRCA sheet steel compatmentalised enclosure free standing type with all supports, accessories, switch gears, control gears, protections, wiring, interconnections, control MCBs and maintain PF,I-THD,V-THD as per IEEE 519-2014 etc. as required. Also Certification Standard having surge test IEC61000-4-5, conducted suseptiablity IEC 61000-4-6 and fast transient test IEC61000-4-4 and IEC50178:1997, IEC 61000-6-2/ CISPR11 Group 1,Class A , IGBT based modules series performance comply EN 50091-3/IEC 62040-3/AS 62040 -3 (VFISS111), EN 61000-6-4 main components as below along with all other standard components, circuitry & specifications as required. | 1.00 | Job | 10.00 | 2090000.00 | 2090000.00 | 2750000.00 | 2750000.00 | 2037883.00 | 2037883.00 | 1650000.00 | 1650000.00 | 715000.00 | 715000.00 | 715000.00 | Shiva Enterprises
39.01 | INCOMMER 1 No. of 630 Amps. 415 Volts 4P. Type ACB. of 36KA with overload, S/C, O/C and earth fault protection. 1 No. of Display meter with compatible RS 485 ports. 3 No.of Phase Indicating & ON-OFF LED Lights 230 V. 1 Set. of Ammeter - digital 3 Phase. 3 No. of MCB 6A-SP-10kA-C-Curve. BUS BARS 800-Amps (neutral equal size) 3 phase 4 wire 415 volts 50 HZ aluminium bus bars with colour coded PVC heat shrinkable sleeves. OUTGOING (a) Active Harmonic Filter 150Amp - 1 Nos. (IGBT based active technology with gate driver, interfacing, voltage sensing & control cards, heat sinks, cooling fan, current tranducers, SMPS, SSR etc.) having following. 1 No of 100 Amp AHF module and 1 no of 50 Amps (3 -Level Topology, 12 IGBT Circuit) with proper rating of Surge protection devices. 1 No. of Programmable HMI With 7inches LED Display. Space future provision for 50 Amps module in the Panel. Configuration -3phase 4 wire Negative Sequence load current cancellation - It should work 1phase and 2 phase as well and Harmonics mitigation upto 51 th Level.
39.02 | (b) Static Var Generator 300 Kvar-1Nos. The Static Var Generator (SVG), 300 Kvar with 100/50 kVAr modular IGBT based design should be a power electronic device to be connected in parallel with the loads that require inductive and/or capacitive reactive powers, for their operation having following. 3 Nos of 100 Kvar SVG module (3 -Level Topology, 12 IGBT Circuit) with Proper Surge protection meeting The SVG should mitigate the Harmonics level upto 15th order The SVG should maintain power factor >=0.99. A 300 kVAR Static VAR Generator, in modular configuration, strictly as per attached specifications, as a complete system in all respect. The Static VAR Generator modules should consist of 3-Level IGBT inverter, housed in casing, with dedicated cooling, and necessary protections. The Static VAR Generator should perform inductive/capacitive reactive power correction, and capable to receive feedback from LT as well HT sides. Power losses shall be less than 3% per 100 KVAR module, This shall be designed for 50°C without derating. This shall have HMI displaying 3 phase active power, 3 phase apparent power, 3 phase displacement power factor, 3 line RMS voltage, 3 line current, 3 phase SVG current. Each module shall have separate protection MCCB. For easy repairability the IGBT driver cards shall be separate for different phases, separate common control cards and these should be fitted on main PCB. DC capacitors shall not be mounted on PCB. SVG shall used powder iron core instead of CRGO and LCL circuit to reduce noises created by switching frequency. The SVG shall also be suitable for unbalanced load usage. The Hybrid PQ Solution described as above complete in all respect as per specification enclosed, up to the entire satisfaction of engineer In Charge. To ensure safety, reliability and accountability of component co ordination, the SVG and AHF modules shall be of same OEM.
40.00 | Supply, Installation, Testing and Commissioning of smart energy management cloud server complete with Gateway, Data Base, Reporting tool, License Key and capable of integrating 50 number of devices including developing of the graphical screen, reporting formats etc. The cloud server shall also having capability to integrate with the existing EMS system and remote monitoring system through Web and LAN. The cloud server shall be compatible with windows based operating system and shall have the following minimum features complete as required: 1. Continuous Monitoring & Control of devices 2. View instantaneous parameters like voltage, current, power factor, temperature, humidity and all type of harmonics, parameters, e.g. power, kWh, KVAHr current, voltage, frequency, temperature etc. 3. Historical Trend patterns for any logged parameters such as electrical energy usage, power demand and any other logged parameter. Leverage these values In Excel to create detailed reports data storage 2 yrs. 4. Energies by day, energies by hour – analyses measured kilowatt-hours for cost allocation or comparison purpose. 5. Generation and transmission of alerts / notifications through e-mails and SMS. Included 2 yrs cloud service. Approved by CE/UL/NABL Make:- Schnieder/ Siemens/ Dehn/ Selec | 1.00 | Nos | 10.00 | 850000.00 | 850000.00 | 525000.00 | 525000.00 | 322680.00 | 322680.00 | 400000.00 | 400000.00 | 820000.00 | 820000.00 | 322680.00 | Leo Air and Power Solution Pvt Ltd.,
41.00 | SITC of 3 Phase / Type1+2 (KEMA/VDE Certified) Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single-pole combined lightning current and surge arrester, Type 1 SPD The device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350µs) of 25kA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV, Follow current extinguishing capability [L-N]/[N-PE] : 100kArms / 100Arms. The device shall have built in fuse and operation of SPD shall be independent of Line current for L?N SPD. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643-11:2011 or or EN 61643-11:2012 for testing of all parameter at 10/350 µs and 8/20 µs. with transparent enclosure IP65 | 2.00 | Set | 10.00 | 50000.00 | 100000.00 | 475000.00 | 950000.00 | 150300.00 | 300600.00 | 150000.00 | 300000.00 | 60000.00 | 120000.00 | 100000.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 29999365.00 |  | 30821227.00 |  | 23432668.00 |  | 31809000.00 |  | 22438478.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words (Iteration 0)
|  |  | Bidder Price | Amount in Words
1 | DOSHI ELECTRIC ENGG. CO. | 22438478.00 | 21092168.00 | Two Crore Ten Lakh Ninty Two Thousand One Hundred and Sixty Eight
2 | Leo Air and Power Solution Pvt Ltd., | 22438478.00 | Not Quoted | Not Quoted
3 | HIMALAYA GENERATORS | 22438478.00 | 21002414.00 | Two Crore Ten Lakh Two Thousand Four Hundred and Fourteen
4 | JCC ENGINEERS PRIVATE LIMITED | 22438478.00 | 21540938.00 | Two Crore Fifteen Lakh Fourty Thousand Nine Hundred and Thirty Eight
5 | Shiva Enterprises | 22438478.00 | 21047291.00 | Two Crore Ten Lakh Fourty Seven Thousand Two Hundred and Ninty One
Lowest Amount Quoted BY: HIMALAYA GENERATORS(21002414.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of Power Supply at Old Area Safdarjung Airport. Tender ID: 2024_AAI_201536_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises | 22438478.00 | L1
| 2 | Leo Air and Power Solution Pvt Ltd., | 23432668.00 | L2
| 3 | DOSHI ELECTRIC ENGG. CO. | 29999365.00 | L3
| 4 | HIMALAYA GENERATORS | 30821227.00 | L4
| 5 | JCC ENGINEERS PRIVATE LIMITED | 31809000.00 | L5