## BoQ1
Government eProcurement System Created By: SINDHU L S Created Date/Time: 13-Sep-2024 05:51 PM Tender Title: Electrical works at ASTI facilities and other Miscellaneous Works at Southern Region, Residential Colony, Chennai. Tender ID: 2024_AAI_201875_1
Tender Inviting Authority: Asst. General Manager (Engg-Electrical), AAI, RHQ SR, Chennai Airport, Chennai - 600027
Name of Work: Electrical works at ASTI facilities and other Miscellaneous Works at RHQ, SR, Residential Colony, Chennai.
Contract No: 2024_AAI_201875_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | POWER TECH ENTEPRISES (GSTN-33AASFP5921B1ZC) BID ID -736219 |  | vk sam engineering (GSTN-33AMZPS4037L1ZA) BID ID -737914 |  | CHENNAI ENGINEERING SERVICES (GSTN-33AADFC4373K1ZH) BID ID -739851 |  | GVD ENGINEERS & CONTRACTOR(GSTN-NA)--738929 |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)--738401
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | Supply of recess mounted Round spot light of wattage upto 5 Watts and having minimum 500 Lumens with opal diffuser, separate electronic driver, IP20, CCT 3000 to 4000 K, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 15.00 | Each | Item No.1 | 10500.00 | 12390.00 | 9105.00 | 10743.90 | 3435.00 | 4053.30 | 5250.00 | 6195.00 | 14985.00 | 17682.30 | 3435.00 | CHENNAI ENGINEERING SERVICES | 4053.30 | CHENNAI ENGINEERING SERVICES
2.00 | Supply of Recess mounted downlighter of wattage upto 9 Watts and having minimum 900 Lumens with pressure die-cast aluminium heat sink, Clear PC as a cover in white, powder coated finish with Independent electronic LED driver, IP20, CCT 3000 to 4000 K, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 123.00 | Each | Item No.2 | 110700.00 | 130626.00 | 86961.00 | 102613.98 | 125337.00 | 147897.66 | 67650.00 | 79827.00 | 91020.00 | 107403.60 | 67650.00 | GVD ENGINEERS & CONTRACTOR | 79827.00 | GVD ENGINEERS & CONTRACTOR
3.00 | Supply of aesthetic and compact, weather proof fitting of wattage upto 8 Watts and having minimum 880 Lumens, Polyester coated aluminium body or metal body, IP65 , CCT 3000 to 4000 K, CRI 80, wall/ground mounting and suitable for operation on 230V +/- 10% AC supply etc. complete as required. | 5.00 | Each | Item No.3 | 11000.00 | 12980.00 | 4140.00 | 4885.20 | 22995.00 | 27134.10 | 3250.00 | 3835.00 | 4995.00 | 5894.10 | 3250.00 | GVD ENGINEERS & CONTRACTOR | 3835.00 | GVD ENGINEERS & CONTRACTOR
4.00 | Supply of recess mounting type prewired white LED panel type luminare (cool day light) made of extruded or pressure die casted aluminium housing, opal diffuser/ reflector, separate Electronic driver, wattage not excceding 15W and having minimum 1500 Lumens, IP20, CCT 5700 to 6500 K, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., as required. | 60.00 | Each | Item No.4 | 54000.00 | 63720.00 | 46380.00 | 54728.40 | 47340.00 | 55861.20 | 39000.00 | 46020.00 | 53940.00 | 63649.20 | 39000.00 | GVD ENGINEERS & CONTRACTOR | 46020.00 | GVD ENGINEERS & CONTRACTOR
5.00 | Supply of wall washer fitting with Four-Directional Beam, aluminum Die Cast, IP65 with overall system wattage not excceding 7 W and having minimum 770 lumens, CCT 3000 to 4000 K, CRI 70 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 3.00 | Each | Item No.5 | 5400.00 | 6372.00 | 12420.00 | 14655.60 | 7557.00 | 8917.26 | 3900.00 | 4602.00 | 6000.00 | 7080.00 | 3900.00 | GVD ENGINEERS & CONTRACTOR | 4602.00 | GVD ENGINEERS & CONTRACTOR
6.00 | Supply of Bollard fitting, Pressure die cast & Powder coated body, PC opal diffuser. Efficient high output LED with IP65, system wattage not excceding 10 W, minimum 1100 lumens, CCT 3000 to 4000 K, CRI 70 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 45.00 | Each | Item No.6 | 162000.00 | 191160.00 | 149040.00 | 175867.20 | 200205.00 | 236241.90 | 202500.00 | 238950.00 | 148455.00 | 175176.90 | 148455.00 | DElite System Engineering (India) Pvt. Ltd. | 175176.90 | DElite System Engineering (India) Pvt. Ltd.
7.00 | Supply of LED strip, white/Blue Colour, 5 meter Flexible LED strips with uniform light distribution and long lasting adhesive for perfect cover with suitable driver, 24 W Efficient high output LED, IP 20 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 30.00 | Each | Item No.7 | 36000.00 | 42480.00 | 30870.00 | 36426.60 | 23670.00 | 27930.60 | 43500.00 | 51330.00 | 38970.00 | 45984.60 | 23670.00 | CHENNAI ENGINEERING SERVICES | 27930.60 | CHENNAI ENGINEERING SERVICES
8.00 | Supply of 2 feet x 2 feet (approx) size, recess mounting type, prewired white LED panel type luminare (cool day light) made of CRCA stainless steel with suitable diffuser/reflector to have uniform illumination with overall sytem wattage not excceding 36W and having minimum 3600 Lumens, IP20, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 65.00 | Each | Item No.8 | 143000.00 | 168740.00 | 142025.00 | 167589.50 | 277485.00 | 327432.30 | 110500.00 | 130390.00 | 129935.00 | 153323.30 | 110500.00 | GVD ENGINEERS & CONTRACTOR | 130390.00 | GVD ENGINEERS & CONTRACTOR
9.00 | Supply of 2 feet x 2 feet (approx) size, surface mounting type prewired white LED panel type luminare(cool day light) made of CRCA stainless steel with suitable diffuser/reflector to have uniform illumination with overall sytem wattage not excceding 36W and having minimum 3600 Lumens, IP20, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 14.00 | Each | Item No.09 | 44800.00 | 52864.00 | 20608.00 | 24317.44 | 69986.00 | 82583.48 | 30800.00 | 36344.00 | 32186.00 | 37979.48 | 20608.00 | vk sam engineering | 24317.44 | vk sam engineering
10.00 | Supply of 1 feet x 1 feet (approx) size, surface mounting type prewired white LED panel type luminare(cool day light) made of CRCA stainless steel with suitable diffuser/reflector to have uniform illumination with overall sytem wattage not excceding 18W and having minimum 1800 Lumens, IP20, CRI 80 and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 22.00 | Each | Item No.10 | 26400.00 | 31152.00 | 32384.00 | 38213.12 | 31878.00 | 37616.04 | 30800.00 | 36344.00 | 43978.00 | 51894.04 | 26400.00 | POWER TECH ENTEPRISES | 31152.00 | POWER TECH ENTEPRISES
11.00 | Supply of recess mounting type, LED Down light luminare with powder coated die-cast aluminium housing with overall sytem wattage not exceeding 18W & having minimum 1800 lumens, IP 20, CRI 80 and suitable for operation on 230V +/- 10% AC supply as required. | 47.00 | Each | Item No.11 | 51700.00 | 61006.00 | 102695.00 | 121180.10 | 67163.00 | 79252.34 | 39950.00 | 47141.00 | 117453.00 | 138594.54 | 39950.00 | GVD ENGINEERS & CONTRACTOR | 47141.00 | GVD ENGINEERS & CONTRACTOR
12.00 | Supply of Flood Light, LED luminare with powder coated, pressure die-cast, aluminium housing with overall sytem wattage not exceeding 100 W and having minimum 1100 lumens, IP 66, CCT 5700 to 6500 K, CRI 70 and suitable for operation on 230V +/- 10% AC supply as required. | 20.00 | Each | Item No.12 | 88000.00 | 103840.00 | 85100.00 | 100418.00 | 65180.00 | 76912.40 | 46000.00 | 54280.00 | 79980.00 | 94376.40 | 46000.00 | GVD ENGINEERS & CONTRACTOR | 54280.00 | GVD ENGINEERS & CONTRACTOR
13.00 | Supply of 45 W street Light, made with pressure die cast Aluminium housing with toughened glass and high power LED's with secondary optics, IP66 protection, 110 Lumens/watt and suitable for operation on 230V +/- 10% AC supply etc., complete as required. | 50.00 | Each | Item No.13 | 95000.00 | 112100.00 | 107650.00 | 127027.00 | 224450.00 | 264851.00 | 115000.00 | 135700.00 | 109950.00 | 129741.00 | 95000.00 | POWER TECH ENTEPRISES | 112100.00 | POWER TECH ENTEPRISES
14.00 | Supply of surface mounted bulk head fitting with 10W LED lamp & all accessories, IP 66, CRI 70, 110 Lumens/watt, CCT 6500K and suitable for operation on 230V +/- 10%, 50Hz, AC supply etc., complete as required. | 8.00 | Each | Item No.14 | 8800.00 | 10384.00 | 7120.00 | 8401.60 | 112072.00 | 132244.96 | 9600.00 | 11328.00 | 7992.00 | 9430.56 | 7120.00 | vk sam engineering | 8401.60 | vk sam engineering
15.00 | Supply of surface mounted 40W batten LED fitting, IP 66, 110 Lumens/watt, CRI 80, CCT 5700K to 6500 K and suitable for operation on 230V +/- 10%, 50Hz, AC supply etc., complete as required. | 75.00 | Each | Item No.15 | 180000.00 | 212400.00 | 178050.00 | 210099.00 | 40350.00 | 47613.00 | 41250.00 | 48675.00 | 74925.00 | 88411.50 | 40350.00 | CHENNAI ENGINEERING SERVICES | 47613.00 | CHENNAI ENGINEERING SERVICES
16.00 | Supply of following diameter, single phase, metal body, 900 RPM heavy duty Exhaust fan( ISI marked) with louver including all acccessories etc., as required.
16.01 | 300 mm dia | 10.00 | Each | Item No.16.A | 28000.00 | 33040.00 | 32570.00 | 38432.60 | 41590.00 | 49076.20 | 32000.00 | 37760.00 | 39990.00 | 47188.20 | 28000.00 | POWER TECH ENTEPRISES | 33040.00 | POWER TECH ENTEPRISES
16.02 | 150 mm dia | 8.00 | Each | Item No.16.B | 14400.00 | 16992.00 | 9456.00 | 11158.08 | 12712.00 | 15000.16 | 16000.00 | 18880.00 | 27992.00 | 33030.56 | 9456.00 | vk sam engineering | 11158.08 | vk sam engineering
17.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group B | 30.00 | Each | Item No.17 | 23700.00 | 27966.00 | 37530.00 | 44285.40 | 32970.00 | 38904.60 | 43500.00 | 51330.00 | 29970.00 | 35364.60 | 23700.00 | POWER TECH ENTEPRISES | 27966.00 | POWER TECH ENTEPRISES
18.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group B A. 2 x 2.5 sqmm + 1 x 2.5 sqmm earth wire | 195.00 | Meter | Item No.18 | 27300.00 | 32214.00 | 34905.00 | 41187.90 | 48555.00 | 57294.90 | 21450.00 | 25311.00 | 60255.00 | 71100.90 | 21450.00 | GVD ENGINEERS & CONTRACTOR | 25311.00 | GVD ENGINEERS & CONTRACTOR
19.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 175.00 | Meter | Item No.19 | 33250.00 | 39235.00 | 44450.00 | 52451.00 | 52325.00 | 61743.50 | 26250.00 | 30975.00 | 104825.00 | 123693.50 | 26250.00 | GVD ENGINEERS & CONTRACTOR | 30975.00 | GVD ENGINEERS & CONTRACTOR
20.00 | Supplying and fixing following Modular base & cover plate suitable for existing modular metal boxes etc. as required.
20.01 | 1 or 2 Module | 35.00 | Each | Item No.20.A | 14000.00 | 16520.00 | 6755.00 | 7970.90 | 5215.00 | 6153.70 | 7700.00 | 9086.00 | 13965.00 | 16478.70 | 5215.00 | CHENNAI ENGINEERING SERVICES | 6153.70 | CHENNAI ENGINEERING SERVICES
20.02 | 3 Module | 15.00 | Each | Item No.20.B | 6750.00 | 7965.00 | 4830.00 | 5699.40 | 2535.00 | 2991.30 | 4500.00 | 5310.00 | 7485.00 | 8832.30 | 2535.00 | CHENNAI ENGINEERING SERVICES | 2991.30 | CHENNAI ENGINEERING SERVICES
20.03 | 4 Module | 32.00 | Each | Item No.20.C | 16000.00 | 18880.00 | 11328.00 | 13367.04 | 6368.00 | 7514.24 | 13760.00 | 16236.80 | 15968.00 | 18842.24 | 6368.00 | CHENNAI ENGINEERING SERVICES | 7514.24 | CHENNAI ENGINEERING SERVICES
20.04 | 6 Module | 15.00 | Each | Item No.20.D | 8250.00 | 9735.00 | 7110.00 | 8389.80 | 3585.00 | 4230.30 | 7800.00 | 9204.00 | 11985.00 | 14142.30 | 3585.00 | CHENNAI ENGINEERING SERVICES | 4230.30 | CHENNAI ENGINEERING SERVICES
20.05 | 8 Module | 15.00 | Each | Item No.20.E | 9000.00 | 10620.00 | 8760.00 | 10336.80 | 4335.00 | 5115.30 | 10200.00 | 12036.00 | 11985.00 | 14142.30 | 4335.00 | CHENNAI ENGINEERING SERVICES | 5115.30 | CHENNAI ENGINEERING SERVICES
20.06 | 12 Module | 15.00 | Each | Item No.20.F | 9750.00 | 11505.00 | 11385.00 | 13434.30 | 5085.00 | 6000.30 | 14100.00 | 16638.00 | 14985.00 | 17682.30 | 5085.00 | CHENNAI ENGINEERING SERVICES | 6000.30 | CHENNAI ENGINEERING SERVICES
21.00 | Supplying and fixing following way,vertical type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 4 way (4 + 12), Double door | 1.00 | Each | Item No.21 | 5500.00 | 6490.00 | 25701.00 | 30327.18 | 3999.00 | 4718.82 | 5000.00 | 5900.00 | 9000.00 | 10620.00 | 3999.00 | CHENNAI ENGINEERING SERVICES | 4718.82 | CHENNAI ENGINEERING SERVICES
22.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’s and incomer ) as required .(Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) 4 way (4 + 12), Double door | 1.00 | Each | Item No.22 | 9500.00 | 11210.00 | 25701.00 | 30327.18 | 4699.00 | 5544.82 | 12000.00 | 14160.00 | 15000.00 | 17700.00 | 4699.00 | CHENNAI ENGINEERING SERVICES | 5544.82 | CHENNAI ENGINEERING SERVICES
23.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 20.00 | Each | Item No.23 | 4000.00 | 4720.00 | 2760.00 | 3256.80 | 3980.00 | 4696.40 | 4800.00 | 5664.00 | 9980.00 | 11776.40 | 2760.00 | vk sam engineering | 3256.80 | vk sam engineering
24.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple pole 32 A | 2.00 | Each | Item No.24 | 3600.00 | 4248.00 | 2392.00 | 2822.56 | 1798.00 | 2121.64 | 1000.00 | 1180.00 | 1798.00 | 2121.64 | 1000.00 | GVD ENGINEERS & CONTRACTOR | 1180.00 | GVD ENGINEERS & CONTRACTOR
25.00 | Supplying and fixing following rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Four pole 40 A | 2.00 | Each | Item No.25 | 4800.00 | 5664.00 | 2778.00 | 3278.04 | 3198.00 | 3773.64 | 1460.00 | 1722.80 | 5998.00 | 7077.64 | 1460.00 | GVD ENGINEERS & CONTRACTOR | 1722.80 | GVD ENGINEERS & CONTRACTOR
26.00 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 1 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 6.00 | Each | Item No.26 | 12600.00 | 14868.00 | 7728.00 | 9119.04 | 11994.00 | 14152.92 | 6600.00 | 7788.00 | 9000.00 | 10620.00 | 6600.00 | GVD ENGINEERS & CONTRACTOR | 7788.00 | GVD ENGINEERS & CONTRACTOR
27.00 | Supplying and fixing modular switch/socket on the existing modular plate & switch box, including connectiopn but excluding modular plate etc., as required.
27.01 | 5/6 amps switch | 175.00 | Each | Item No.27.A | 14000.00 | 16520.00 | 5600.00 | 6608.00 | 19075.00 | 22508.50 | 23625.00 | 27877.50 | 17325.00 | 20443.50 | 5600.00 | vk sam engineering | 6608.00 | vk sam engineering
27.02 | 15/16 amp switch | 45.00 | Each | Item No.27.B | 8100.00 | 9558.00 | 2700.00 | 3186.00 | 8055.00 | 9504.90 | 9900.00 | 11682.00 | 8955.00 | 10566.90 | 2700.00 | vk sam engineering | 3186.00 | vk sam engineering
27.03 | 5 pin 5/6 amp socket outlet | 40.00 | Each | Item No.27.C | 5600.00 | 6608.00 | 5520.00 | 6513.60 | 6760.00 | 7976.80 | 7200.00 | 8496.00 | 15960.00 | 18832.80 | 5520.00 | vk sam engineering | 6513.60 | vk sam engineering
27.04 | 6 pin 15/16 amp socket outlet | 40.00 | Each | Item No.27.D | 8000.00 | 9440.00 | 4960.00 | 5852.80 | 11160.00 | 13168.80 | 11200.00 | 13216.00 | 19960.00 | 23552.80 | 4960.00 | vk sam engineering | 5852.80 | vk sam engineering
28.00 | Supplying and replacing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc.as required. | 35.00 | Each | Item No.28 | 16800.00 | 19824.00 | 10465.00 | 12348.70 | 16415.00 | 19369.70 | 38500.00 | 45430.00 | 14315.00 | 16891.70 | 10465.00 | vk sam engineering | 12348.70 | vk sam engineering
29.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 20.00 | Each | Item No.29 | 500.00 | 590.00 | 360.00 | 424.80 | 180.00 | 212.40 | 500.00 | 590.00 | 800.00 | 944.00 | 180.00 | CHENNAI ENGINEERING SERVICES | 212.40 | CHENNAI ENGINEERING SERVICES
30.00 | Providing and fixing extra conduit down rod of 20 mm dia, 1 meter length, wiring with 3 X 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable including removing existing down rod etc. complete as required. | 16.00 | Each | Item No.30 | 4800.00 | 5664.00 | 3904.00 | 4606.72 | 6384.00 | 7533.12 | 1440.00 | 1699.20 | 6384.00 | 7533.12 | 1440.00 | GVD ENGINEERS & CONTRACTOR | 1699.20 | GVD ENGINEERS & CONTRACTOR
31.00 | Installation, testing and commissioning of LED Pre-wired, box type /down lighter / spot light fitting of all types, complete with all accessories and tube etc in recess/on surface directly on ceiling /wall, connection with 1.5 sq.mm FRLS PVC insulated, copper conductor, single core cable and earthing at existing fitting location including dismantling the existing fitting etc., complete as required. | 524.00 | Each | Item No.31 | 78600.00 | 92748.00 | 72312.00 | 85328.16 | 104276.00 | 123045.68 | 146720.00 | 173129.60 | 156676.00 | 184877.68 | 72312.00 | vk sam engineering | 85328.16 | vk sam engineering
32.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. up to 450 mm sweep | 8.00 | Each | Item No.32 | 2400.00 | 2832.00 | 5152.00 | 6079.36 | 3992.00 | 4710.56 | 4400.00 | 5192.00 | 4792.00 | 5654.56 | 2400.00 | POWER TECH ENTEPRISES | 2832.00 | POWER TECH ENTEPRISES
33.00 | Supply of following size XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (PART-I) with upto date amendments as required. 4 x 16 Sq.mm | 300.00 | Meter | Item No.33 | 54000.00 | 63720.00 | 49800.00 | 58764.00 | 50700.00 | 59826.00 | 72000.00 | 84960.00 | 119700.00 | 141246.00 | 49800.00 | vk sam engineering | 58764.00 | vk sam engineering
34.00 | Supply of following size XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (PART-I) with upto date amendments as required. 3.5 x 240 Sq.mm | 450.00 | Meter | Item No.34 | 540000.00 | 637200.00 | 520200.00 | 613836.00 | 584550.00 | 689769.00 | 697500.00 | 823050.00 | 449550.00 | 530469.00 | 449550.00 | DElite System Engineering (India) Pvt. Ltd. | 530469.00 | DElite System Engineering (India) Pvt. Ltd.
35.00 | Supplying and laying of 50 mm OD HDPE Pipe of PE 80 PN 6 ISI Marked along with all accessories like socket, bend etc., confirming to IS 4984 complete with fitting and cutting, jointing etc., direct in ground (.75 mtr below the ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., as required. 1 X Run of 50 MM HDPE Pipe | 300.00 | Meter | Item No.35 | 45000.00 | 53100.00 | 89700.00 | 105846.00 | 47700.00 | 56286.00 | 105000.00 | 123900.00 | 149700.00 | 176646.00 | 45000.00 | POWER TECH ENTEPRISES | 53100.00 | POWER TECH ENTEPRISES
36.00 | Laying of following size HDPE pipe with all accessories complete with fitting, cutting, jointing etc., direct in ground at a depth of 0.75m and width of 0.35m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc., as required. 1 X Run of 125 MM HDPE Pipe | 100.00 | Meter | Item No.36 | 20000.00 | 23600.00 | 21600.00 | 25488.00 | 24900.00 | 29382.00 | 22000.00 | 25960.00 | 29900.00 | 35282.00 | 20000.00 | POWER TECH ENTEPRISES | 23600.00 | POWER TECH ENTEPRISES
37.00 | Laying of one number PVC/XLPE insulated and PVC sheathed power cable of 1.1KV grade Upto 35 sq.mm in the existing RCC/Hume/STONEWARE/METAL/HDPE Pipe as required. | 300.00 | Meter | Item No.37 | 22500.00 | 26550.00 | 13800.00 | 16284.00 | 11700.00 | 13806.00 | 15000.00 | 17700.00 | 14700.00 | 17346.00 | 11700.00 | CHENNAI ENGINEERING SERVICES | 13806.00 | CHENNAI ENGINEERING SERVICES
38.00 | Laying of one number PVC/XLPE insulated and PVC sheathed power cable of 1.1KV grade Above 185 sq. mm and upto 400 sq. mm in the existing RCC/Hume/STONEWARE/METAL/HDPE Pipe as required. | 300.00 | Meter | Item No.38 | 30000.00 | 35400.00 | 24900.00 | 29382.00 | 47700.00 | 56286.00 | 45000.00 | 53100.00 | 14700.00 | 17346.00 | 14700.00 | DElite System Engineering (India) Pvt. Ltd. | 17346.00 | DElite System Engineering (India) Pvt. Ltd.
39.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 100.00 | Meter | Item No.39 | 15000.00 | 17700.00 | 7400.00 | 8732.00 | 14900.00 | 17582.00 | 16000.00 | 18880.00 | 4900.00 | 5782.00 | 4900.00 | DElite System Engineering (India) Pvt. Ltd. | 5782.00 | DElite System Engineering (India) Pvt. Ltd.
40.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 50.00 | Meter | Item No.40 | 10000.00 | 11800.00 | 5500.00 | 6490.00 | 9950.00 | 11741.00 | 9000.00 | 10620.00 | 2450.00 | 2891.00 | 2450.00 | DElite System Engineering (India) Pvt. Ltd. | 2891.00 | DElite System Engineering (India) Pvt. Ltd.
41.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 10.00 | Each | Item No.41 | 6000.00 | 7080.00 | 1610.00 | 1899.80 | 4490.00 | 5298.20 | 6500.00 | 7670.00 | 9990.00 | 11788.20 | 1610.00 | vk sam engineering | 1899.80 | vk sam engineering
42.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 240 sq. mm (62 mm) | 4.00 | Each | Item No.42 | 8400.00 | 9912.00 | 4784.00 | 5645.12 | 7996.00 | 9435.28 | 12000.00 | 14160.00 | 4800.00 | 5664.00 | 4784.00 | vk sam engineering | 5645.12 | vk sam engineering
43.00 | Supply, Installation, Testing and Commissioning of 2 TR capacity wall mounted type Split AC unit, 5 star rated, invertor type, fitted with hermetically sealed compressor operating on 220 V +10% 50 Hz Single phase AC supply with evaporator and condensing unit made of copper tubes with aluminium fins i/c cordless remote control, copper piping for both suction and discharge of 3 metres length alongwith power control cables and thermal insulation, metal frame for mounting condensing unit, etc complete as per specifications complete as required | 6.00 | Each | Item No.43 | 390000.00 | 460200.00 | 376050.00 | 443739.00 | 272994.00 | 322132.92 | 312000.00 | 368160.00 | 414000.00 | 488520.00 | 272994.00 | CHENNAI ENGINEERING SERVICES | 322132.92 | CHENNAI ENGINEERING SERVICES
44.00 | Supply, Installation, Testing and Commissioning of 1.5 TR capacity wall mounted type Split AC unit (5 star rating invertor type) fitted with hermetically sealed compressor operating on 220 V +10% 50 Hz Single phase AC supply with evaporator and condensing unit made of copper tubes with aluminium fins i/c cordless remote control, copper piping for both suction and discharge of 3 metres length alongwith power control cables and thermal insulation, metal frame for mounting condensing unit, etc complete as per specifications complete as required | 15.00 | Each | Item No.44 | 675000.00 | 796500.00 | 690000.00 | 814200.00 | 614985.00 | 725682.30 | 630000.00 | 743400.00 | 899985.00 | 1061982.30 | 614985.00 | CHENNAI ENGINEERING SERVICES | 725682.30 | CHENNAI ENGINEERING SERVICES
45.00 | Supply and Installation of Copper pipe for the following capacity Air conditioners including suction and delivery copper pipes with all accessories such as insulation, power & control cabling, etc. as per specifications complete as required
45.01 | For 2 TR Split Air conditioner (beyond 3 meters per Split AC unit) | 50.00 | Meter | Item No.45.A | 60000.00 | 70800.00 | 138000.00 | 162840.00 | 69950.00 | 82541.00 | 72500.00 | 85550.00 | 49950.00 | 58941.00 | 49950.00 | DElite System Engineering (India) Pvt. Ltd. | 58941.00 | DElite System Engineering (India) Pvt. Ltd.
45.02 | For 1.5 TR Split Air conditioner (beyond 3 meters per Split AC unit) | 50.00 | Meter | Item No.45.B | 60000.00 | 70800.00 | 115000.00 | 135700.00 | 64950.00 | 76641.00 | 65000.00 | 76700.00 | 49950.00 | 58941.00 | 49950.00 | DElite System Engineering (India) Pvt. Ltd. | 58941.00 | DElite System Engineering (India) Pvt. Ltd.
46.00 | SITC of following capacity voltage stabilisers with copper wound coil having range of 170 to 270 voltage single phase, 50 Hz AC supply i/c necessary fixing arrangements, clamps, screws, metal clad top, connecting 3 core cable of 1 metre length, complete, etc as per specifications complete as required. A. 4/5 KVA stabilizer for Spilt AC | 21.00 | Each | Item No.46 | 100800.00 | 118944.00 | 115920.00 | 136785.60 | 62979.00 | 74315.22 | 109200.00 | 128856.00 | 146979.00 | 173435.22 | 62979.00 | CHENNAI ENGINEERING SERVICES | 74315.22 | CHENNAI ENGINEERING SERVICES
47.00 | Supplying & laying of condensate water drain pipe made of PVC having size of 40mm dia, 6kg/cm capacity, for additional requirement for AC units i/c necessary clamps, screws, supports, etc as per specifications complete as required | 150.00 | Meter | Item No.47 | 22500.00 | 26550.00 | 9000.00 | 10620.00 | 22350.00 | 26373.00 | 31500.00 | 37170.00 | 14850.00 | 17523.00 | 9000.00 | vk sam engineering | 10620.00 | vk sam engineering
48.00 | Dismantling and shifting of following capacity Indoor and outdoor units to AAI store /any location specified by AAI, including gas pumping down, pipes, cables, etc.,complete as required. A. 1.5 TR capacity split AC | 10.00 | Each | Item No.48 | 25000.00 | 29500.00 | 13800.00 | 16284.00 | 9990.00 | 11788.20 | 20000.00 | 23600.00 | 7000.00 | 8260.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd. | 8260.00 | DElite System Engineering (India) Pvt. Ltd.
49.00 | Supply, Installation, Testing and Commissioning of indoor LT panel made of 2mm thick CRCA Sheet for inner doors & partitions, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing panel with IP 54 protection, suitable for operation at 415 V, 3 Phase, 4 Wire, 50 Hz AC System, complete with all accessories, interconnection, connection, earthing, painting and comprising of the following: a) Incomer: Two Nos. of 400 A, 36 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps, Phase Indication Lamps with Auto transfer switch facility and bypass arrangement as required. b) Outgoing: 2 Nos. of 315 A, 36 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoings, with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. c) Outgoing : 2 Nos. of 250 A, 36 KA, 4P MCCB with Microprocessor Based Releases (L&T MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as Outgoings, with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. d) One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required. e) All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required. | 1.00 | Each | Item No.49 | 275000.00 | 324500.00 | 731400.00 | 863052.00 | 639999.00 | 755198.82 | 310000.00 | 365800.00 | 300000.00 | 354000.00 | 275000.00 | POWER TECH ENTEPRISES | 324500.00 | POWER TECH ENTEPRISES
50.00 | Supply, Installation, Testing and Commissioning of indoor Type metering box made out of 2mm thick CRCA Sheet Steel, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing panel with IP 54 protection, suitable for operation at 415 V, 3 Phase, 4 Wire, 50 Hz AC System, complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel suitable for bottom entry and locking arrangements including fixing of panel etc. complete as required and comprising of the following 2 cubicles: a) Cubicle 1 : Provision on for One No. 200 KVA, 3Ph, Energy meter along with C.T. etc., complete as required (Energy meter and CT not in scope) with see through Glass in door. b) Cubicle 2 : Provision of two Sets of 400 Amps Al. Bus Bars with at Par Neutral Bus Bars as required. | 1.00 | Each | Item No.50 | 125000.00 | 147500.00 | 32200.00 | 37996.00 | 14999.00 | 17698.82 | 120000.00 | 141600.00 | 175000.00 | 206500.00 | 14999.00 | CHENNAI ENGINEERING SERVICES | 17698.82 | CHENNAI ENGINEERING SERVICES
51.00 | Supply and fixing of double door Outdoor Panel with 2 cubicles each having providing 2 Nos. DOL starter suitable for 5 HP motor, digital volt & ammeter, contactor, push button, selector switch, Overload, High-Low voltage & Dry run protection etc., earth terminals, making connections, Suitable foundation etc complete as required. | 2.00 | Each | Item No.51 | 65000.00 | 76700.00 | 113160.00 | 133528.80 | 29998.00 | 35397.64 | 84000.00 | 99120.00 | 30000.00 | 35400.00 | 29998.00 | CHENNAI ENGINEERING SERVICES | 35397.64 | CHENNAI ENGINEERING SERVICES
52.00 | Supply, Installation, Testing and Commissioning of Outdoor Type (Double door) junction box/ adaptor box made out of 3mm thick CRCA Sheet Steel for outer Shell dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing panel with IP 54 protection, suitable for operation at 415 V, 3 Phase, 4 Wire, 50 Hz AC System, complete with all accessories, earthing, painting, provided with bottom base channel suitable for bottom entry and locking arrangements including excavation for foundation, providing foundation, suitable RCC pedestal of minimum 700 mm height,100mm PCC, erection of panel etc. complete as required and comprising of One Set of 400 Amps Al. Bus Bars (RYBN) with at Par Neutral Bus Bars as required. | 2.00 | Each | Item No.52 | 250000.00 | 295000.00 | 20240.00 | 23883.20 | 29998.00 | 35397.64 | 160000.00 | 188800.00 | 150000.00 | 177000.00 | 20240.00 | vk sam engineering | 23883.20 | vk sam engineering
53.00 | Supplying, fixing, testing and commissioning of 5 HP Vertical borewell submersible pumpset , 26 stage, 2.50 LPS discharge (minimum) , head range 66 to 96 Mtr , C.I impeller,SS shaft etc suitable for 50 mm dia delivery line for operation on 415 V, 3 phase power supply etc., complete as required. (Make : Kiloskar KU4 1526 T ) | 2.00 | Each | Item No.53 | 77000.00 | 90860.00 | 85560.00 | 100960.80 | 107998.00 | 127437.64 | 220000.00 | 259600.00 | 80000.00 | 94400.00 | 77000.00 | POWER TECH ENTEPRISES | 90860.00 | POWER TECH ENTEPRISES
54.00 | Supplying, fixing, testing and commissioning of 10 HP Vertical borewll submersible pumpset 5.5 LPS discharge (minimum), head range 40 to 64 Mtr, C.I impeller,SS shaft etc., for operation on 415 V,3 phase power supply etc, complete as required. (Model :KS6B 1020 ) | 2.00 | Each | Item No.54 | 97000.00 | 114460.00 | 128800.00 | 151984.00 | 147998.00 | 174637.64 | 310000.00 | 365800.00 | 100000.00 | 118000.00 | 97000.00 | POWER TECH ENTEPRISES | 114460.00 | POWER TECH ENTEPRISES
55.00 | Earthing with G.I earth pipe 4.5 meter long, 40 mm dia. including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt complete as required. | 2.00 | Each | Item No.55 | 18000.00 | 21240.00 | 8280.00 | 9770.40 | 9998.00 | 11797.64 | 22000.00 | 25960.00 | 18000.00 | 21240.00 | 8280.00 | vk sam engineering | 9770.40 | vk sam engineering
56.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 150.00 | Meter | Item No.56 | 5250.00 | 6195.00 | 8250.00 | 9735.00 | 5850.00 | 6903.00 | 9000.00 | 10620.00 | 8850.00 | 10443.00 | 5250.00 | POWER TECH ENTEPRISES | 6195.00 | POWER TECH ENTEPRISES
57.00 | Providing and fixing 25 mm x 5 mm G.I strip on surface or in recess for connections etc. as required | 10.00 | Meter | Item No.57 | 2500.00 | 2950.00 | 2240.00 | 2643.20 | 2290.00 | 2702.20 | 2100.00 | 2478.00 | 7990.00 | 9428.20 | 2100.00 | GVD ENGINEERS & CONTRACTOR | 2478.00 | GVD ENGINEERS & CONTRACTOR
58.00 | Supply and replacement of 400 A, 50 KA, 4P MCCBs in the existing panel and providing 50 x 10 MM Buslinks and 3 Nos. 400/5 A resin cast CTs including testing and commissioning etc., complete as required. | 1.00 | Each | Item No.58 | 32000.00 | 37760.00 | 42596.00 | 50263.28 | 42999.00 | 50738.82 | 50000.00 | 59000.00 | 99000.00 | 116820.00 | 32000.00 | POWER TECH ENTEPRISES | 37760.00 | POWER TECH ENTEPRISES
| Total in Figures |  |  |  | 4427450.00 | 5224391.00 | 4771450.00 | 5630311.00 | 4695254.00 | 5540399.72 | 4787855.00 | 5649668.90 | 4942056.00 | 5831626.08

## BOQ Summary
BOQ Summary Details Tender Title: Electrical works at ASTI facilities and other Miscellaneous Works at Southern Region, Residential Colony, Chennai. Tender ID: 2024_AAI_201875_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | POWER TECH ENTEPRISES | 5224391.00 | L1
| 2 | CHENNAI ENGINEERING SERVICES | 5540399.72 | L2
| 3 | vk sam engineering | 5630311.00 | L3
| 4 | GVD ENGINEERS & CONTRACTOR | 5649668.90 | L4
| 5 | DElite System Engineering (India) Pvt. Ltd. | 5831626.08 | L5