## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 18-Sep-2024 05:44 PM Tender Title: Misc. Electrical work related to NITB at R. B. Airport, Bhopal. SH Provision of High Mast at Apron Area. Tender ID: 2024_AAI_202036_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Misc. Electrical work related to NITB at R. B. Airport, Bhopal. SH: Provision of High Mast at Apron Area.
Contract No: AAI/BPL/ENGG(E)/NIT-04/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation (GSTN-24ACIPP6157B1ZQ) BID ID -734485 |  | elektron (GSTN-09AAFFE6230P1Z2) BID ID -734525 |  | ENERGYGREEN TECHNOPOWER PVT LTD (GSTN-23AAECE7344J1ZM) BID ID -734619 |  | Kripa Electronics india pvt ltd (GSTN-27AACCK9472B1ZI) BID ID -734715 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -734799 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -734994 |  | MANNA ELECTRONICS AND ELECTRICAL WORKS (GSTN-19AALFM9363P2Z6) BID ID -735084 |  | srinivasa power solution(GSTN-NA)--734676 |  | Avinash Chopra(GSTN-NA)--733430 |  | BATRA ENGINEERS(GSTN-NA)--734163 |  | METRO ENGINEERS SERVICES(GSTN-NA)--734730
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 20 Mtr High mast systems in two sections suitable for IS 875 part 3 complete with all accessories as per specifications. Mast shaft shall be in two sections, hot dip galvanized and suitable for IS 875 part 3 wind speed criteria. It shall also include accessories comprising latching type head frame, galvanized luminaries carriage suitable to install minimum 15 nos. of LED luminaries (500 Watt) asymmetrically with suitable counter weights, double drum winch, 8mm dia stainless steel wire rope, 6C X 2.5 sq.mm. ERP trailing copper cable with connectors, integral electrically operated power tool install inside the base compartment with raising with suitable capacity TPN MCB etc. providing M 20 grade RCC foundation with suitable design as per site conditions, foundation bolts of suitable size as per approved design and manufactured from special steel along with nuts, washers, suitable size anchor plates etc. complete as required. | 4.00 | Each |  | 650000.00 | 2600000.00 | 582944.00 | 2331776.00 | 309120.00 | 1236480.00 | 552561.33 | 2210245.32 | 501496.00 | 2005984.00 | 460000.00 | 1840000.00 | 321701.00 | 1286804.00 | 350000.00 | 1400000.00 | 529200.00 | 2116800.00 | 450000.00 | 1800000.00 | 415000.00 | 1660000.00 | 1236480.00 | ENERGYGREEN TECHNOPOWER PVT LTD
2.00 | Supply, Installation, testing and Commissioning of high-quality integrated LED Flood Light with a minimum system lumen of 63700 Lm and system efficacy of minimum 135 lumen/watt. CCT of 5700K with SDCM < 5 and CRI ≥ 70. The housing should be of non-corrosive single pice high-pressure die-cast aluminum to with stand extreme environments. with PF > 0.95. Lifetime of 50K hours @L70. Product should be suitable for continuous operation (10-12 Hrs. per day). The Ingress protection should be minimum IP 66 with an IK rating of 08. Optical and control gear compartments shall be maintainable/ replaceable without impacting the LED units. The access to the optical and the gear compartment should be separate. While accessing the gear compartment, the optical compartment should not be accessible. The Luminaire should have a 20 KV /10 KA SPD duly bolted in the Luminaire. LM79 and LM80 reports must be submitted from a NABL accredited laboratory. Luminaire and driver must be BIS Certified and the certificates must be submitted for records. Luminaire and driver should be of same make. Similar to Philips BVP485 LED637 CW NB A1 PSU GR SPD suitable to operate on 240 V, 50 Hz AC complete as required suitable for Apron High Mast. | 48.00 | Each |  | 20000.00 | 960000.00 | 22803.00 | 1094544.00 | 21528.00 | 1033344.00 | 20890.83 | 1002759.84 | 17233.00 | 827184.00 | 18500.00 | 888000.00 | 18500.00 | 888000.00 | 19500.00 | 936000.00 | 21630.00 | 1038240.00 | 32000.00 | 1536000.00 | 23500.00 | 1128000.00 | 827184.00 | SARASWAT ENGINEERING SERVICES
3.00 | Design, Manufacture, Supplying, Indoor type LT Panel & Transport to the site, Receiving, Unloading, Shifting to various locations, handling, assembling, installation in correct aligned position, grouting with dash fasteners, GI nuts-bolts, testing and commissioning of the following bolted fabricated in compartmentalized conform to IEC61439, IS: 8623/1993 suitable for 415V, 3Phase, 4 Wire 50 Hz Ac supply, are housed in design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick for gland plate, bottom base channel of MS section not less than 100mmx 50mmx50mmx 5mm thick for Main L.T. Panel and 40mm x 25mm x 25mm x 5mm thick plates for MDB/MCC and SDBs etc., incl. cleaning & finishing complete, SMC bus bar supports, fabrication shall be done in transportable sections and all front and back doors shall be hinged type and earth with frame. Entire panel shall have a common copper continuous earth bar of size 50mm x 6mm or as specified below, including all features of electrical & mechanical interlocking with incomers. a) 2 No. 250A FP 36KA MCCB having thermal magnetic release with rotary handle as incoming with metering, CTs & R, Y & B indication lamps along with mechanical interlock in between incommers. b) 6 Nos. 63 A FP MCCB, 16KA having thermal magnetic release with rotary handle as outgoing with On/Off indication using LED lamps etc. as required. | 2.00 | Each |  | 300000.00 | 600000.00 | 204800.00 | 409600.00 | 135654.00 | 271308.00 | 379833.33 | 759666.66 | 349984.00 | 699968.00 | 348000.00 | 696000.00 | 225000.00 | 450000.00 | 273320.00 | 546640.00 | 148000.00 | 296000.00 | 380000.00 | 760000.00 | 350000.00 | 700000.00 | 271308.00 | ENERGYGREEN TECHNOPOWER PVT LTD
4.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of double door floor mounted LT power supply top sloped outdoor panel of size (1200mm x 1000mm x 200mm(deep)) made out of 14 SWG CRCA sheet steel totally enclosed, weather, dust, vermin proof, complete with accessories, Selector switch for Auto/Manual Operations, Push Button for Raising & Lowering and necessary arrangement for remote raise & lower operation, terminal blocks for termination of cables with top/bottom entry as per site conditions, locking arrangement, painting. etc. including the following minimum accessories as per technical specifications and drawing as approved by engineer-in- charge. Incomer: 63 Amps, 4 Pole MCCB, 35 kA breaking capacity, Thermal Magnetic Release Type, Ics = 100%Icu with LED indication for each phase - 1 No(RED, YELLOW, BLUE) - 1 Nos Outgoing: 20 Amps, 2 Pole MCB with 10 kA breaking capacity (C-Curve) 2 Nos 25 Amps 3 Pole power Contactor - 1 No 24 HR Seting Timer to operate above contactor on Auto mode. Illuminated Push Button (Raise & Lower)- 2 Nos 6 Amps, single Pole MCB with 10 kA breaking capacity (C-Curve)- 1 No 10 Amps 3 Pole power Contactor - 2 Nos 10 Amps 3 Pole Motor protection Circuit breaker - 1 No | 4.00 | Each |  | 24000.00 | 96000.00 | 44800.00 | 179200.00 | 53544.00 | 214176.00 | 100440.00 | 401760.00 | 99287.00 | 397148.00 | 48000.00 | 192000.00 | 72000.00 | 288000.00 | 32000.00 | 128000.00 | 52750.00 | 211000.00 | 98000.00 | 392000.00 | 55000.00 | 220000.00 | 96000.00 | jaydeep agency corporation
5.00 | Supply of 4 X 16 sq.mm PVC insulated and XLPE Sheathed armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required. | 1550.00 | Meter |  | 215.00 | 333250.00 | 149.00 | 230950.00 | 145.00 | 224750.00 | 132.50 | 205375.00 | 139.00 | 215450.00 | 138.00 | 213900.00 | 200.00 | 310000.00 | 160.00 | 248000.00 | 143.00 | 221650.00 | 220.00 | 341000.00 | 177.00 | 274350.00 | 205375.00 | Kripa Electronics india pvt ltd
6.00 | Supply of 3.5 X 50 sq.mm PVC insulated and XLPE Sheathed armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required. | 2000.00 | Meter |  | 433.00 | 866000.00 | 307.00 | 614000.00 | 286.00 | 572000.00 | 260.00 | 520000.00 | 280.00 | 560000.00 | 270.00 | 540000.00 | 395.00 | 790000.00 | 407.00 | 814000.00 | 299.00 | 598000.00 | 450.00 | 900000.00 | 302.00 | 604000.00 | 520000.00 | Kripa Electronics india pvt ltd
7.00 | Supply of 3.5 X 240 sq.mm PVC insulated and XLPE Sheathed armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required. | 700.00 | Meter |  | 1718.00 | 1202600.00 | 1207.00 | 844900.00 | 1152.00 | 806400.00 | 1038.75 | 727125.00 | 1111.00 | 777700.00 | 1090.00 | 763000.00 | 1580.50 | 1106350.00 | 1655.00 | 1158500.00 | 1339.65 | 937755.00 | 1500.00 | 1050000.00 | 1203.00 | 842100.00 | 727125.00 | Kripa Electronics india pvt ltd
8.00 | Supply of integral LED Aviation (Obstruction) light comprising of aluminium housing with polycarbonate enclosure with suitable size G.I. Pipe complete etc as required. | 4.00 | Each |  | 3000.00 | 12000.00 | 2176.00 | 8704.00 | 6900.00 | 27600.00 | 4212.11 | 16848.44 | 5345.00 | 21380.00 | 6500.00 | 26000.00 | 3900.00 | 15600.00 | 4705.00 | 18820.00 | 3900.00 | 15600.00 | 4500.00 | 18000.00 | 5500.00 | 22000.00 | 8704.00 | elektron
9.00 | Earthing with G.I. earth plate 600 mm x600 mm x 6mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7metre long with charcoal or coke and salt as required. | 8.00 | SET |  | 7890.00 | 63120.00 | 7150.00 | 57200.00 | 16560.00 | 132480.00 | 12500.00 | 100000.00 | 10674.00 | 85392.00 | 7500.00 | 60000.00 | 6500.00 | 52000.00 | 11587.00 | 92696.00 | 12500.00 | 100000.00 | 8900.00 | 71200.00 | 15500.00 | 124000.00 | 52000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
10.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 100.00 | Meter |  | 125.00 | 12500.00 | 133.00 | 13300.00 | 690.00 | 69000.00 | 1254.00 | 125400.00 | 178.00 | 17800.00 | 540.00 | 54000.00 | 124.00 | 12400.00 | 130.00 | 13000.00 | 250.00 | 25000.00 | 150.00 | 15000.00 | 205.00 | 20500.00 | 12400.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
11.00 | Supplying and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 40.00 | Meter |  | 165.00 | 6600.00 | 126.00 | 5040.00 | 262.00 | 10480.00 | 142.56 | 5702.40 | 322.00 | 12880.00 | 185.00 | 7400.00 | 200.00 | 8000.00 | 175.00 | 7000.00 | 94.00 | 3760.00 | 220.00 | 8800.00 | 135.00 | 5400.00 | 3760.00 | Avinash Chopra
12.00 | Supplying and laying of 120 mm dia (OD-120 mm & ID-103 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 200.00 | Meter |  | 185.00 | 37000.00 | 209.00 | 41800.00 | 359.00 | 71800.00 | 246.05 | 49210.00 | 387.00 | 77400.00 | 240.00 | 48000.00 | 220.00 | 44000.00 | 279.00 | 55800.00 | 165.00 | 33000.00 | 340.00 | 68000.00 | 210.00 | 42000.00 | 33000.00 | Avinash Chopra
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sq. mm | 50.00 | Meter |  | 20.00 | 1000.00 | 27.50 | 1375.00 | 69.00 | 3450.00 | 104.00 | 5200.00 | 42.00 | 2100.00 | 35.00 | 1750.00 | 34.00 | 1700.00 | 246.00 | 12300.00 | 34.00 | 1700.00 | 110.00 | 5500.00 | 200.00 | 10000.00 | 1000.00 | jaydeep agency corporation
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 35 sq. mm and upto 95 sq. mm | 1900.00 | Meter |  | 25.00 | 47500.00 | 55.00 | 104500.00 | 110.00 | 209000.00 | 130.00 | 247000.00 | 54.00 | 102600.00 | 20.00 | 38000.00 | 47.00 | 89300.00 | 246.00 | 467400.00 | 45.00 | 85500.00 | 100.00 | 190000.00 | 200.00 | 380000.00 | 38000.00 | Manish Electricals
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 185 sq. mm and upto 400 sq. mm | 100.00 | Meter |  | 65.00 | 6500.00 | 99.00 | 9900.00 | 207.00 | 20700.00 | 104.00 | 10400.00 | 72.00 | 7200.00 | 50.00 | 5000.00 | 90.00 | 9000.00 | 206.00 | 20600.00 | 65.00 | 6500.00 | 200.00 | 20000.00 | 200.00 | 20000.00 | 5000.00 | Manish Electricals
16.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 100.00 | Meter |  | 35.00 | 3500.00 | 55.00 | 5500.00 | 138.00 | 13800.00 | 182.00 | 18200.00 | 54.00 | 5400.00 | 90.00 | 9000.00 | 100.00 | 10000.00 | 35.00 | 3500.00 | 115.00 | 11500.00 | 150.00 | 15000.00 | 200.00 | 20000.00 | 3500.00 | jaydeep agency corporation, srinivasa power solution
17.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 600.00 | Meter |  | 65.00 | 39000.00 | 154.00 | 92400.00 | 248.00 | 148800.00 | 182.00 | 109200.00 | 72.00 | 43200.00 | 120.00 | 72000.00 | 180.00 | 108000.00 | 850.00 | 510000.00 | 475.00 | 285000.00 | 140.00 | 84000.00 | 200.00 | 120000.00 | 39000.00 | jaydeep agency corporation
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. a) 4 X 16 sq. mm | 8.00 | Set |  | 225.00 | 1800.00 | 1088.00 | 8704.00 | 345.00 | 2760.00 | 137.80 | 1102.40 | 415.00 | 3320.00 | 400.00 | 3200.00 | 250.00 | 2000.00 | 468.00 | 3744.00 | 150.00 | 1200.00 | 150.00 | 1200.00 | 200.00 | 1600.00 | 1102.40 | Kripa Electronics india pvt ltd
19.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. i) 3½ X 50 sq. mm | 8.00 | Set |  | 325.00 | 2600.00 | 1728.00 | 13824.00 | 621.00 | 4968.00 | 270.40 | 2163.20 | 651.00 | 5208.00 | 700.00 | 5600.00 | 350.00 | 2800.00 | 240.00 | 1920.00 | 585.00 | 4680.00 | 200.00 | 1600.00 | 500.00 | 4000.00 | 1600.00 | BATRA ENGINEERS
20.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. i) 3½ X 240 sq. mm | 4.00 | Set |  | 1450.00 | 5800.00 | 3302.00 | 13208.00 | 2594.00 | 10376.00 | 1080.00 | 4320.00 | 1742.00 | 6968.00 | 1195.00 | 4780.00 | 927.00 | 3708.00 | 1125.00 | 4500.00 | 1350.00 | 5400.00 | 350.00 | 1400.00 | 500.00 | 2000.00 | 1400.00 | BATRA ENGINEERS
| Total in Figures |  |  |  |  | 6896770.00 |  | 6080425.00 |  | 5083672.00 |  | 6521678.26 |  | 5874282.00 |  | 5467630.00 |  | 5477662.00 |  | 6442420.00 |  | 5998285.00 |  | 7278700.00 |  | 6199950.00
Lowest Amount Quoted BY: ENERGYGREEN TECHNOPOWER PVT LTD(5083672.00)

## BOQ Summary
BOQ Summary Details Tender Title: Misc. Electrical work related to NITB at R. B. Airport, Bhopal. SH Provision of High Mast at Apron Area. Tender ID: 2024_AAI_202036_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ENERGYGREEN TECHNOPOWER PVT LTD | 5083672.00 | L1
| 2 | Manish Electricals | 5467630.00 | L2
| 3 | MANNA ELECTRONICS AND ELECTRICAL WORKS | 5477662.00 | L3
| 4 | SARASWAT ENGINEERING SERVICES | 5874282.00 | L4
| 5 | Avinash Chopra | 5998285.00 | L5
| 6 | elektron | 6080425.00 | L6
| 7 | METRO ENGINEERS SERVICES | 6199950.00 | L7
| 8 | srinivasa power solution | 6442420.00 | L8
| 9 | Kripa Electronics india pvt ltd | 6521678.26 | L9
| 10 | jaydeep agency corporation | 6896770.00 | L10
| 11 | BATRA ENGINEERS | 7278700.00 | L11