## BoQ1
Government eProcurement System Created By: Benu Madhab Nayak Created Date/Time: 29-Aug-2024 05:25 PM Tender Title: Provision of power supply for EV Charging at B.P.I Airport, Bhubaneswar Tender ID: 2024_AAI_202261_1
Tender Inviting Authority: Sr. Manager (Engg-Elect.)
Name of Work: Provision of power supply for EV Charging at B.P.I Airport, Bhubaneswar.
Contract No: Tender ID: 2024_AAI_202261_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RASS CONTRACTOR AND ENGINEERS (GSTN-09AFIPR1600N1Z7) BID ID -727814 |  | Youngmen Traders (GSTN-19AEIPB6323B1ZZ) BID ID -732011 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -732206 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -732404
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date. 3.5C X 300 Sq.mm | 360.00 | Mtr | 2054.00 | 1535.00 | 552600.00 | 1325.00 | 477000.00 | 1320.00 | 475200.00 | 1450.00 | 522000.00 | 475200.00 | Yash Energy Pvt. Ltd
2.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated and PVC sheathed aluminium conductor cable of 1.1 KV grade as required. 3.5C X 300 Sq.mm | 8.00 | Set | 1058.00 | 2250.00 | 18000.00 | 950.00 | 7600.00 | 4730.00 | 37840.00 | 1500.00 | 12000.00 | 7600.00 | Youngmen Traders
3.00 | Supply of 125 mm dia PE-100 , PN-10 HDPE pipe along with all accessories like socket, bend, couplers etc. confirming to IS 4984-2016 complete etc.as required. | 640.00 | Mtr | 581.00 | 625.00 | 400000.00 | 975.00 | 624000.00 | 473.00 | 302720.00 | 750.00 | 480000.00 | 302720.00 | Yash Energy Pvt. Ltd
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 60.00 | Mtr | 100.00 | 75.00 | 4500.00 | 50.00 | 3000.00 | 130.00 | 7800.00 | 80.00 | 4800.00 | 3000.00 | Youngmen Traders
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required. Above 185 sq. mm and upto 400 sq. mm | 680.00 | Mtr | 117.00 | 95.00 | 64600.00 | 40.00 | 27200.00 | 165.00 | 112200.00 | 70.00 | 47600.00 | 27200.00 | Youngmen Traders
6.00 | Laying of 125 mm OD HDPE pipe PN 10 grade at a depth of 0.8 meter below the ground level including excavation in soft soil , refilling of the trench, after laying of HDPE pipe and cable etc, complese as required. | 640.00 | Mtr | 179.00 | 135.00 | 86400.00 | 150.00 | 96000.00 | 220.00 | 140800.00 | 290.00 | 185600.00 | 86400.00 | RASS CONTRACTOR AND ENGINEERS
7.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 6557.00 | 8500.00 | 17000.00 | 8000.00 | 16000.00 | 14300.00 | 28600.00 | 9000.00 | 18000.00 | 16000.00 | Youngmen Traders
8.00 | Supplying and laying of 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 12.00 | Mtr | 128.00 | 175.00 | 2100.00 | 95.00 | 1140.00 | 297.00 | 3564.00 | 525.00 | 6300.00 | 1140.00 | Youngmen Traders
9.00 | Providing and fixing 25 mm X 5 mm G.I strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 12.00 | Mtr | 620.00 | 625.00 | 7500.00 | 435.00 | 5220.00 | 682.00 | 8184.00 | 750.00 | 9000.00 | 5220.00 | Youngmen Traders
10.00 | Design, Supply, Installation, Testing and commissioning of Outdoor cubicle LT panel as per IEC 60439, weather & vermin proof, powder coated, free floor standing, fully compartmentalised , bottom entry double door type , Outdoor canopy type Electrical Main Distribution panel (Feeder Pillar Panel), generally conforming to IP-65 and higher, fabricated from 2 mm. thick CRCA sheet , treated through seven tank process along with detachable 3mm thick gland plate sutable for operation on 415V +/-10% , 3 phase , 4 wire, 50 Hz AC supply, TPN aluminium busbars of high conductivity, DMC/SMC busbar supports with bottom base channel made out of MS section not less than 100 mm x50 mm x 5 mm thick, entire panel shall have a common copper earthbar of size as per IS 3043 subject to minimum 30 mm x 5 mm at the rear with 2 Nos. earth stud ,solid connection from main busbar to switchgears with required size of aluminium busbar & control wiring with 2.5 sqmm FRLS insulated copper conductor cable, cable alleys, lifting hooks including swapping, recoiling and handling of all incoming and outgoing cables, Civil work for RCC foundation, cutting , fixing, grouting, painting and sign writing etc. complete as required. Incomer : 630A, 4P MCCB, Microprocessor based release (Ics = Icu = 36kA) with inbuilt Adjustable O/L & S/C and E/F protection with spreader link and rotary handle as per specifion - 02 nos. Buscoupler : 630A, 4P MCCB, Microprocessor based release (Ics = Icu = 36kA) with inbuilt Adjustable O/L & S/C and E/F protection with spreader link and rotary handle as per specification - 01 No. Electrical and Mechanical Interlocking between incommers and bus coupler - 1 set Busbar:4P aluminium bus bars of 800A Capacity with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 36 KA for 1 sec Out goings 160, FP, 25kA MCCB (Ics=100%Icu) with adjustable Thermal magnetic release having O/L & S/C and Earth Fault protection with rotary handle - 4 Nos 125A, FP, 25kA MCCB (Ics=100%Icu) with adjustable Thermal magnetic release having O/L & S/C and Earth Fault protection with rotary handle - 2 Nos Metering: Digital type voltmer, accuracy class 0.5 of suitable range along with inbuilt selector switch-02 No's Digital type Ammeter, accuracy class 0.5 of suitable range along with inbuilt selector switch with 03 numbers class 0.5 accuracy, 15VA burdan & suitable range C.T's -02 NO's. Intelligent Digital MFM meter and Class 0.5 accuracy and 10 VA burden, suitable to measure voltage,Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, with RS 485 port with suitable ratio 3 no's cast resin CTs = 08 set (for02 incomers+06 out goings). LED Phase Indication lamp with control MCBs - 02 Set's and ON-OFF indication lamps (LED type) -09 sets SURGE PROTECTION DEVICE:02 No Surge protection device Type 2 ( Class C), 4 Mode, MOV type suitable for 8/ 20µs surge,Voltage Protection level Up < 1.8kV, Operating Temperature -40 deg 'c' - +80 deg 'C', Connected Between 3Nos. phase to neutral and 1Nos. neutral to earth with discharge Current Imax. ≥ 40KA Per mode & In ≥ 20kA per Mode. SPD with 63A 4P HRC fuses of 100kA breaking capacity. For connecting SPD mini 10sqmm copper wire must be used & length of connecting leads shall not be more than 500mm for per mode connection with each busbar including all necessary accessories. The SPD shall complience with IEC 61643-11 and certified by CE and ROHS | 1.00 | Job | 601960.00 | 625000.00 | 625000.00 | 700000.00 | 700000.00 | 643500.00 | 643500.00 | 375000.00 | 375000.00 | 375000.00 | Manish Electricals
| Total in Figures |  |  |  |  | 1777700.00 |  | 1957160.00 |  | 1760408.00 |  | 1660300.00
Lowest Amount Quoted BY: Manish Electricals(1660300.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of power supply for EV Charging at B.P.I Airport, Bhubaneswar Tender ID: 2024_AAI_202261_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 1660300.00 | L1
| 2 | Yash Energy Pvt. Ltd | 1760408.00 | L2
| 3 | RASS CONTRACTOR AND ENGINEERS | 1777700.00 | L3
| 4 | Youngmen Traders | 1957160.00 | L4