## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 27-Aug-2024 12:56 PM Tender Title: Replacement of existing package AC units by VRV at Maharana Pratap Airport, Udaipur. Tender ID: 2024_AAI_202666_1
Tender Inviting Authority: SM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: Replacement of existing package AC units by VRV at Maharana Pratap Airport, Udaipur.
Contract No: AAI/UDR/ENGG(E)/2024-25/AC/VRV
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (GSTN-24AAHCP2093C1ZP) BID ID -727683 |  | VOLTAS LIMITED (GSTN-07AAACV2809D1ZO) BID ID -731276 |  | Utility Services (GSTN-06AABFU8051C1ZG) BID ID -731847 |  | HV AIRCONDITIONING SYSTEMS PVT. LTD. (GSTN-07AAACH0827M1ZL) BID ID -732414 |  | NIRMAN ELECTRIC STORE (GSTN-08AOIPS5332P1Z8) BID ID -733678
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation, Testing & Commissioning of commulative upto 222 HP (individual unit not more than 32 HP) modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling, having all hermetically sealed inverter type Scroll Compressor(s) having 05 years warranty on compressor, minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 52°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant, ready to use, conforming to technical specifications and complete as required at site. | 222.00 | HP | 0.00 | 20500.00 | 4551000.00 | 15951.00 | 3541122.00 | 12635.00 | 2804970.00 | 19000.00 | 4218000.00 | 19500.00 | 4329000.00 | 2804970.00 | Utility Services
2.00 | Supply, Installation, Testing and Commissioning of various capacities between 1.5 Tr. to 2.8 Tr. (max. 3 types of Tr. shall be used) VRV/VRF High wall type Indoor unit equipped with washable synthetic media pre- filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cord less remote control, drain pan, necessary accessories etc., suitable for operation on 230 V ± 10%, 50 Hz, single phase AC supply to cool the offices of Operational cum Admin block, conforming to technical specifications and complete as required at site. | 183.00 | TR | 0.00 | 9200.00 | 1683600.00 | 9514.00 | 1741062.00 | 12655.00 | 2315865.00 | 11500.00 | 2104500.00 | 16000.00 | 2928000.00 | 1683600.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
3.00 | Supply, Installation, Testing and Commissioning of PC based centralized monitoring and remote control system to control all the individual wall type indoor unit including supply of CPU, Monitor, UPS with minimum of 15 minutes backup, controller etc., with 05 years warranty on complete set incl. hardware and software, conforming to technical specifications and complete as required at site. | 1.00 | Each | 0.00 | 148000.00 | 148000.00 | 136450.00 | 136450.00 | 222325.00 | 222325.00 | 250000.00 | 250000.00 | 116000.00 | 116000.00 | 116000.00 | NIRMAN ELECTRIC STORE
4.00 | Supply, Installation, Testing and Commisioning of Y - Joint (Refnut) for connecting all the indoor unit and outdoor unit piping, conforming to technical specifications and complete as required at site. | 65.00 | Each | 0.00 | 3200.00 | 208000.00 | 3879.00 | 252135.00 | 3404.00 | 221260.00 | 3850.00 | 250250.00 | 4000.00 | 260000.00 | 208000.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
5.00 | Supply, Installation, Testing and Commissioning of Passive Infrared (PIR) technology based occupancy sensors having high performance, regulating programmable type, suitable for connected load upto 10 Amp. and 5 meter (approx.) diameter coverage area along with necessary fixing arrangement including programming at site etc. The same shall be suitable for above mentioned indoor split Air conditioners units of VRV / VRF system based on occupancy, including supply and laying cables for power, control and communication from AC to sensor, ready to operate, conforming to technical specifications and complete as required at site. (Sensor make reference : Philips/ Siemens/ Johnson Controls/ Honeywell or equivalent reputed make). | 19.00 | Each | 0.00 | 14000.00 | 266000.00 | 6549.00 | 124431.00 | 8333.00 | 158327.00 | 25000.00 | 475000.00 | 2200.00 | 41800.00 | 41800.00 | NIRMAN ELECTRIC STORE
6.00 | Design, Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of various nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable supports of GI, jointing/brazing including accessories, insulated with XLPE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness for Suction and Liquid lines, all accessories, conforming to following technical specifications, approved drawings and complete as required at site. 1) Two separate runs pertaining to suction and liquid line wil be measured as a single running meter. 2) The Copper Piping & Piping Circuit should be with Minimum Number of joints, which shall be attained by using one end expanded tubes and bending the tubes instead of using elbow joints wherever 90 degree bending is required. (3) Piping should be routed at site in such a manner, that brazed joints in the refrigeration piping are kept to a minimum. (4) The makes of tube fittings shall be same as that of tubes. (5) The thickness of fittings used shall be same as that of the pipe. | 900.00 | Meter | 0.00 | 1870.00 | 1683000.00 | 2528.00 | 2275200.00 | 1701.00 | 1530900.00 | 1800.00 | 1620000.00 | 1210.00 | 1089000.00 | 1089000.00 | NIRMAN ELECTRIC STORE
7.10 | Supply, Installation, Testing and Commissioning of CPVC pipes of following sizes, condensate drain piping shall be insulated using 9 mm thick nitrile rubber tubes including Chiseling, fitting, supports, plastering incl. minor civils works to make the surface good as same as before, conforming to technical specifications, approved drawings and complete as required at site. 25 mm dia | 200.00 | Meter | 0.00 | 175.00 | 35000.00 | 209.00 | 41800.00 | 354.00 | 70800.00 | 250.00 | 50000.00 | 190.00 | 38000.00 | 35000.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
7.20 | 32 mm dia | 125.00 | Meter | 0.00 | 240.00 | 30000.00 | 300.00 | 37500.00 | 498.00 | 62250.00 | 300.00 | 37500.00 | 250.00 | 31250.00 | 30000.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
7.30 | 40 mm dia | 150.00 | Meter | 0.00 | 315.00 | 47250.00 | 407.00 | 61050.00 | 673.00 | 100950.00 | 350.00 | 52500.00 | 320.00 | 48000.00 | 47250.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
7.40 | 50 mm dia | 70.00 | Meter | 0.00 | 500.00 | 35000.00 | 602.00 | 42140.00 | 985.00 | 68950.00 | 400.00 | 28000.00 | 400.00 | 28000.00 | 28000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD., NIRMAN ELECTRIC STORE
8.00 | Supply of 4 x 25 Sqmm size XLPE insulated and PVC sheathed power cable of grade 1.1 KV, aluminium conductor armoured cable confirming to IS 7098 (Part - I) with up to date amendments, conforming to technical specifications and complete as required at site. | 350.00 | Meter | 0.00 | 270.00 | 94500.00 | 234.00 | 81900.00 | 299.00 | 104650.00 | 200.00 | 70000.00 | 230.00 | 80500.00 | 70000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD.
9.00 | Supplying and installing of following size of non perforated Hot Dipped Galvanised Iron Raceway (Galvanisation thickness not less than 50 microns), in convenient sections, joined with connectors, support from the wall with G.I. support including bolts & nuts, painting suspenders etc. as required. 300 mm width x 100 mm depth x 1.6 mm thickness | 30.00 | Meter | 0.00 | 1600.00 | 48000.00 | 1062.00 | 31860.00 | 1707.00 | 51210.00 | 1200.00 | 36000.00 | 1053.00 | 31590.00 | 31590.00 | NIRMAN ELECTRIC STORE
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/ cable tray, conforming to technical specifications and complete as required at site. Upto 35 sq. mm (clamped with 1mm thick saddle on wall surface) | 350.00 | Meter | 0.00 | 87.00 | 30450.00 | 127.00 | 44450.00 | 116.00 | 40600.00 | 65.00 | 22750.00 | 30.00 | 10500.00 | 10500.00 | NIRMAN ELECTRIC STORE
11.00 | Supplying and laying following size of FRLS PVC insulated and PVC round sheathed, Multicore Annealed Bare Copper Conductor (flexible) industrial cable for 1.1 kV grade, as per IS 694:2010 upto date ammended, on cable tray/ wall surface, conforming to technical specifications and complete as required at site. 3 x 1.5 sq.mm | 1400.00 | Meter | 0.00 | 100.00 | 140000.00 | 121.00 | 169400.00 | 181.00 | 253400.00 | 80.00 | 112000.00 | 90.00 | 126000.00 | 112000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD.
12.00 | Supplying and drawing following size of PVC type D insulated, core laid up, overall shielded and overall PVC type ST-3 sheathed cable, multicore Copper Conductor (flexible) cable of 1.1 kV grade for communication, on cable tray/ wall surface, conforming to technical specifications and complete as required at site. 2 x 1.5 sq.mm | 1500.00 | Meter | 0.00 | 125.00 | 187500.00 | 98.00 | 147000.00 | 168.00 | 252000.00 | 85.00 | 127500.00 | 70.00 | 105000.00 | 105000.00 | NIRMAN ELECTRIC STORE
13.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 6 way (8+ 18), Double door | 6.00 | Each | 0.00 | 17200.00 | 103200.00 | 6580.00 | 39480.00 | 5293.00 | 31758.00 | 5000.00 | 30000.00 | 9153.00 | 54918.00 | 30000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD.
14.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 80.00 | Each | 0.00 | 306.00 | 24480.00 | 321.00 | 25680.00 | 368.00 | 29440.00 | 400.00 | 32000.00 | 400.00 | 32000.00 | 24480.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
15.00 | Supplying and fixing following rating, three pole neutral, 415 V, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A, TPN | 6.00 | Each | 0.00 | 2300.00 | 13800.00 | 2178.00 | 13068.00 | 2715.00 | 16290.00 | 2000.00 | 12000.00 | 1384.00 | 8304.00 | 8304.00 | NIRMAN ELECTRIC STORE
16.00 | Providing and fixing following rating and breaking capacity MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc., conforming to technical specifications and complete as required at site. 40 A, 25KA, FPMCCB (Ics = 100% of Icu) | 4.00 | Each | 0.00 | 9900.00 | 39600.00 | 7234.00 | 28936.00 | 3004.00 | 12016.00 | 7500.00 | 30000.00 | 4890.00 | 19560.00 | 12016.00 | Utility Services
17.00 | Providing and fixing following rating and breaking capacity MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc., conforming to technical specifications and complete as required at site. 63 A, 25KA, FPMCCB (Ics = 100% of Icu) | 6.00 | Each | 0.00 | 11800.00 | 70800.00 | 7234.00 | 43404.00 | 4520.00 | 27120.00 | 7500.00 | 45000.00 | 5170.00 | 31020.00 | 27120.00 | Utility Services
18.00 | Supply and top up of refrigerent gas R-410A in liquid line length, conforming to technical specifications and complete as required at site. | 140.00 | KG | 0.00 | 600.00 | 84000.00 | 771.00 | 107940.00 | 1008.00 | 141120.00 | 1000.00 | 140000.00 | 1200.00 | 168000.00 | 84000.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
19.00 | Supply and fixing of MS duly painted floor mounted stand with MS angle size not less than 35 x 35 x 5 suitable for VRF / VRV outdoor unit supplied at sr. no. 1 complete as required at site. | 10.00 | Each | 0.00 | 8200.00 | 82000.00 | 5790.00 | 57900.00 | 7582.00 | 75820.00 | 5500.00 | 55000.00 | 5500.00 | 55000.00 | 55000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD., NIRMAN ELECTRIC STORE
20.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt, conforming to technical specifications and complete as required at site. | 4.00 | Each | 0.00 | 15500.00 | 62000.00 | 5392.00 | 21568.00 | 11802.00 | 47208.00 | 12500.00 | 50000.00 | 10500.00 | 42000.00 | 21568.00 | VOLTAS LIMITED
21.00 | Providing and fixing 25 mm x 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter | 0.00 | 310.00 | 9300.00 | 462.00 | 13860.00 | 648.00 | 19440.00 | 150.00 | 4500.00 | 1200.00 | 36000.00 | 4500.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD.
22.00 | Providing and fixing 25 mm x 5 mm G.I. strip on surface or in recess for connections etc. as required. | 100.00 | Meter | 0.00 | 231.61 | 23161.00 | 115.00 | 11500.00 | 242.00 | 24200.00 | 100.00 | 10000.00 | 358.00 | 35800.00 | 10000.00 | HV AIRCONDITIONING SYSTEMS PVT. LTD.
| Total in Figures |  |  |  |  | 9699641.00 |  | 9090836.00 |  | 8682869.00 |  | 9862500.00 |  | 9745242.00
Lowest Amount Quoted BY: Utility Services(8682869.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of existing package AC units by VRV at Maharana Pratap Airport, Udaipur. Tender ID: 2024_AAI_202666_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Utility Services | 8682869.00 | L1
| 2 | VOLTAS LIMITED | 9090836.00 | L2
| 3 | M/s. PRANAM HVAC ENGINEERING PVT. LTD. | 9699641.00 | L3
| 4 | NIRMAN ELECTRIC STORE | 9745242.00 | L4
| 5 | HV AIRCONDITIONING SYSTEMS PVT. LTD. | 9862500.00 | L5