## BoQ1
Government eProcurement System Created By: Brijesh Kumar Rajpoot Created Date/Time: 19-Sep-2024 12:35 PM Tender Title: Installation of AWOS at MET Park 27 and Mid at LBSI Airport, Varanasi. SH- Electrical Works. Tender ID: 2024_AAI_204265_1
Tender Inviting Authority: Sr, Manager (Engg.-E), LBSI Airport Varanasi.
Name of Work: Installation of AWOS at MET Park 27 & Mid at LBSI Airport, Varanasi. SH: Electrical Works.
Contract No: 2024_AAI_204265_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Dubey Trading Company(GSTN-NA)--739280 |  | SANKAT MOCHAN ELECTRICALS(GSTN-NA)--740233 |  | GVD ENGINEERS & CONTRACTOR(GSTN-NA)--740238
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Following sizes of Aluminium Armoured XLPE insulated & PVC sheated aluminium conductor cable of 1.1 KV grade as per IS 7098:1988 Part 1 with upto date amendments complete as required. 3.5 C x 35 sq.mm | 259.00 | Meter |  | 180.00 | 46620.00 | 300.00 | 77700.00 | 220.00 | 56980.00 | 46620.00 | Dubey Trading Company
2.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.conforming to IS 14930, Part II complete with fitting and cutting,jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 297.00 | Meter |  | 130.00 | 38610.00 | 200.00 | 59400.00 | 195.00 | 57915.00 | 38610.00 | Dubey Trading Company
3.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.conforming to IS 14930, Part II complete with fitting and cutting,jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 40 mm dia | 25.00 | Meter |  | 135.00 | 3375.00 | 180.00 | 4500.00 | 170.00 | 4250.00 | 3375.00 | Dubey Trading Company
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing DWC/HDPE/RCC/ HUME/ METAL pipe as required Upto 35 sq. mm | 325.00 | Meter |  | 25.00 | 8125.00 | 30.00 | 9750.00 | 48.00 | 15600.00 | 8125.00 | Dubey Trading Company
5.00 | Design, manufacture, supply, installation, testing and commissioning of outddoor type feeder pillar box of suitable size with double door fabricated from 2 mm thick CRCA steel sheet including accomodation/fixing of 01 No. 4 Pole ,25kA , 415V, 63A MCCB (with Thermal Magnetic Release) with rotatory handle and 03 No (R,Y,B) indication LED lamp , suitable for termiantion 01No. incomer and 01 No. outgoing power cable, cable entry from bottom, arrangment for earth connection, totally enclosed type with free standing floor mounted, dust & vermin proof suitable to be used outside etc. as per site requirement complete as required. ( The work includes Instaling/Fixing of the Feeder panel by making suitable size concrete foundation & MS angle support 35 mm x 35 mm x 6 mm) | 1.00 | Job |  | 28000.00 | 28000.00 | 19200.00 | 19200.00 | 19500.00 | 19500.00 | 19200.00 | SANKAT MOCHAN ELECTRICALS
6.00 | Design, fabrication, assembling, supply, installation, testing and commissioning of outdoor cubicle type double door LT panels with triangular shape rain shelter canopy & 50 mm x 50 mm x 6 mm thick MS angle iron support for fixing the feeder pillar on cement concrete foundation suitable for 415 V 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentised design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning and finishing complete 7 tank process for powder coating in approved shade, extendable type TPN aluminium alloy busbars of high condectivity, DMC/SMC busbar supports, entire panel shall have earthbar, require size of aluminium busbar & control wiring with 2.5 sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates i/c civil work & accessories as per specification and providing switchgears, metering instruments etc. as per following. INCOMER a) 63 Amps thermal magnetic release four pole MCCB of breaking capacity 25 KA with O/C, S/C, E/F Protection, Make: L & T Cat No CM91612OOHOOG or Equivalent with rotary handle - 2 No. BUS COUPLER b) 63 Amps four pole MCCB Switch Disconnector without protection release. Make: L & T Cat No CM90716OOHO or Equivalent with rotary handle -1 No. INTERLOCKING Elecrtrical & Mechanical interlocking between Incomers & Buscoupler Indicating & Metering (i) LED Type Indicating lamps (Red,Yellow,Blue) with MCB protection - 06 Nos. (ii) Digital Voltmeter (0-500V) with MCB protection and built in selector switch-- 2 Set (iii) Digital Ammeters 3 with MCB protection, and built in selector switch or equivalent - 2 set (iv) CT 75/5 - 6 Nos. OUT GOING a) 32 Amps 4 Pole MCB, 10 KA-02 Nos. b) 20 Amps DP MCB, 10 KA-02 Nos. BUS BARS : 100 Amps TPN Bus bar of Aluminium. - 1set. | 1.00 | Job |  | 93500.00 | 93500.00 | 87000.00 | 87000.00 | 102000.00 | 102000.00 | 87000.00 | SANKAT MOCHAN ELECTRICALS
7.00 | Supply & fixing 2 mm thick CRCA steel sheet outdoor type feeder pillar of suitable size with triangular shape rain shelter canopy & 35 mm x35 mm x 6 mm thick MS angle iron support for fixing the feeder pillar on cement concrete foundation & fixing of switchgears with nut bolts, earthing, connections, painting etc as required. The feeder pillar shall have ventilation arrangement, insect trap mesh but duly protected against heavy rainwater ingress, duly painted with powder coated paint from all sides and having proper locking arrangement.The enclosure shall be suppiled with the following equipment/switch gear and suitable to accomodate the same :- a- 2 KVA UPS - 01 No. ( Input voltage range 150-280 V AC, Output Voltage:230 V AC, Breakup time: 30 minute, Harmonic distortion: <3% (linear load),, Operating temperature: 0 degree to 55 degree C, Short circuit, overload, battery deep discharge & over charge protection). b- 20 Amp SPN MCB for incoming power-01 No. c- 5/6 A switch socket combine mounted over phenolic laminated sheet fixed on suitable size metal box. - 05 Nos. d- One number 8 way Single door SPN MCB Distribution Box consisiting of following MCB's :- i) 6 A SP MCB - 03 Nos. ii) 10 A SP MCB - 01 No. iii) Blanking plate - 02 No. | 1.00 | Job |  | 80850.00 | 80850.00 | 50000.00 | 50000.00 | 51000.00 | 51000.00 | 50000.00 | SANKAT MOCHAN ELECTRICALS
8.00 | Supply, Installation, testing and commissioning of 3.0 KVA UPS with True Online IGBT based rectifier with of Input Voltage range 180-280V AC , Output Voltage 230V AC, Harmonic distortion <7%, Operating Temperature : 0 degree to 45 degree Centigrade, having LCD display, with 6Nos. 42Ah, 12V battery having backup time : 30 minutes. | 1.00 | Job |  | 55000.00 | 55000.00 | 79000.00 | 79000.00 | 64000.00 | 64000.00 | 55000.00 | Dubey Trading Company
9.00 | For UPS installation ( 3 KVA ) Design, manufacture, supply & installation of outdoor type MS box of size 0.650m (W) X 0.500m (D) x 0.650m(H) fabricated from 2 mm thick MS steel, with locking arrangement of door, cable entry from bottom with 2 mm gland plate, arrangement for earth connection, totally enclosed type, the box enclosure to be fixed/ mounted on collapsible/frangible post /leg ( 04 Nos.) with frangible coupling, mounting flanges duly painted and the same shall be grouted in the cement concrete foundation. The box enclosure should be welded with 50mm (OD) , 3mm thick and 300 mm long MS/GI pipe (leg) on all four corners for holding box with frangible coupling & flange. The box enclosure shall have triangular shape rain shelter canopy, ventilation arrangement, insect trap mesh and duly protected against heavy rainwater ingress, ventilating axial fan of 120mm, 230V, 50hz, duly painted with powder coated paint from all sides and having proper locking arrangement complete as required. The box enclosure should have:- - Terminal block , 32A , 4P dual row -01 No for main incomer cable. -25 A DP MCB for input power supply to UPS - Distribution section with 25 A DP- 01 No from UPS, 6A SP MCB -02 & 16 A SP MCB -02 No for outgoing. - 6/15A 3 pin socket -03 No. - Neutral link 10way -01 No - Earth link 10way - 01 No. The work includes making foundation as required. | 1.00 | Job |  | 30250.00 | 30250.00 | 23225.00 | 23225.00 | 25500.00 | 25500.00 | 23225.00 | SANKAT MOCHAN ELECTRICALS
10.00 | For UPS Battery installation ( 42Ah/12V 06 Nos.) Design, manufacture, supply & installation of outdoor type MS box of size 0.650m (W) X 0.500m (D) x 0.650m(H) fabricated from 2 mm thick MS steel, with locking arrangement of door, cable entry from bottom with 2 mm gland plate, arrangement for earth connection, totally enclosed type, the box enclosure to be fixed/ mounted on collapsible/frangible post /leg ( 04 Nos.) , frangible coupling , mounting flanges duly painted and same shall be grouted in the cement concrete foundation. The box enclosure should be welded with 50mm (OD), 3mm thick and 300 mm long MS/GI pipe (leg) on all four corners for holding box with frangible coupling & flange. The box enclosure shall have triangular shape rain shelter canopy, ventilation arrangement, insect trap mesh and duly protected against heavy rainwater ingress, ventilating axial fan of 120mm, 230V, 50hz, duly painted with powder coated paint from all sides and having proper locking arrangement complete as required. The work includes making foundation as required. | 1.00 | Job |  | 16500.00 | 16500.00 | 16773.00 | 16773.00 | 21000.00 | 21000.00 | 16500.00 | Dubey Trading Company
11.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 15000.00 | 30000.00 | 6472.00 | 12944.00 | 19500.00 | 39000.00 | 12944.00 | SANKAT MOCHAN ELECTRICALS
12.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Meter |  | 1500.00 | 15000.00 | 1360.00 | 13600.00 | 2200.00 | 22000.00 | 13600.00 | SANKAT MOCHAN ELECTRICALS
13.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 4.00 | Meter |  | 1400.00 | 5600.00 | 1020.00 | 4080.00 | 1800.00 | 7200.00 | 4080.00 | SANKAT MOCHAN ELECTRICALS
14.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 5000.00 | 20000.00 | 6080.00 | 24320.00 | 7000.00 | 28000.00 | 20000.00 | Dubey Trading Company
15.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 12.00 | Meter |  | 200.00 | 2400.00 | 220.00 | 2640.00 | 70.00 | 840.00 | 840.00 | GVD ENGINEERS & CONTRACTOR
16.00 | Providing, laying and fixing following dia G.I. pipe (medium class) complete with G.I. fittings , clamps etc for drain /nala crossing as required. 65 mm dia. | 6.00 | Meter |  | 900.00 | 5400.00 | 850.00 | 5100.00 | 150.00 | 900.00 | 900.00 | GVD ENGINEERS & CONTRACTOR
17.00 | Supply of 4x4 sqmm flexible, PVC insulated & sheathed copper conductor cable suitable upto 1100V grade conforming to IS:694/1990 with latest amendments. | 80.00 | Meter |  | 175.00 | 14000.00 | 310.00 | 24800.00 | 250.00 | 20000.00 | 14000.00 | Dubey Trading Company
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed /XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5X 35 sqmm. | 5.00 | Each |  | 400.00 | 2000.00 | 280.00 | 1400.00 | 1500.00 | 7500.00 | 1400.00 | SANKAT MOCHAN ELECTRICALS
19.00 | Supply of 3x1.5 sqmm flexible, PVC insulated copper conductor cable suitable upto 1100V grade conforming to IS:694/1990 with latest amendments. | 25.00 | Meter |  | 60.00 | 1500.00 | 80.00 | 2000.00 | 150.00 | 3750.00 | 1500.00 | Dubey Trading Company
20.00 | Supply of 3x4 sqmm flexible, PVC insulated copper conductor cable suitable upto 1100V grade conforming to IS:694/1990 with latest amendments. | 10.00 | Meter |  | 135.00 | 1350.00 | 220.00 | 2200.00 | 200.00 | 2000.00 | 1350.00 | Dubey Trading Company
21.00 | Supply of 3 pin 6A plug Top suitable for 220V, 50 Hz AC supply. | 3.00 | Each |  | 70.00 | 210.00 | 51.00 | 153.00 | 90.00 | 270.00 | 153.00 | SANKAT MOCHAN ELECTRICALS
| Total in Figures |  |  |  |  | 498290.00 |  | 519785.00 |  | 549205.00
Lowest Amount Quoted BY: Dubey Trading Company(498290.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of AWOS at MET Park 27 and Mid at LBSI Airport, Varanasi. SH- Electrical Works. Tender ID: 2024_AAI_204265_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Dubey Trading Company | 498290.00 | L1
| 2 | SANKAT MOCHAN ELECTRICALS | 519785.00 | L2
| 3 | GVD ENGINEERS & CONTRACTOR | 549205.00 | L3