## BoQ1
Government eProcurement System Created By: Samir Kumar Mazumder Created Date/Time: 24-Oct-2024 11:44 AM Tender Title: Renovation of Fire Fighting System in Existing Terminal Building at Silchar Airport Tender ID: 2024_AAI_204904_2
Tender Inviting Authority: Sr. Manager (Engg-Electrical), AAI, Silchar Airport.
Name of Work: Renovation of Fire Fighting System in Existing Terminal Building at Silchar Airport.
Tender Id: 2024_AAI_204904_2
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BA-PAN ENGINEERING co. (GSTN-07AYDPS2409Q1ZX) BID ID -747802 |  | SHIMMER ENTERPRISE (GSTN-18ACKPB9483G1ZA) BID ID -753742 |  | GVD ENGINEERS & CONTRACTOR (GSTN-NA) BID ID -753734
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I - ELECTRICAL WORK MAIN HYDRANT PUMP SET Supplying, installing, testing and commissioning of electric driven Fire Pump suitable for automatic operation consisting of the following (as per latest CPWD specification and its amendments up to date.) 1) Fire Pump with bronze impeller horizontal split casing centrifugal suction type multi stage having a capacity of 2850 Ltrs/minute against a total head of 70 meters so as to ensure a minimum pressure of 3.5 kg per square cm. at the highest and farthest outlet at the specified flow complete with necessary Pressure Gauge on the delivery side including by pass arrangement for periodical testing of the working of the pumping set with 50mm dia G.I. pipe upto 5 Mtr. length & control valve. The Pump shall be provided with mechanical seals. 2) Squirrel cage type TEFC motor suitable for operation on 415V, 3 phases 50 Hz. system of 50 HP for the above pump with synchronous speed of 1500 RPM and flexible coupling with the Pump Motor should confirm to latest IS standards and ECBC norms. 3) Common bed plate fabricated from mild steel channel or Cast Iron type. 4) Construction of cement concrete foundation as required. 5) All coupling of pump and motor should be covered with Safety Guard. 6) PRV, fittings and assoicated spares shall be provided to mount with the existing piping systems etc. as required. 7) Provision of vibration damping arrangement by cushy foot mounting, as required complete in all respects. | 2.00 | Job | 0.00 | 500000.00 | 1000000.00 | 478428.00 | 956856.00 | 520000.00 | 1040000.00 | 956856.00 | SHIMMER ENTERPRISE
2.00 | DIESEL PUMP SET Supply, Installation, Testing and Commissioning of Diesel Engine driven Fire Pump suitable for automatic operation consisting of the following (as per specifications.) 1) Horizontal centrifugal type, Fire Pump with bronze impeller complete for delivery of 2850 Ltrs/minute at a total head of 70 meters so as to ensure a minimum pressure of 3.5 kg per sq.cm. at the highest & farthest outlet at the specified flow, complete with necessary pressure gauge on the delivery side including by pass arrangement for periodical testing of the working of the pump set as required. The pump shall be provided with mechanical seals. 2) Water cooled cold starting type multi cylinder 4 stroke diesel engine, developing suitable minimum BHP at 1500 RPM for the above pump set with automatic starting mechanism, cooling system with radial cool engine, maintenance free batteries, battery charge unit, flexible coupling with the pump. Provision of additional 200 ltr capacity diesel tank and connecting fuel piping from the diesel tank. Provision of vibration damping arrangement by cushy foot mounting, as required complete in all respects. 3) Common bed plate fabricated from mild steel channel or Cast Iron type. 4) Construction of cement concrete pump foundation as required. 5) Exhaust pipe with thermal insulation with 50mm thick Glass wool insulation and aluminium cladding 24 SWG sheet around upto external wall outside the pump room as directed by Engineer-In-Charge complete in all respects. 6) All coupling of Pump and Motor should be covered with Safety Guard. 7) PRV, fittings and associated spares shall be provided to mount with the existing piping systems etc. as required. | 1.00 | Job | 0.00 | 770000.00 | 770000.00 | 719767.00 | 719767.00 | 790000.00 | 790000.00 | 719767.00 | SHIMMER ENTERPRISE
3.00 | JOCKEY PUMP SET Supplying, installation, testing and commissioning of Electric Motor driven automatic pressurization Pump Set consisting of the following (As per specification). 1) Centrifugal Pump of 180 LPM capacity capable of building up pressure lost in any leakage in the system against a total head of 70 m approx. complete with necessary Pressure Gauge on the delivery side including by-pass arrangement for testing of the working of the pumping set and with mechanical seals as required. 2) Squirrel cage A.C. induction motor suitable for operation on 415 V, 3 phase 50 Hz. A.C. supply and of minimum 10 HP for the above Pump with flexible coupling as per specification and conforming to IS: 325. 3) Common bed plate fabricated of mild Steel Channel or Cast Iron type. 4) Provision of vibration damping arrangement by cushy foot mounting, as required complete in all respects. 5) All couplings of Pump & Motors should be covered with Safety Guard. 6) PRV, fittings and assoicated spares shall be provided to mount with the existing piping systems etc. as required | 1.00 | Job | 0.00 | 130000.00 | 130000.00 | 217000.00 | 217000.00 | 220000.00 | 220000.00 | 130000.00 | BA-PAN ENGINEERING co.
4.00 | CONTROL PANEL: Fabrication, supplying, erection testing and commissioning of fully automatic motor control panel, totally enclosed cubical type free standing, floor mounting compartmentalized, sectionalized, dust, damp and vermin proof with suitable natural ventilation arrangement, front accessible with lockable hinged doors, fabricated from 2mm thick CRCA sheet (to give IP 54 protection) powder coated of spray painted with approve colour shade, heavy four strip sleeved aluminium bus bar, bus bar supports interconnecting from bus bars to outgoing switches / MCCB's including earthing the board suitable for operation on 415V, 3 phase, 50 Hz AC supply to accommodate the following including numbering etc. as required Common cubical panel in fire pump House as described above the following: INCOMMER: 2 Nos 250 A TPN MCCB (36 KA) with mechanical/ electrical interlocking 1 Sets of 250 Amps. TPN Al. Bus bars with color coded heat shrinkable PVC sleeves. INSTRUMENTS: 1 sets digital voltmeter for 3 phase, 4 wire operation with inbuilt selector switches alongwith 3 No. control MCB's., 1 sets digital ammeter of suitable range (measure 0 to 250 Amp) for 3 phase, 4 wire operation with inbuilt selector switches and 3 No. suitable range CT's., 1 Sets of phase indicating lamps, LED type, RYB. OUTGOING: FEEDER FOR MAIN PUMPS - 02 Nos 02 Nos 160 A 25 kA TP MCCB , 50 HP 3 phase 415V fully automatic start delta starters with 02 Nos 0-100 Amps. Ammeter with selector switch and suitable rated current transformers. Starter with over load relay, single phase preventer and indicating lamps with ON / OFF push buttons. 02 Nos Auto manual selector switch. FEEDER FOR JOCKEY PUMPS - 01 No 01 No 63A 25 kA TP MCCB , 10 HP 3 phase 415V DOL starter with 1 No 0-25 Amps. Ammeter with selector switch and suitable rated current transformers. Starter with over load relay, single phase preventer and indicating lamps with ON / OFF push buttons. 01 No Auto manual selector switch. DIESEL ENGINE PUMP - 01 No a) 20Amps DPMCB - 01 No. b) Battery charger with transformer with rectifier resistance DC ammeter, DC voltmeter, Trickle / booster / off selector switch - 1 No. c) 1 set of indicating lamps for the following : 1. phase indication 2. battery charger on 3. over load relay 4. DC supply on 5. control switch on 6. Engine fails to start 7. Pump on 8. Low oil pressure 9. High water temperature 10. Auto manual selector switch d) 1 sets of push button stations for the following : 1. Engine Start 2. Engine Stop 3. Engine - hooter ACK 4. Engine - fault reset e) Selector switches (Engine control, mode selector)-1 No f) Auxiliary relays / contactors / timer for sequence operating for starting and stopping of the engine - 1 set. g) Hooter for audio alarm (Industrial type) - 1 No All the components shall be housed in a common cubical made of 16 swg. M.S. sheet with required stiffeners ( if required). The panel shall be powder coated of approved color both inside & outside. The panel shall have both bottom & top cable entry provisions and panel shall be mounted on Pedestal of 300 mm height. Also panel shall have sufficient (min. 50 Nos) NO/NC contacts for extending the status( annunciation) of fire pumps to the Fire alarm panel. | 1.00 | Nos | 0.00 | 230000.00 | 230000.00 | 598750.00 | 598750.00 | 445000.00 | 445000.00 | 230000.00 | BA-PAN ENGINEERING co.
5.00 | Supplying, installation, testing & commissioning of pressure switches for Pumps including necessary wiring up to the control panel. | 3.00 | Job | 0.00 | 3200.00 | 9600.00 | 2780.00 | 8340.00 | 9500.00 | 28500.00 | 8340.00 | SHIMMER ENTERPRISE
6.00 | Supply of 2.5 Sq.mm X 12C FRLSHS PVC insulated flexible cable (control cable) having copper conductor including making end termination etc. complete as required. | 25.00 | Mtr | 0.00 | 500.00 | 12500.00 | 850.00 | 21250.00 | 740.00 | 18500.00 | 12500.00 | BA-PAN ENGINEERING co.
7.00 | Gl earth plate electrode: Earthing with G.I. Earth Plate 600mm x 60mm x 6mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal or coke and salt) complete as required. | 2.00 | Set | 0.00 | 13000.00 | 26000.00 | 58500.00 | 117000.00 | 10800.00 | 21600.00 | 21600.00 | GVD ENGINEERS & CONTRACTOR
8.00 | Providing and fixing 25 mm x 5 mm G.I. strip in 40 mm dia. G.I. pipe from earth electrode etc. Complete as required. | 25.00 | Mtr | 0.00 | 500.00 | 12500.00 | 1755.00 | 43875.00 | 925.00 | 23125.00 | 12500.00 | BA-PAN ENGINEERING co.
9.00 | Supplying and laying 25mm x 5mm G.I. Strip at 0.50 m below ground level as strip earth electrode, including soldering etc. as required. | 20.00 | Mtr | 0.00 | 220.00 | 4400.00 | 280.00 | 5600.00 | 210.00 | 4200.00 | 4200.00 | GVD ENGINEERS & CONTRACTOR
10.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. complete as required. | 20.00 | Mtr | 0.00 | 121.00 | 2420.00 | 240.00 | 4800.00 | 170.00 | 3400.00 | 2420.00 | BA-PAN ENGINEERING co.
11.00 | Supplying and laying 6SWG G.I. wire at 0.50 m below ground level for conductor earth electrode, including soldering etc. (but without charcoal or coke and salt) complete as required. | 60.00 | Mtr | 0.00 | 40.00 | 2400.00 | 75.00 | 4500.00 | 48.00 | 2880.00 | 2400.00 | BA-PAN ENGINEERING co.
12.00 | Supplying and installation of Fire Pressure vessel of 450mm dia and 1m high fabricated from 10mm thick M.S. Plate suitable for 10kg/sq.cm. working pressure with accessories, painted with two coats of- Postal Red Enamel outside over a coat of primer and Epoxy Paint inside for automatic operation of Pump. | 1.00 | Nos | 0.00 | 31000.00 | 31000.00 | 42750.00 | 42750.00 | 43500.00 | 43500.00 | 31000.00 | BA-PAN ENGINEERING co.
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 50 Sq.mm x 3.0 Core | 4.00 | Set | 0.00 | 500.00 | 2000.00 | 1240.00 | 4960.00 | 1850.00 | 7400.00 | 2000.00 | BA-PAN ENGINEERING co.
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 16 Sq.mm x 3.0 Core | 2.00 | Set | 0.00 | 400.00 | 800.00 | 875.00 | 1750.00 | 900.00 | 1800.00 | 800.00 | BA-PAN ENGINEERING co.
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable / control cable of 1.1 KV grade of following size in the existing HDPE/ METAL pipe as required. Upto 35 sq. mm | 6.00 | Mtr | 0.00 | 220.00 | 1320.00 | 580.00 | 3480.00 | 75.00 | 450.00 | 450.00 | GVD ENGINEERS & CONTRACTOR
16.00 | Supplying and making end termination with copper lugs for 2.5 Sq.mm x 12.0 Core size of PVC insulated control cable of 1.1 KV grade as required. 2.5 Sq.mm x 12.0 Core | 2.00 | Set | 0.00 | 500.00 | 1000.00 | 290.00 | 580.00 | 850.00 | 1700.00 | 580.00 | SHIMMER ENTERPRISE
17.00 | Providing, laying, testing and commissioning of 150mm dia 'C' class heavy duty MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. | 160.00 | Mtr | 0.00 | 2002.00 | 320320.00 | 2650.00 | 424000.00 | 2750.00 | 440000.00 | 320320.00 | BA-PAN ENGINEERING co.
18.00 | Providing, laying, testing and commissioning of 100mm dia 'C' class heavy duty MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. | 100.00 | Mtr | 0.00 | 1400.00 | 140000.00 | 2017.00 | 201700.00 | 2150.00 | 215000.00 | 140000.00 | BA-PAN ENGINEERING co.
19.00 | Providing, laying, testing and commissioning of 80mm dia 'C' class heavy duty MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. | 18.00 | Mtr | 0.00 | 1120.00 | 20160.00 | 1742.00 | 31356.00 | 1580.00 | 28440.00 | 20160.00 | BA-PAN ENGINEERING co.
20.00 | Providing, laying, testing and commissioning of 150mm dia 'C' class heavy duty MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows and fixing the pipe below the ground shall be treated with anti-corrosive wrapping & coating of "Pypkote" make as per detailed specification complete as required. | 20.00 | Mtr | 0.00 | 2200.00 | 44000.00 | 3149.00 | 62980.00 | 3200.00 | 64000.00 | 44000.00 | BA-PAN ENGINEERING co.
21.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze / gunmetal seat duly ISI marked complete with flanges, nuts, bolts, washers, gaskets conforming to IS 13095 of 150mm dia sizes as required. | 2.00 | Nos | 0.00 | 8000.00 | 16000.00 | 9822.00 | 19644.00 | 12500.00 | 25000.00 | 16000.00 | BA-PAN ENGINEERING co.
22.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze / gunmetal seat duly ISI marked complete with flanges, nuts, bolts, washers, gaskets conforming to IS 13095 of 80mm dia sizes as required. | 18.00 | Nos | 0.00 | 5000.00 | 90000.00 | 5484.00 | 98712.00 | 8150.00 | 146700.00 | 90000.00 | BA-PAN ENGINEERING co.
23.00 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with flanges, nuts, bolts, washers, gaskets and conforming to IS 780 of 150mm dia sizes as required | 4.00 | Nos | 0.00 | 22000.00 | 88000.00 | 37500.00 | 150000.00 | 21000.00 | 84000.00 | 84000.00 | GVD ENGINEERS & CONTRACTOR
24.00 | Supply, installation, testing and commissioning of non-return valve of 150mm dia sizes confirming to IS: 5312 complete with flanges, rubber gasket, GI bolts, nuts, washers etc.as required | 2.00 | Nos | 0.00 | 13000.00 | 26000.00 | 32000.00 | 64000.00 | 22500.00 | 45000.00 | 26000.00 | BA-PAN ENGINEERING co.
25.00 | Supply, installation, testing and commissioning of non-return valve of 100mm dia sizes confirming to IS: 5312 complete with flanges, rubber gasket, GI bolts, nuts, washers etc.as required | 4.00 | Nos | 0.00 | 13000.00 | 52000.00 | 21768.00 | 87072.00 | 18500.00 | 74000.00 | 52000.00 | BA-PAN ENGINEERING co.
26.00 | Supply, installation, testing and commissioning of foot valve of 150mm dia sizes confirming to IS: 5312 complete with flanges, rubber gasket, GI bolts, nuts, washers etc.as required | 1.00 | Nos | 0.00 | 22000.00 | 22000.00 | 19800.00 | 19800.00 | 16500.00 | 16500.00 | 16500.00 | GVD ENGINEERS & CONTRACTOR
27.00 | Supply,Installation,Testing & Commissioning of Forged brass Ball Valve cast iron body with ISI mark of 25 mm size complete as required and as specified. | 3.00 | Nos | 0.00 | 2200.00 | 6600.00 | 1450.00 | 4350.00 | 2200.00 | 6600.00 | 4350.00 | SHIMMER ENTERPRISE
28.00 | Supply,Installation,Testing & Commissioning of pressure switch having 1/4" BSP (F) connection IP:32 enclosure protection, pressure rage 0 to 200 psi with necessary contact complete as required and as specified. | 3.00 | Nos | 0.00 | 2200.00 | 6600.00 | 3780.00 | 11340.00 | 3200.00 | 9600.00 | 6600.00 | BA-PAN ENGINEERING co.
29.00 | Supply,Installation,Testing & Commissioning of pressure guage 4 " dial , 0 - 225 psi range Bottom SS Case SS Internal with Gly fill complete as required and as specified. | 3.00 | Nos | 0.00 | 1300.00 | 3900.00 | 2170.00 | 6510.00 | 3300.00 | 9900.00 | 3900.00 | BA-PAN ENGINEERING co.
30.00 | Supply,Installation,Testing & Commissioning of 4 way Pumping in Breech (Fire Brigade Inlet / Siamese Connection) 4 way having 4 nos. 63mm Male Inst. Inlet with built in NRV & 150 mm NB flanged outlet with 1” drain valve & Rubber Dust Caps complete as required. | 4.00 | Nos | 0.00 | 13000.00 | 52000.00 | 16500.00 | 66000.00 | 35000.00 | 140000.00 | 52000.00 | BA-PAN ENGINEERING co.
31.00 | Supply,Installation,Testing & Commissioning of Air release valve SS body 25 mm dia. complete as required. | 1.00 | Nos | 0.00 | 4000.00 | 4000.00 | 2749.00 | 2749.00 | 5500.00 | 5500.00 | 2749.00 | SHIMMER ENTERPRISE
32.00 | Supply,Installation,Testing & Commissioning of cylindrical Air Vessel tank of 2000 mm x 600 mm size, of thickness 8 mm M.S. sheet, 10 mm thick dish ends complete with air release valve, safety valve, pressure gauge, etc. complete as required and as specified. | 1.00 | Nos | 0.00 | 40000.00 | 40000.00 | 72000.00 | 72000.00 | 75000.00 | 75000.00 | 40000.00 | BA-PAN ENGINEERING co.
33.00 | Supply,Installation,Testing & Commissioning of 150 mm CI Strainer For safer operation of pump. complete as required. | 3.00 | Nos | 0.00 | 13000.00 | 39000.00 | 29847.00 | 89541.00 | 21500.00 | 64500.00 | 39000.00 | BA-PAN ENGINEERING co.
34.00 | Supply, installation, testing and commissioning of Yard Hydrants comprising with 80 mm dia. MS bend & 80 mm dia MS stand pipe (1 mtr above ground) of the following: (a) 80mm dia pipe fitted with single headed 63mm dia landing valve as per design. (b) Providing 2nos 15mts long 63mm dia CP hose with gun metal male and female instantaneous Coupling. (c) 63mm dia branch pipe with gun metal hexogonal detachable nozzle made of instantaneous coupling. (d) Two keys in recess type compartment for break glass. (e) Hose cabinet to accomodate two sets of controled percolating hose of 15mt length with 1 pair of male and female coupling and 1 branch pipe with nozzle. The cabinet is made of MS sheet of 14 SWG/2 mm thick, with a double door , glass font (4mm thick) with hinged door and lock. The cabinet is painted to scarlet red colour size 30"x10"x24" & wall / floor mounted. | 14.00 | Job | 0.00 | 50000.00 | 700000.00 | 42750.00 | 598500.00 | 45000.00 | 630000.00 | 598500.00 | SHIMMER ENTERPRISE
35.00 | Supplying, erecting & commissioning Fire Hose cabinet comprising of internal hydrant. a) 63mm dia instantaneous pattern single headed oblique hydrant valve with gun metal cap, GI chain twist release type plug. b) 2 lengths of 15mtrs. 63mm dia reinforced rubber lined hose with instantaneous male and female coupling. c) 1 no gun metal branch pipe with nozzle (63mm x 20mm) with Gunmetal gate/ ball valve (20mm) d) Two keys in recess type compartment for break glass. e) 19mm dia. Reinforced hose reel 30m length as per IS 5132 fitted with 6.35mm dia nozzle and shut off valve (IS 884 - 1969) . The hose reel shall be recessed swing type with reel 180 Degree drum.The hose shall be provided with coupling as per detailed specifications. f) The Frame shall comprise of 800 mm wide x 150 mm deep x 1200mm high made of 14 guage 'MS sheet to house the above accessories. The cabinet shall be firmly fixed to the wall / floor mounted with expansion bolts. The cabinet shall be powder coated both internally and externally. The door shall be provided with suitable locking arrangement as per standards.The quote shall include fixing the cabinet to the wall / floor mounted & making good to the wall / floor. | 4.00 | Job | 0.00 | 50000.00 | 200000.00 | 64000.00 | 256000.00 | 55000.00 | 220000.00 | 200000.00 | BA-PAN ENGINEERING co.
36.00 | Supplying, installing and commissioning of fire brigade inlet connection conforming to IS 5290 comprising of 4nos. 63mm dia instantaneous couplings complete, CI butterfly valve, connected to 100/150mm dia Fire hydrant ring main and fire hydrant wet riser pipe. | 2.00 | Nos | 0.00 | 13000.00 | 26000.00 | 37000.00 | 74000.00 | 32000.00 | 64000.00 | 26000.00 | BA-PAN ENGINEERING co.
37.00 | Cutting of road /bituminous /concrete pavement etc.at a depth of minimum 300 mm including supply and laying of 150mm dia 'C' class heavy duty MS pipe, making the damages good etc. complete as required. | 20.00 | Mtr | 0.00 | 3100.00 | 62000.00 | 5475.00 | 109500.00 | 2650.00 | 53000.00 | 53000.00 | GVD ENGINEERS & CONTRACTOR
38.00 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type Pendent sprinklers of rating 68 degree centigrade with required accessories. | 85.00 | Nos. | 0.00 | 450.00 | 38250.00 | 395.00 | 33575.00 | 1350.00 | 114750.00 | 33575.00 | SHIMMER ENTERPRISE
39.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 25 mm dia | 60.00 | Mtrs | 0.00 | 500.00 | 30000.00 | 474.00 | 28440.00 | 975.00 | 58500.00 | 28440.00 | SHIMMER ENTERPRISE
40.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 32 mm dia | 60.00 | Mtrs | 0.00 | 800.00 | 48000.00 | 782.00 | 46920.00 | 1380.00 | 82800.00 | 46920.00 | SHIMMER ENTERPRISE
41.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 40 mm dia | 60.00 | Mtrs | 0.00 | 900.00 | 54000.00 | 917.00 | 55020.00 | 1550.00 | 93000.00 | 54000.00 | BA-PAN ENGINEERING co.
42.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 50 mm dia | 30.00 | Mtrs | 0.00 | 1100.00 | 33000.00 | 1294.00 | 38820.00 | 1715.00 | 51450.00 | 33000.00 | BA-PAN ENGINEERING co.
43.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 65 mm dia | 25.00 | Mtrs | 0.00 | 1300.00 | 32500.00 | 1394.00 | 34850.00 | 1900.00 | 47500.00 | 32500.00 | BA-PAN ENGINEERING co.
44.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including jointing as per specification, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 80 mm dia | 40.00 | Mtrs | 0.00 | 1400.00 | 56000.00 | 8792.00 | 351680.00 | 2100.00 | 84000.00 | 56000.00 | BA-PAN ENGINEERING co.
45.00 | Supply & Making suitable RCC foundation base for installation of new pump set of 1:3:6 grade having approx size 4ft x 2.5ft x 0.5 ft after making suitable RCC underground foundation complete as required. 50 HP Fire Fighting Pump Motor Set | 2.00 | Job | 0.00 | 13000.00 | 26000.00 | 45000.00 | 90000.00 | 12500.00 | 25000.00 | 25000.00 | GVD ENGINEERS & CONTRACTOR
46.00 | FIRE EXTINGUISHERS: Supply Installation,Testing & Commissioning of DCP type fire extinguisher of capacity 9 Kg complete as required. | 25.00 | Nos | 0.00 | 4500.00 | 112500.00 | 3988.00 | 99700.00 | 4800.00 | 120000.00 | 99700.00 | SHIMMER ENTERPRISE
47.00 | Supply Installation,Testing & Commissioning of Water type fire extinguisher of capacity 9 Ltr complete as required. | 15.00 | Nos | 0.00 | 2200.00 | 33000.00 | 3600.00 | 54000.00 | 4500.00 | 67500.00 | 33000.00 | BA-PAN ENGINEERING co.
48.00 | Supply Installation,Testing & Commissioning of Co2 type fire extinguisher of capacity 4.5 Kg including horn & hose Pipe complete as required. | 20.00 | Nos | 0.00 | 13000.00 | 260000.00 | 6200.00 | 124000.00 | 5500.00 | 110000.00 | 110000.00 | GVD ENGINEERS & CONTRACTOR
49.00 | Supply Installation,Testing & Commissioning of Co2 type fire extinguisher of capacity 9.0 Kg including horn & hose Pipe complete as required. | 25.00 | Nos | 0.00 | 14000.00 | 350000.00 | 13450.00 | 336250.00 | 10800.00 | 270000.00 | 270000.00 | GVD ENGINEERS & CONTRACTOR
50.00 | Supply Installation,Testing & Commissioning of Co2 type fire extinguisher of capacity 22.5 Kg including horn & hose Pipe complete as required. | 4.00 | Nos | 0.00 | 23000.00 | 92000.00 | 24000.00 | 96000.00 | 21500.00 | 86000.00 | 86000.00 | GVD ENGINEERS & CONTRACTOR
51.00 | Supply Installation,Testing & Commissioning of AFFF type fire extinguisher of capacity 9.0 Ltr complete as required. | 10.00 | Nos | 0.00 | 4000.00 | 40000.00 | 3150.00 | 31500.00 | 8500.00 | 85000.00 | 31500.00 | SHIMMER ENTERPRISE
52.00 | Dismantling the existing multistage centrifugal motor pump set from the foundation alongwith related accessories and transporting the same from operational area to AAI store around 1 KM (Approx) complete as required. 50 HP Fire Fighting Pump Motor Set | 2.00 | Job | 0.00 | 5000.00 | 10000.00 | 15000.00 | 30000.00 | 12000.00 | 24000.00 | 10000.00 | BA-PAN ENGINEERING co.
53.00 | Dismantling the existing Centrifugal Pump set from the foundation alongwith related accessories and transporting the same from operational area to AAI store around 1 KM (Approx) complete as required. 7.5 HP Jockey Pump Set | 1.00 | Job | 0.00 | 4000.00 | 4000.00 | 7600.00 | 7600.00 | 5000.00 | 5000.00 | 4000.00 | BA-PAN ENGINEERING co.
54.00 | Dismantling of existing 'C' class heavy duty 80 mm MS pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc complete as required. | 150.00 | Mtr | 0.00 | 220.00 | 33000.00 | 500.00 | 75000.00 | 270.00 | 40500.00 | 33000.00 | BA-PAN ENGINEERING co.
55.00 | Dismantling of existing 'C' class heavy duty 100 mm MS pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc complete as required. | 100.00 | Mtr | 0.00 | 230.00 | 23000.00 | 600.00 | 60000.00 | 310.00 | 31000.00 | 23000.00 | BA-PAN ENGINEERING co.
56.00 | Dismantling of LT panel of size (2.2x2.15x.6 mtr) from its existing location & transporting the same from operational area to AAI store around 1 KM (Approx) etc complete as per site requirement. | 1.00 | Job | 0.00 | 4000.00 | 4000.00 | 5000.00 | 5000.00 | 8000.00 | 8000.00 | 4000.00 | BA-PAN ENGINEERING co.
57.00 | Re-fixing of 'C' class heavy duty 80 mm MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc complete as required. | 150.00 | Mtr | 0.00 | 400.00 | 60000.00 | 700.00 | 105000.00 | 425.00 | 63750.00 | 60000.00 | BA-PAN ENGINEERING co.
58.00 | Re-fixing of 'C' class heavy duty 100 mm MS pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, dummy, bend, tapers, nuts bolts, gaskets etc complete as required. | 100.00 | Mtr | 0.00 | 500.00 | 50000.00 | 900.00 | 90000.00 | 545.00 | 54500.00 | 50000.00 | BA-PAN ENGINEERING co.
59.00 | Dismantling the existing Internal / External MS Hose cabinet of following size : 1.5M x 1.0M x 0.75 M / 0.91M x 0.61M x 0.50M / 1.0M x 0.61M x 0.46M i/c removing of old butterfly valve, hoses, branch pipes connection etc. and transporting the same from operational area to AAI store around 1 KM (Approx) with proper dismantle record registered and submitted to E.I.C complete as required. | 10.00 | Job | 0.00 | 4000.00 | 40000.00 | 4500.00 | 45000.00 | 6000.00 | 60000.00 | 40000.00 | BA-PAN ENGINEERING co.
60.00 | SH: II - CIVIL WORK CONSTRUCTION OF FIRE TANK, RENOVATION AND ASSOCIATED WORKS Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and for all lift, as directed by Engineer-incharge. (a) All kinds of soil | 232.00 | Cum | 0.00 | 400.00 | 92800.00 | 405.00 | 93960.00 | 350.00 | 81200.00 | 81200.00 | GVD ENGINEERS & CONTRACTOR
61.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, for all lift, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. (a) All kinds of soil. | 14.50 | Cum | 0.00 | 500.00 | 7250.00 | 390.00 | 5655.00 | 560.00 | 8120.00 | 5655.00 | SHIMMER ENTERPRISE
62.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 and for all lift. | 75.00 | Cum | 0.00 | 400.00 | 30000.00 | 225.00 | 16875.00 | 250.00 | 18750.00 | 16875.00 | SHIMMER ENTERPRISE
63.00 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. (a) All kinds of soil. | 58.00 | Cum | 0.00 | 400.00 | 23200.00 | 220.00 | 12760.00 | 150.00 | 8700.00 | 8700.00 | GVD ENGINEERS & CONTRACTOR
64.00 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | 4.00 | Cum | 0.00 | 4000.00 | 16000.00 | 4500.00 | 18000.00 | 2200.00 | 8800.00 | 8800.00 | GVD ENGINEERS & CONTRACTOR
65.00 | Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. All kinds of soil. | 80.00 | Sqm | 0.00 | 230.00 | 18400.00 | 450.00 | 36000.00 | 120.00 | 9600.00 | 9600.00 | GVD ENGINEERS & CONTRACTOR
66.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level: (a) 1:2:4 (1 cement : 2 coarse sand (zone-II) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources). | 2.00 | Cum | 0.00 | 13000.00 | 26000.00 | 10200.00 | 20400.00 | 9500.00 | 19000.00 | 19000.00 | GVD ENGINEERS & CONTRACTOR
67.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : (a) 1:4:8 (1 Cement : 4 coarse sand (zone-II) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources). | 15.00 | Cum | 0.00 | 13000.00 | 195000.00 | 7175.00 | 107625.00 | 7500.00 | 112500.00 | 107625.00 | SHIMMER ENTERPRISE
68.00 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-II) derived from natural sources : 4 graded stone aggregate 12.5 mm nominal size derived from natural sources). | 2.50 | Sqm | 0.00 | 400.00 | 1000.00 | 2400.00 | 6000.00 | 2200.00 | 5500.00 | 1000.00 | BA-PAN ENGINEERING co.
69.00 | Extra for providing and mixing water proofing material in cement concrete work in doses by weight of cement as per manufacturer’s specification. | 320.00 | Per bag of 50 kg cement | 0.00 | 230.00 | 73600.00 | 378.00 | 120960.00 | 375.00 | 120000.00 | 73600.00 | BA-PAN ENGINEERING co.
70.00 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-II) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. | 43.00 | Sqm | 0.00 | 500.00 | 21500.00 | 900.00 | 38700.00 | 870.00 | 37410.00 | 21500.00 | BA-PAN ENGINEERING co.
71.00 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement: (a) 1:1.5:3 (1 cement : 1.5 coarse sand(zone-II) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 1.00 | Cum | 0.00 | 13000.00 | 13000.00 | 14000.00 | 14000.00 | 13000.00 | 13000.00 | 13000.00 | BA-PAN ENGINEERING co., GVD ENGINEERS & CONTRACTOR
72.00 | Centering and shuttering including strutting, propping etc. and removal of form for: (a) Foundations, footings, bases of columns, etc. for mass concrete. | 323.00 | Sqm | 0.00 | 1400.00 | 452200.00 | 417.00 | 134691.00 | 560.00 | 180880.00 | 134691.00 | SHIMMER ENTERPRISE
73.00 | Centering and shuttering including strutting, ropping etc. and removal of form for: (b) Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 313.00 | Sqm | 0.00 | 1400.00 | 438200.00 | 728.00 | 227864.00 | 670.00 | 209710.00 | 209710.00 | GVD ENGINEERS & CONTRACTOR
74.00 | Centering and shuttering including strutting, propping etc. and removal of form for: Lintels, beams, plinth beams, girders, bressumers and cantilevers. | 3.00 | Sqm | 0.00 | 1400.00 | 4200.00 | 900.00 | 2700.00 | 1200.00 | 3600.00 | 2700.00 | SHIMMER ENTERPRISE
75.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. (a) Thermo-Mechanically Treated bars of grade Fe-500D or more. | 3045.00 | Kg | 0.00 | 130.00 | 395850.00 | 101.00 | 307545.00 | 122.00 | 371490.00 | 307545.00 | SHIMMER ENTERPRISE
76.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. (i) All works upto plinth level (a) Concrete of M25 grade with minimum cement content of 330 kg /cum. | 48.00 | Cum | 0.00 | 13000.00 | 624000.00 | 10500.00 | 504000.00 | 14000.00 | 672000.00 | 504000.00 | SHIMMER ENTERPRISE
77.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: (a) Cement mortar 1:6 (1 cement : 6 coarse sand). | 5.00 | Cum | 0.00 | 9000.00 | 45000.00 | 11800.00 | 59000.00 | 7500.00 | 37500.00 | 37500.00 | GVD ENGINEERS & CONTRACTOR
78.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in: (a) Cement mortar 1:6 (1 cement : 6 coarse sand) | 6.00 | Cum | 0.00 | 9000.00 | 54000.00 | 14500.00 | 87000.00 | 8800.00 | 52800.00 | 52800.00 | GVD ENGINEERS & CONTRACTOR
79.00 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) nondecorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters: (a) 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws. | 5.10 | Sqm | 0.00 | 4000.00 | 20400.00 | 4300.00 | 21930.00 | 6200.00 | 31620.00 | 20400.00 | BA-PAN ENGINEERING co.
80.00 | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete: (a) 300 x 16 mm. | 2.00 | Each | 0.00 | 5000.00 | 10000.00 | 550.00 | 1100.00 | 12500.00 | 25000.00 | 1100.00 | SHIMMER ENTERPRISE
81.00 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete: (a) 300 x 10 mm | 2.00 | Each | 0.00 | 230.00 | 460.00 | 375.00 | 750.00 | 550.00 | 1100.00 | 460.00 | BA-PAN ENGINEERING co.
82.00 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete: (a) 125 mm. | 2.00 | Each | 0.00 | 230.00 | 460.00 | 175.00 | 350.00 | 520.00 | 1040.00 | 350.00 | SHIMMER ENTERPRISE
83.00 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. (a) Single Rubber Stopper. | 2.00 | Each | 0.00 | 250.00 | 500.00 | 128.00 | 256.00 | 450.00 | 900.00 | 256.00 | SHIMMER ENTERPRISE
84.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 200.00 | Kg | 0.00 | 140.00 | 28000.00 | 130.00 | 26000.00 | 210.00 | 42000.00 | 26000.00 | SHIMMER ENTERPRISE
85.00 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolledsteel sections, joints mitred and flash butt welded and sash bars tenoned and riveted,including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment) Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | 40.00 | Kg | 0.00 | 230.00 | 9200.00 | 295.00 | 11800.00 | 250.00 | 10000.00 | 9200.00 | BA-PAN ENGINEERING co.
86.00 | Providing and fixing bolts including nuts and washers complete. | 20.00 | Kg | 0.00 | 230.00 | 4600.00 | 194.00 | 3880.00 | 130.00 | 2600.00 | 2600.00 | GVD ENGINEERS & CONTRACTOR
87.00 | 62 mm thick cement concrete flooring with concrete hardener topping, under layer 50 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) and top layer 12mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate, 6mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacture’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete. | 30.00 | Sqm | 0.00 | 2300.00 | 69000.00 | 1472.00 | 44160.00 | 3200.00 | 96000.00 | 44160.00 | SHIMMER ENTERPRISE
88.00 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. 110 mm diameter. | 16.00 | Mtr. | 0.00 | 400.00 | 6400.00 | 714.00 | 11424.00 | 480.00 | 7680.00 | 6400.00 | BA-PAN ENGINEERING co.
89.00 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50mm (base metal of minimum 0.45mm thickness with total coating thickness of 0.05 mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5 x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | 10.00 | Sqm | 0.00 | 2300.00 | 23000.00 | 1155.00 | 11550.00 | 1800.00 | 18000.00 | 11550.00 | SHIMMER ENTERPRISE
90.00 | Providing and fixing precoated galvanised steel sheet roofing accessories of total coated thickness 0.50mm (base metal of minimum 0.45mm thickness with total coating thickness of 0.05 mm) with Zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete: (a) Gutter (600 mm over all girth). | 6.00 | Mtr. | 0.00 | 2300.00 | 13800.00 | 1775.00 | 10650.00 | 1400.00 | 8400.00 | 8400.00 | GVD ENGINEERS & CONTRACTOR
91.00 | 12 mm cement plaster of mix: (a) 1:6 (1 cement: 6 fine sand). | 290.00 | Sqm | 0.00 | 400.00 | 116000.00 | 415.00 | 120350.00 | 380.00 | 110200.00 | 110200.00 | GVD ENGINEERS & CONTRACTOR
92.00 | 15 mm cement plaster on the rough side of single or half brick wall of mix: 1:6 (1 cement: 6 fine sand). | 114.00 | Sqm | 0.00 | 500.00 | 57000.00 | 472.00 | 53808.00 | 285.00 | 32490.00 | 32490.00 | GVD ENGINEERS & CONTRACTOR
93.00 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade: (a) New work (Two or more coats applied @ 1.43 ltr/10 sqm over and including priming coat of exterior primer applied @ 0.90 litre/10 sqm). | 114.00 | Sqm | 0.00 | 230.00 | 26220.00 | 398.00 | 45372.00 | 240.00 | 27360.00 | 26220.00 | BA-PAN ENGINEERING co.
94.00 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade :Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture | 10.00 | Sqm | 0.00 | 230.00 | 2300.00 | 342.00 | 3420.00 | 210.00 | 2100.00 | 2100.00 | GVD ENGINEERS & CONTRACTOR
95.00 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 114.00 | Sqm | 0.00 | 50.00 | 5700.00 | 328.00 | 37392.00 | 150.00 | 17100.00 | 5700.00 | BA-PAN ENGINEERING co.
96.00 | Wall painting with acrylic emulsion paint, having VOC (Volatile Organic Compound) content less than 50 grams/ litre, of approved brand and manufacture, including applying additional coats wherever required, to achieve even shade and colour. (a) Two coats. | 114.00 | Sqm | 0.00 | 140.00 | 15960.00 | 327.00 | 37278.00 | 280.00 | 31920.00 | 15960.00 | BA-PAN ENGINEERING co.
97.00 | Hacking of CC flooring including cleaning for surface etc. complete as per direction of the Engineer-in-Charge. | 26.00 | Sqm | 0.00 | 40.00 | 1040.00 | 295.00 | 7670.00 | 210.00 | 5460.00 | 1040.00 | BA-PAN ENGINEERING co.
98.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer-in-charge. (a) Nominal concrete 1:3:6 or richer mix (including equivalent design mix). | 3.10 | Cum | 0.00 | 2300.00 | 7130.00 | 750.00 | 2325.00 | 1200.00 | 3720.00 | 2325.00 | SHIMMER ENTERPRISE
99.00 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. (a) In cement mortar. | 1.00 | Cum | 0.00 | 2300.00 | 2300.00 | 890.00 | 890.00 | 980.00 | 980.00 | 890.00 | SHIMMER ENTERPRISE
100.00 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead: (a) Of area 3 sq. metres and below. | 3.00 | Each | 0.00 | 2300.00 | 6900.00 | 500.00 | 1500.00 | 450.00 | 1350.00 | 1350.00 | GVD ENGINEERS & CONTRACTOR
101.00 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. | 178.00 | Sqm | 0.00 | 2300.00 | 409400.00 | 100.00 | 17800.00 | 195.00 | 34710.00 | 17800.00 | SHIMMER ENTERPRISE
102.00 | Providing and laying factory made chamfered edge Cement Concrete paver blocks in footpath, parks, lawns, drive ways or light traffic parking etc, of required strength, thickness & size/ shape, made by table vibratory method using PU mould, laid in required colour & pattern over 50 mm thick compacted bed of sand, compacting and proper embedding/laying of inter locking paver blocks into the sand bedding layer through vibratory compaction by using plate vibrator, filling the joints with sand and cutting of paver blocks as per required size and pattern, finishing and sweeping extra sand. complete all as per direction of Engineer-in-Charge. (a) 80 mm thick C.C. paver block of M-35 grade with approved colour design and pattern. | 70.00 | Sqm | 0.00 | 500.00 | 35000.00 | 1490.00 | 104300.00 | 1450.00 | 101500.00 | 35000.00 | BA-PAN ENGINEERING co.
103.00 | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, including cutting and making good the walls etc. Internal work - Exposed on wall. | 50.00 | Mtr. | 0.00 | 400.00 | 20000.00 | 1150.00 | 57500.00 | 650.00 | 32500.00 | 20000.00 | BA-PAN ENGINEERING co.
104.00 | Making connection of G.I. distribution branch with G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete: (a) 50 to 80 mm nominal bore. | 2.00 | Each | 0.00 | 400.00 | 800.00 | 600.00 | 1200.00 | 2800.00 | 5600.00 | 800.00 | BA-PAN ENGINEERING co.
105.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end): (a) 50 mm nominal bore. | 3.00 | Each | 0.00 | 2500.00 | 7500.00 | 3500.00 | 10500.00 | 4750.00 | 14250.00 | 7500.00 | BA-PAN ENGINEERING co.
106.00 | Providing and fixing G.I. Union in G.I. pipe including cutting and threading the pipe and making long screws etc. complete (New work): (a) 50 mm nominal bore. | 7.00 | Each | 0.00 | 500.00 | 3500.00 | 250.00 | 1750.00 | 1450.00 | 10150.00 | 1750.00 | SHIMMER ENTERPRISE
| Total in Figures |  |  |  |  | 9057540.00 |  | 9500007.00 |  | 9297335.00
Lowest Amount Quoted BY: BA-PAN ENGINEERING co.(9057540.00)

## BOQ Summary
BOQ Summary Details Tender Title: Renovation of Fire Fighting System in Existing Terminal Building at Silchar Airport Tender ID: 2024_AAI_204904_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BA-PAN ENGINEERING co. (BID ID -747802) | 9057540.00 | L1
| 2 | GVD ENGINEERS & CONTRACTOR (BID ID -753734) | 9297335.00 | L2
| 3 | SHIMMER ENTERPRISE (BID ID -753742) | 9500007.00 | L3