## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 01-Oct-2024 05:04 PM Tender Title: Miscellaneous / unforeseen capital Electrical works. SH - Execution of Miscellaneous Electrical Works in Power House, Fire Station and Operational Area at Dibrugarh Airport Tender ID: 2024_AAI_205401_1
Tender Inviting Authority: Airports Authority of india, Dibrugarh Airport
Name of Work: Miscellaneous / unforeseen capital Electrical works. SH : Execution of Miscellaneous Electrical Works in Power House, Fire Station and Operational Area at Dibrugarh Airport
Contract No: 2024_AAI_205401_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SAHA COMMERCIAL CONSTRUCTION (GSTN-19AASFS6288A1ZN) BID ID -743172 |  | SHARMA TRADE AGENCY (GSTN-18ABDFM0295M2ZV) BID ID -744715 |  | Aditya Techno Products Private Limited (GSTN-09AAGCA0910L1ZS) BID ID -744743 |  | MANKHA ELECTROTECH PRIVATE LIMITED (GSTN-NA) BID ID -744632
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Execution of items of schedule of rates CPWD DSR-2022 as per site condition and per direction of E-I-C at different locations in operational area/OTB/Power House/CCR/Firestation/Hangar and other locations. The bidder shall quote the rate for 01 (one) job corresponding to the value of Rs.10,00,000/- (Ex.GST) in INR only and percentage (%) above / below shall be calculated by AAI and paid accordingly. Note: The rate provided in DSR 2022 is inclusive of GST, however the contractor has to quote the amount in rate column, excluding GST, the payment shall be made to contractor as mentioned in special conditions of tender document. | 1.00 | Job | 10.00 | 700000.00 | 700000.00 | 1100000.00 | 1100000.00 | 1250000.00 | 1250000.00 | 960000.00 | 960000.00 | 700000.00 | SAHA COMMERCIAL CONSTRUCTION
2.00 | Supply and fixing of CPRI tested, ISI marked, Class A Electrical insulation mat having minimum thickness of 2mm for working voltage upto 3.3kV, confirming to IS: 15652:2006, infront of LT panels fixing using suitable adhesive material as per recommendation of manufacturer and as per direction of E-I-C. | 150.00 | Sqmtr | 10.00 | 600.00 | 90000.00 | 600.00 | 90000.00 | 225.00 | 33750.00 | 330.00 | 49500.00 | 33750.00 | Aditya Techno Products Private Limited
3.00 | Supply and fixing of CPRI tested, ISI marked, Class C Electrical insulation mat having minimum thickness of 3 mm for working voltage upto 33 kV, confirming to IS: 15652:2006, infront of HT panels fixing using suitable adhesive material as per recommendation of manufacturer and as per direction of E-I-C. | 80.00 | Sqmtr | 10.00 | 850.00 | 68000.00 | 850.00 | 68000.00 | 250.00 | 20000.00 | 3840.00 | 307200.00 | 20000.00 | Aditya Techno Products Private Limited
4.00 | Spray Painting of Electrial Panels with same as existing colour with minimum two coates and finish along with marking the lines,writing the description as per direction of Engineer-In-Charge. | 70.00 | Sqmtr | 10.00 | 300.00 | 21000.00 | 170.00 | 11900.00 | 124.00 | 8680.00 | 2400.00 | 168000.00 | 8680.00 | Aditya Techno Products Private Limited
5.00 | Supply of Highbay LED luminaries having minimum lumen output of 11000 lm, system efficacy not less than 110 lumen/watt, control driver with more than 4kV surge suppressor, made up of pressure die cast aluminum alloy housing with tempered protective toughened glass fixed to the housing with SS screws, powered by built in potted, electronic LED driver, suitable to operate on single phase, 50Hz AC supply, meeting with minimum requirements specfied in the technical specification (Make : Havells, Model: FLAREULTRACA100WLED757PWBLTG or equivalent) | 50.00 | Each | 10.00 | 3400.00 | 170000.00 | 4300.00 | 215000.00 | 6000.00 | 300000.00 | 7200.00 | 360000.00 | 170000.00 | SAHA COMMERCIAL CONSTRUCTION
6.00 | Supply of LED Flood light luminaries having minimum lumen output of 11000 lm, system efficacy not less than 110 lumen/watt, control driver with more than 4kV surge suppressor, made up of pressure die cast aluminum alloy housing with tempered protective toughened glass fixed to the housing with SS screws, powered by built in potted, isolated electronic LED driver , suitable to operate on single phase, 50Hz AC supply, meeting with minimum requirements specfied in the technical specification. (Make : Havells, Model : JETALEGANZAFLS100WLED757P60DTOTG or equivalent) | 30.00 | Each | 10.00 | 3500.00 | 105000.00 | 4400.00 | 132000.00 | 6200.00 | 186000.00 | 7200.00 | 216000.00 | 105000.00 | SAHA COMMERCIAL CONSTRUCTION
7.00 | Supply of LED Flood light (Narrow Beam) luminaries having minimum lumen output of 33000 lm, system efficacy not less than 110 lumen/watt, control driver with more than 4kV surge suppressor, made up of pressure die cast aluminum alloy housing with toughened glass fixed to the housing with SS screws, powered by built in potted electronic LED driver , suitable to operate on single phase, 50Hz AC supply, meeting with minimum requirements specfied in the technical specification.(Make : Havells, Model : JETAIRISMAXFL300WLED757PNBLTG or equivalent) | 25.00 | Each | 10.00 | 10595.00 | 264875.00 | 13000.00 | 325000.00 | 15000.00 | 375000.00 | 21600.00 | 540000.00 | 264875.00 | SAHA COMMERCIAL CONSTRUCTION
8.00 | Supply of LED Flood light (Wide beam) luminaries having minimum lumen output of 33000 lm, system efficacy not less than 110 lumen/watt, control driver with more than 4kV surge suppressor, made up of pressure die cast aluminum alloy housing with toughened glass fixed to the housing with SS screws, powered by built in potted electronic LED driver , suitable to operate on single phase, 50Hz AC supply, meeting with minimum requirements specfied in the technical specification. (Make : Havells, Model : JETAIRISMAXFL300WLED757PWBLTG or equivalent) | 15.00 | Each | 10.00 | 10595.00 | 158925.00 | 13000.00 | 195000.00 | 16000.00 | 240000.00 | 21000.00 | 315000.00 | 158925.00 | SAHA COMMERCIAL CONSTRUCTION
9.00 | Installation, Testing and Commissioning of LED highbay lights/flood light fitting in power house/fire station/MT section/Highmast etc.,(Illumination levels to be submitted) | 120.00 | Each | 10.00 | 350.00 | 42000.00 | 200.00 | 24000.00 | 126.00 | 15120.00 | 330.00 | 39600.00 | 15120.00 | Aditya Techno Products Private Limited
10.00 | Providing and fixing/Retrofitting of following rating and breaking capacity and pole MCCB with thermomagnetic release and suitable necessary connecting arrangement, extended rotary handle in existing cubicle panel board including modification of bus bars(as required), modification/replacement of door to make good finish including providing R,Y,B indication lamps and painting, marking on particular cubicle, making connections, etc. as required as per site condition and as per instruction of Engineer-In-Charge
10.10 | 250 A,36KA,FP MCCB | 22.00 | Each | 10.00 | 25750.00 | 566500.00 | 14500.00 | 319000.00 | 7500.00 | 165000.00 | 15000.00 | 330000.00 | 165000.00 | Aditya Techno Products Private Limited
10.20 | 630 A,50KA,FP MCCB | 4.00 | Each | 10.00 | 45000.00 | 180000.00 | 35000.00 | 140000.00 | 31300.00 | 125200.00 | 42000.00 | 168000.00 | 125200.00 | Aditya Techno Products Private Limited
11.00 | Supply of following LED indication lamps of 22.5mm dia in cluster design working on 220-240VAC
11.10 | RED colour | 100.00 | Each | 10.00 | 103.00 | 10300.00 | 120.00 | 12000.00 | 131.00 | 13100.00 | 330.00 | 33000.00 | 10300.00 | SAHA COMMERCIAL CONSTRUCTION
11.20 | YELLOW colour | 100.00 | Each | 10.00 | 103.00 | 10300.00 | 120.00 | 12000.00 | 130.00 | 13000.00 | 330.00 | 33000.00 | 10300.00 | SAHA COMMERCIAL CONSTRUCTION
11.30 | BLUE Colour | 100.00 | Each | 10.00 | 175.00 | 17500.00 | 200.00 | 20000.00 | 200.00 | 20000.00 | 300.00 | 30000.00 | 17500.00 | SAHA COMMERCIAL CONSTRUCTION
11.40 | GREEN Colour | 100.00 | Each | 10.00 | 103.00 | 10300.00 | 120.00 | 12000.00 | 131.00 | 13100.00 | 300.00 | 30000.00 | 10300.00 | SAHA COMMERCIAL CONSTRUCTION
11.50 | AMBER Colour | 100.00 | Each | 10.00 | 175.00 | 17500.00 | 120.00 | 12000.00 | 130.00 | 13000.00 | 300.00 | 30000.00 | 12000.00 | SHARMA TRADE AGENCY
12.00 | Supply and Fixing of 450 mm , 1400 RPM heavy duty exhaust fan working on single phase 230/240V, AC Supply including motor mounting brackets, shutters, all accessories including removal of existing fan(if any), connections as required as per direction of E-I-C. | 12.00 | Each | 10.00 | 3500.00 | 42000.00 | 4000.00 | 48000.00 | 2000.00 | 24000.00 | 4200.00 | 50400.00 | 24000.00 | Aditya Techno Products Private Limited
13.00 | Supply of C.I. Isolating Transformer housing box,water tight round type,metal container of outside size 330mm height 450mm made of 10mm thick cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole centre at one side surface centre 75mm above bottom surface suitable to receive one of 50mm dia "B" class GI pipe(Double Hole type) and including check nuts as required and another hole at 175mm from the bottom of the CI Box to receive one no. 15mm dia "B" class GI pipe and check nut as required.The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts as required as per the drawings. | 95.00 | Each | 10.00 | 6750.00 | 641250.00 | 6000.00 | 570000.00 | 5500.00 | 522500.00 | 3300.00 | 313500.00 | 313500.00 | MANKHA ELECTROTECH PRIVATE LIMITED
| Total in Figures |  |  |  |  | 3115450.00 |  | 3305900.00 |  | 3337450.00 |  | 3973200.00
Lowest Amount Quoted BY: SAHA COMMERCIAL CONSTRUCTION(3115450.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous / unforeseen capital Electrical works. SH - Execution of Miscellaneous Electrical Works in Power House, Fire Station and Operational Area at Dibrugarh Airport Tender ID: 2024_AAI_205401_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAHA COMMERCIAL CONSTRUCTION (BID ID -743172) | 3115450.00 | L1
| 2 | SHARMA TRADE AGENCY (BID ID -744715) | 3305900.00 | L2
| 3 | Aditya Techno Products Private Limited (BID ID -744743) | 3337450.00 | L3
| 4 | MANKHA ELECTROTECH PRIVATE LIMITED (BID ID -744632) | 3973200.00 | L4