## BoQ1
Government eProcurement System Created By: Jyoti Prakash chauhan Created Date/Time: 29-Oct-2024 12:56 PM Tender Title: Replacement of existing LT Panels of residential colony and allied works at CATC Prayagraj Tender ID: 2024_AAI_209020_1
Tender Inviting Authority: Asstt. General Manager (Engg.-Electrical), AAI, CATC, Prayagraj
Name of Work: Replacement of existing LT Panels of residential colony and allied works at CATC Prayagraj.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Avion industries (GSTN-09AFZPJ4337F1ZZ) BID ID -758702 |  | DEEPAKELECTRICALS (GSTN-33ALUPD3531C1ZI) BID ID -759113 |  | Genesis (GSTN-09AGAPJ4118N1ZA) BID ID -760000 |  | MANNA ELECTRONICS AND ELECTRICAL WORKS (GSTN-19AALFM9363P2Z6) BID ID -760055 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -760299 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -759707 |  | Shiva Enterprises (GSTN-NA) BID ID -760165
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | LT Panel Colony Sub-station
2.00 | Design, manufacture supply, installation, testing and commissioning of Main LT Panel (Non-Essential Panel), as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with all process, powder coated, painting, with front face having openable transparent tempered glass door with PU gasket (for ACB only) complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
3.00 | INCOMER
4.00 | 1000A 4P ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with Protection.- 02 nos.
5.00 | Indication Lamps, LED type for R,Y,B and breaker 'ON', spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection for both incomers.
6.00 | Breaker control switch (TNC switch)-02 nos.
7.00 | Feeder protection relay -02 nos.
8.00 | BUS COUPLER
9.00 | 1000A 4P ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with Protection.- 01 no.
10.00 | Breaker control switch (TNC switch)-01 no.
11.00 | Indication Lamps, LED type for R,Y,B and breaker 'ON', spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection for bus coupler.
12.00 | METERING & INDICATIONS
13.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 2 Sets
14.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-1000A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers suitable range CTs.- 2 sets
15.00 | Digital multi function digital meter to read V,A,KVA, KW, KVAR, KWH, PF, Hz etc with communication module (RS485) and LED display with 3 Nos. CTs and control circuit wiring with 2 Amp. SP MCBs.-2 sets
16.00 | 3 Nos, 1000/5A, CL 0.5 , 15 VA, Cast Resin CTs for metering- 2 sets
17.00 | BUSBARS
18.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 1250 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
19.00 | ACCESSORIES FOR ELECTRICAL & MECHANICAL INTERLOCKING
20.00 | Electrical & mechanical interlocking arrangement as per specifications among 2 nos. Incomers and 01 bus coupler including interconnections etc. as required.
21.00 | OUTGOING
22.00 | 02 Nos. of 400 A, FP, 36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit protection.
23.00 | 04 Nos. of 250 A, FP, 36 kA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit.
24.00 | 03 Nos. of 200A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection.
25.00 | 02 Nos. of 200A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection and suitable rating/capacity 3 phase 02 nos. energy meters.
26.00 | Note- 1. All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF LED Indication (iv) All MCCBs shall be current limiting type. 2. Each outgoing shall also be equiped with 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A). | 1.00 | Each | 10.00 | 1390000.00 | 1390000.00 | 650000.00 | 650000.00 | 1690000.00 | 1690000.00 | 1315000.00 | 1315000.00 | 1530000.00 | 1530000.00 | 1823850.00 | 1823850.00 | 1171075.00 | 1171075.00 | 650000.00 | DEEPAKELECTRICALS
27.00 | Design, manufacture supply, installation, testing and commissioning of LT Panel (Essential Panel), as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification.
28.00 | INCOMER
29.00 | 2 Nos. of 400 A, FP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit.
30.00 | 96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 02 set
31.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 02 set
32.00 | 2 Set of Indication Lamps, LED type, R,Y,B each with 2 Amp. SP MCB for protection.
33.00 | 2 nos. Intelligent multi function digital meter to read V, A, KVA, KW, KVAR, PF, Hz etc with communication facility (RS485 module) and LED display with CTs 500A/5A/5A, 15 VA burden, class 0.5 accuracy for metering and control circuit wiring with 2 Amp. SP MCBs for protection.
34.00 | BUSBARS
35.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 500 Amps capacity, TPN with heat shrinkable colored sleeves andnon-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
36.00 | ACCESSORIES FOR ELECTRICAL & MECHANICAL INTERLOCKING
37.00 | Electrical & mechanical interlocking arrangement as per specifications among 2 nos. Incomers including interconnections etc. as required.
38.00 | OUTGOING
39.00 | 3 Nos. of 200 A, FP, 36 KA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit, earth fault protection inbuilt with release
40.00 | 3 Nos. of 125 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit
41.00 | 2 Nos. of 63A, FP, 25 KA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection
42.00 | Note- 1. All MCCBs should have (i) Ics = Icu at 415 V (ii) Rotary operating mechanism and terminal extension / spreaders (iii) ON/OFF Indication (iv) All MCCBs shall be current limiting type. 2. Each outgoing shall also be equiped with 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A), | 1.00 | Job | 10.00 | 490000.00 | 490000.00 | 583654.00 | 583654.00 | 490000.00 | 490000.00 | 365000.00 | 365000.00 | 495000.00 | 495000.00 | 540750.00 | 540750.00 | 390000.00 | 390000.00 | 365000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
43.00 | FEEDER PILLARS
44.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door feeder pillar made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
45.00 | INCOMINGS
46.00 | 200 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
47.00 | METERING FOR BOTH INCOMERS
48.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display- 1 set
49.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
50.00 | LED indicators complete - RYB - with HRC fuse & toggle switch for incomer - 01 Set.
51.00 | BUS BAR
52.00 | TPN Al. busbar of 250A rating of high conductivity electrolytic quality aluminium alloy
53.00 | OUTGOINGS
54.00 | 100 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication-5 Nos. | 1.00 | Job | 10.00 | 135000.00 | 135000.00 | 250000.00 | 250000.00 | 140000.00 | 140000.00 | 140000.00 | 140000.00 | 152000.00 | 152000.00 | 153300.00 | 153300.00 | 133075.00 | 133075.00 | 133075.00 | Shiva Enterprises
55.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door feeder pillar made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
56.00 | INCOMINGS
57.00 | 200 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
58.00 | METERING FOR BOTH INCOMERS
59.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display- 1 set
60.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
61.00 | LED indicators complete - RYB - with HRC fuse & toggle switch for incomer - 01 Set.
62.00 | BUS BAR
63.00 | TPN Al. busbar of 250A rating of high conductivity electrolytic quality aluminium alloy
64.00 | OUTGOINGS
65.00 | 150 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication-1 No.
66.00 | 100 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication-5 Nos. | 1.00 | Job | 10.00 | 145000.00 | 145000.00 | 220000.00 | 220000.00 | 140000.00 | 140000.00 | 165000.00 | 165000.00 | 170000.00 | 170000.00 | 169050.00 | 169050.00 | 143075.00 | 143075.00 | 140000.00 | Genesis
67.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door feeder pillar made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
68.00 | INCOMINGS
69.00 | 250 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
70.00 | METERING FOR BOTH INCOMERS
71.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display- 1 set
72.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
73.00 | LED indicators complete - RYB - with HRC fuse & toggle switch for incomer - 01 Set.
74.00 | BUS BAR
75.00 | TPN Al. busbar of 300A rating of high conductivity electrolytic quality aluminium alloy
76.00 | OUTGOINGS
77.00 | 125A, FP, 25 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication-4 Nos. | 3.00 | Job | 10.00 | 122000.00 | 366000.00 | 210000.00 | 630000.00 | 130000.00 | 390000.00 | 133000.00 | 399000.00 | 130000.00 | 390000.00 | 141750.00 | 425250.00 | 135000.00 | 405000.00 | 366000.00 | Avion industries
78.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door feeder pillar made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
79.00 | INCOMINGS
80.00 | 200 A, FP, 36 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
81.00 | METERING FOR BOTH INCOMERS
82.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display- 1 set
83.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-200A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
84.00 | LED indicators complete - RYB - with HRC fuse & toggle switch for incomer - 01 Set.
85.00 | BUS BAR
86.00 | TPN Al. busbar of 250A rating of high conductivity electrolytic quality aluminium alloy
87.00 | OUTGOINGS
88.00 | 100A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals and ON/OFF LED Indication-2 Nos.
89.00 | 40A, DP MCB Isolator-8 Nos. | 1.00 | Job | 10.00 | 90000.00 | 90000.00 | 140000.00 | 140000.00 | 102394.00 | 102394.00 | 99000.00 | 99000.00 | 99000.00 | 99000.00 | 112350.00 | 112350.00 | 92000.00 | 92000.00 | 90000.00 | Avion industries
90.00 | Design, Supply, installation, testing & commissioning of L.T. outdoor double door feeder pillar made of 2 mm thick electro galvanized steel/CRCA sheets for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 55, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing completewith all process, powder coated, painting, with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al. busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification enclosed.
91.00 | INCOMINGS
92.00 | 100 A, FP, 18 KA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit with rotary operating mechanism and spreader terminals-01 No.
93.00 | METERING FOR BOTH INCOMERS
94.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display- 1 set
95.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-200A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
96.00 | LED indicators complete - RYB - with HRC fuse & toggle switch for incomer - 01 Set.
97.00 | BUS BAR
98.00 | TPN Al. busbar of 150A rating of high conductivity electrolytic quality aluminium alloy
99.00 | OUTGOINGS
100.00 | 40A, DP MCB Isolator-5 Nos. | 6.00 | Job | 10.00 | 50000.00 | 300000.00 | 100000.00 | 600000.00 | 49000.00 | 294000.00 | 50000.00 | 300000.00 | 45000.00 | 270000.00 | 53550.00 | 321300.00 | 50000.00 | 300000.00 | 270000.00 | Awasthi Electric Works
101.00 | Supply of following size XLPE insulated, PVC sheathed aluminium conductor armourd power cable of 1.1KV grade confiriming to IS 7098 (Part 1) with upto date amendments etc as required.
102.00 | a) 3.5 x 70 Sq.mm | 300.00 | Meter | 10.00 | 380.00 | 114000.00 | 395.00 | 118500.00 | 351.00 | 105300.00 | 431.42 | 129426.00 | 450.00 | 135000.00 | 380.00 | 114000.00 | 415.00 | 124500.00 | 105300.00 | Genesis
103.00 | a) 4 x 16 Sq.mm | 300.00 | Meter | 10.00 | 150.00 | 45000.00 | 140.00 | 42000.00 | 130.00 | 39000.00 | 159.10 | 47730.00 | 170.00 | 51000.00 | 140.00 | 42000.00 | 153.00 | 45900.00 | 39000.00 | Genesis
104.00 | a) 2 x 10 Sq.mm | 200.00 | Meter | 10.00 | 95.00 | 19000.00 | 98.00 | 19600.00 | 85.00 | 17000.00 | 105.08 | 21016.00 | 110.00 | 22000.00 | 90.00 | 18000.00 | 100.00 | 20000.00 | 17000.00 | Genesis
105.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size direct in ground including excavation, sand cushioning,protective covering and refilling the trench etc as required.
106.00 | a) Upto 35 sq. mm | 400.00 | Meter | 10.00 | 170.00 | 68000.00 | 24.00 | 9600.00 | 300.00 | 120000.00 | 143.19 | 57276.00 | 280.00 | 112000.00 | 250.00 | 100000.00 | 70.00 | 28000.00 | 9600.00 | DEEPAKELECTRICALS
107.00 | b) Above 35 sq. mm and upto 95 sq. mm | 270.00 | Meter | 10.00 | 170.00 | 45900.00 | 26.00 | 7020.00 | 200.00 | 54000.00 | 149.85 | 40459.50 | 290.00 | 78300.00 | 200.00 | 54000.00 | 105.00 | 28350.00 | 7020.00 | DEEPAKELECTRICALS
108.00 | c) Above 95 sq. mm and upto 185 sq. mm | 25.00 | Meter | 10.00 | 170.00 | 4250.00 | 34.00 | 850.00 | 500.00 | 12500.00 | 156.14 | 3903.50 | 325.00 | 8125.00 | 200.00 | 5000.00 | 160.00 | 4000.00 | 850.00 | DEEPAKELECTRICALS
109.00 | d) Above 185 sq. mm and upto 400 sq. mm | 25.00 | Meter | 10.00 | 170.00 | 4250.00 | 41.00 | 1025.00 | 500.00 | 12500.00 | 175.38 | 4384.50 | 325.00 | 8125.00 | 250.00 | 6250.00 | 240.00 | 6000.00 | 1025.00 | DEEPAKELECTRICALS
110.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUMEI METAL pipe as required.
111.00 | a) Upto 35 sq. mm | 20.00 | Meter | 10.00 | 30.00 | 600.00 | 24.00 | 480.00 | 50.00 | 1000.00 | 3.00 | 60.00 | 35.00 | 700.00 | 30.00 | 600.00 | 45.00 | 900.00 | 60.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
112.00 | b) Above 35 sq. mm and upto 95 sq. mm | 10.00 | Meter | 10.00 | 40.00 | 400.00 | 26.00 | 260.00 | 100.00 | 1000.00 | 4.00 | 40.00 | 50.00 | 500.00 | 40.00 | 400.00 | 80.00 | 800.00 | 40.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
113.00 | c) Above 95 sq. mm and upto 185 sq. mm | 5.00 | Meter | 10.00 | 50.00 | 250.00 | 34.00 | 170.00 | 150.00 | 750.00 | 4.00 | 20.00 | 70.00 | 350.00 | 60.00 | 300.00 | 140.00 | 700.00 | 20.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
114.00 | d) Above 185 sq. mm and upto 400 sq. mm | 5.00 | Meter | 10.00 | 60.00 | 300.00 | 41.00 | 205.00 | 200.00 | 1000.00 | 4.00 | 20.00 | 90.00 | 450.00 | 90.00 | 450.00 | 185.00 | 925.00 | 20.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
115.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
116.00 | a) Upto 35 sq. mm | 30.00 | Meter | 10.00 | 40.00 | 1200.00 | 24.00 | 720.00 | 150.00 | 4500.00 | 3.00 | 90.00 | 35.00 | 1050.00 | 25.00 | 750.00 | 30.00 | 900.00 | 90.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
117.00 | b) Above 35 sq. mm and upto 95 sq. mm | 10.00 | Meter | 10.00 | 50.00 | 500.00 | 26.00 | 260.00 | 200.00 | 2000.00 | 4.00 | 40.00 | 40.00 | 400.00 | 30.00 | 300.00 | 50.00 | 500.00 | 40.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
118.00 | c) Above 95 sq. mm and upto 185 sq. mm | 20.00 | Meter | 10.00 | 60.00 | 1200.00 | 34.00 | 680.00 | 250.00 | 5000.00 | 4.00 | 80.00 | 60.00 | 1200.00 | 50.00 | 1000.00 | 90.00 | 1800.00 | 80.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
119.00 | d) Above 185 sq. mm and upto 400 sq. mm | 20.00 | Meter | 10.00 | 70.00 | 1400.00 | 41.00 | 820.00 | 300.00 | 6000.00 | 4.00 | 80.00 | 80.00 | 1600.00 | 50.00 | 1000.00 | 100.00 | 2000.00 | 80.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
120.00 | Laying and fixing of one number PVC insulated and PVC sheathed I XLPE power cable of 1.1 KV grade of following size on wall surface as required.
121.00 | a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Meter | 10.00 | 40.00 | 2000.00 | 31.00 | 1550.00 | 150.00 | 7500.00 | 22.00 | 1100.00 | 145.00 | 7250.00 | 40.00 | 2000.00 | 50.00 | 2500.00 | 1100.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
122.00 | b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 10.00 | Meter | 10.00 | 50.00 | 500.00 | 35.00 | 350.00 | 200.00 | 2000.00 | 60.00 | 600.00 | 145.00 | 1450.00 | 50.00 | 500.00 | 80.00 | 800.00 | 350.00 | DEEPAKELECTRICALS
123.00 | c) Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 10.00 | Meter | 10.00 | 60.00 | 600.00 | 39.00 | 390.00 | 250.00 | 2500.00 | 70.00 | 700.00 | 165.00 | 1650.00 | 60.00 | 600.00 | 120.00 | 1200.00 | 390.00 | DEEPAKELECTRICALS
124.00 | d) Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 10.00 | Meter | 10.00 | 70.00 | 700.00 | 43.00 | 430.00 | 300.00 | 3000.00 | 80.00 | 800.00 | 170.00 | 1700.00 | 70.00 | 700.00 | 200.00 | 2000.00 | 430.00 | DEEPAKELECTRICALS
125.00 | Extra for excavation of hard rock/ concrete surface by cutting the hard road/ concrete surface and getting out the excavated material, lifting and disposing of the same within a lead of 50 Mtrs. as directed by Engineer-in-charge. | 5.00 | Cum | 10.00 | 250.00 | 1250.00 | 650.00 | 3250.00 | 15000.00 | 75000.00 | 2500.00 | 12500.00 | 1100.00 | 5500.00 | 1000.00 | 5000.00 | 2800.00 | 14000.00 | 1250.00 | Avion industries
126.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required (a) 80 mm dia | 30.00 | Mtr | 10.00 | 800.00 | 24000.00 | 1350.00 | 40500.00 | 500.00 | 15000.00 | 950.00 | 28500.00 | 850.00 | 25500.00 | 900.00 | 27000.00 | 805.00 | 24150.00 | 15000.00 | Genesis
127.00 | Earthing with GI earth plate 600mm X 600mm X 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 4.00 | Each | 10.00 | 4500.00 | 18000.00 | 9000.00 | 36000.00 | 10000.00 | 40000.00 | 6472.00 | 25888.00 | 14000.00 | 56000.00 | 10000.00 | 40000.00 | 10400.00 | 41600.00 | 18000.00 | Avion industries
128.00 | Supplying and laying 25 mm X 5 mm G.l strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. | 50.00 | Mtr | 10.00 | 190.00 | 9500.00 | 100.00 | 5000.00 | 300.00 | 15000.00 | 108.00 | 5400.00 | 220.00 | 11000.00 | 150.00 | 7500.00 | 172.00 | 8600.00 | 5000.00 | DEEPAKELECTRICALS
129.00 | Providing and fixing 25 mm x 5 mm G. I. strip in 40 mm dia. G. I. pipe from earth electrode as required. | 20.00 | Mtr | 10.00 | 500.00 | 10000.00 | 230.00 | 4600.00 | 500.00 | 10000.00 | 508.32 | 10166.40 | 670.00 | 13400.00 | 500.00 | 10000.00 | 495.00 | 9900.00 | 4600.00 | DEEPAKELECTRICALS
130.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 10.00 | Mtr | 10.00 | 90.00 | 900.00 | 85.00 | 850.00 | 300.00 | 3000.00 | 120.96 | 1209.60 | 160.00 | 1600.00 | 150.00 | 1500.00 | 175.00 | 1750.00 | 850.00 | DEEPAKELECTRICALS
131.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required | 40.00 | Each | 10.00 | 3600.00 | 144000.00 | 6000.00 | 240000.00 | 2200.00 | 88000.00 | 4798.50 | 191940.00 | 10200.00 | 408000.00 | 4500.00 | 180000.00 | 7000.00 | 280000.00 | 88000.00 | Genesis
132.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 200.00 | Mtr | 10.00 | 170.00 | 34000.00 | 95.00 | 19000.00 | 100.00 | 20000.00 | 200.90 | 40180.00 | 220.00 | 44000.00 | 280.00 | 56000.00 | 35.00 | 7000.00 | 7000.00 | Shiva Enterprises
133.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 100.00 | Mtr | 10.00 | 15.00 | 1500.00 | 35.00 | 3500.00 | 100.00 | 10000.00 | 20.00 | 2000.00 | 30.00 | 3000.00 | 50.00 | 5000.00 | 20.00 | 2000.00 | 1500.00 | Avion industries
134.00 | Providing and fixing 6 SWG dia. G.I. wire on surface or in recess for loop earthing along with the existing surface/recessed conduit/ submain wiring/cable etc. as required. | 800.00 | Mtr | 10.00 | 15.00 | 12000.00 | 33.00 | 26400.00 | 50.00 | 40000.00 | 20.00 | 16000.00 | 30.00 | 24000.00 | 30.00 | 24000.00 | 21.00 | 16800.00 | 12000.00 | Avion industries
135.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 5.00 | CuM | 10.00 | 6000.00 | 30000.00 | 4500.00 | 22500.00 | 2000.00 | 10000.00 | 3500.00 | 17500.00 | 8000.00 | 40000.00 | 5000.00 | 25000.00 | 3500.00 | 17500.00 | 10000.00 | Genesis
136.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed aluminium conductor cable of 1.1 kV grade when as required.
137.00 | (a) 3.5x25 sqmm | 30.00 | Each | 10.00 | 70.00 | 2100.00 | 200.00 | 6000.00 | 300.00 | 9000.00 | 115.71 | 3471.30 | 220.00 | 6600.00 | 500.00 | 15000.00 | 575.00 | 17250.00 | 2100.00 | Avion industries
138.00 | (b) 3.5x50 sqmm | 4.00 | Each | 10.00 | 85.00 | 340.00 | 280.00 | 1120.00 | 500.00 | 2000.00 | 239.54 | 958.16 | 340.00 | 1360.00 | 700.00 | 2800.00 | 690.00 | 2760.00 | 340.00 | Avion industries
139.00 | (c) 3.5x70 sqmm | 4.00 | Each | 10.00 | 95.00 | 380.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 271.44 | 1085.76 | 410.00 | 1640.00 | 1000.00 | 4000.00 | 725.00 | 2900.00 | 380.00 | Avion industries
140.00 | (d) 3.5x95 sqmm | 4.00 | Each | 10.00 | 110.00 | 440.00 | 340.00 | 1360.00 | 500.00 | 2000.00 | 341.04 | 1364.16 | 430.00 | 1720.00 | 1200.00 | 4800.00 | 805.00 | 3220.00 | 440.00 | Avion industries
141.00 | (e) 3.5x120 sqmm | 4.00 | Each | 10.00 | 150.00 | 600.00 | 380.00 | 1520.00 | 600.00 | 2400.00 | 355.54 | 1422.16 | 530.00 | 2120.00 | 1200.00 | 4800.00 | 1035.00 | 4140.00 | 600.00 | Avion industries
142.00 | (f) 3.5x150 sqmm | 4.00 | Each | 10.00 | 210.00 | 840.00 | 400.00 | 1600.00 | 600.00 | 2400.00 | 404.26 | 1617.04 | 670.00 | 2680.00 | 1500.00 | 6000.00 | 1090.00 | 4360.00 | 840.00 | Avion industries
143.00 | (g) 3.5x185 sqmm | 4.00 | Each | 10.00 | 340.00 | 1360.00 | 435.00 | 1740.00 | 600.00 | 2400.00 | 507.50 | 2030.00 | 870.00 | 3480.00 | 1500.00 | 6000.00 | 1205.00 | 4820.00 | 1360.00 | Avion industries
144.00 | (h) 3.5x240 sqmm | 4.00 | Each | 10.00 | 400.00 | 1600.00 | 460.00 | 1840.00 | 600.00 | 2400.00 | 576.52 | 2306.08 | 1100.00 | 4400.00 | 1800.00 | 7200.00 | 1450.00 | 5800.00 | 1600.00 | Avion industries
145.00 | (i) 3.5x300 sqmm | 4.00 | Each | 10.00 | 700.00 | 2800.00 | 495.00 | 1980.00 | 800.00 | 3200.00 | 693.10 | 2772.40 | 1500.00 | 6000.00 | 2000.00 | 8000.00 | 1670.00 | 6680.00 | 1980.00 | DEEPAKELECTRICALS
146.00 | (j) 3.5x400 sqmm | 4.00 | Each | 10.00 | 900.00 | 3600.00 | 550.00 | 2200.00 | 800.00 | 3200.00 | 902.48 | 3609.92 | 1900.00 | 7600.00 | 2000.00 | 8000.00 | 1955.00 | 7820.00 | 2200.00 | DEEPAKELECTRICALS
147.00 | (k) 4x16 sqmm | 30.00 | Each | 10.00 | 60.00 | 1800.00 | 150.00 | 4500.00 | 400.00 | 12000.00 | 179.22 | 5376.60 | 200.00 | 6000.00 | 500.00 | 15000.00 | 690.00 | 20700.00 | 1800.00 | Avion industries
148.00 | (l) 4x25 sqmm | 30.00 | Each | 10.00 | 80.00 | 2400.00 | 180.00 | 5400.00 | 400.00 | 12000.00 | 182.70 | 5481.00 | 150.00 | 4500.00 | 500.00 | 15000.00 | 835.00 | 25050.00 | 2400.00 | Avion industries
149.00 | (m) 2x10 sqmm | 10.00 | Each | 10.00 | 50.00 | 500.00 | 140.00 | 1400.00 | 300.00 | 3000.00 | 139.78 | 1397.80 | 200.00 | 2000.00 | 500.00 | 5000.00 | 460.00 | 4600.00 | 500.00 | Avion industries
150.00 | Supply & fixing following danger notice plate made of mild steel sheet of at least 2mm thick & vitreous enameled white on both sides and with inscription in signal red colour on front side as required. (a) Danger /Caution board for 11KV, min. size 200mm x 150mm . | 5.00 | Each | 10.00 | 150.00 | 750.00 | 120.00 | 600.00 | 1000.00 | 5000.00 | 200.00 | 1000.00 | 180.00 | 900.00 | 2000.00 | 10000.00 | 575.00 | 2875.00 | 600.00 | DEEPAKELECTRICALS
151.00 | Supply and fixing standard shock treatment wall chart in two different languages as per BIS 1986. | 4.00 | Each | 10.00 | 500.00 | 2000.00 | 450.00 | 1800.00 | 200.00 | 800.00 | 500.00 | 2000.00 | 1100.00 | 4400.00 | 1500.00 | 6000.00 | 575.00 | 2300.00 | 800.00 | Genesis
152.00 | Supplying of Rubber hand gloves suitable for use in 11 KV power supply. | 2.00 | Each | 10.00 | 400.00 | 800.00 | 550.00 | 1100.00 | 200.00 | 400.00 | 200.00 | 400.00 | 690.00 | 1380.00 | 2000.00 | 4000.00 | 1200.00 | 2400.00 | 400.00 | Genesis, MANNA ELECTRONICS AND ELECTRICAL WORKS
153.00 | Supply of First Aid Box containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross conforming to IS 2217-1963. | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 900.00 | 1800.00 | 2500.00 | 5000.00 | 2500.00 | 5000.00 | 3300.00 | 6600.00 | 2500.00 | 5000.00 | 2000.00 | 4000.00 | 1000.00 | Avion industries
154.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
155.00 | (a) 3.5x25 sqmm | 1.00 | Each | 10.00 | 700.00 | 700.00 | 700.00 | 700.00 | 600.00 | 600.00 | 1610.70 | 1610.70 | 1550.00 | 1550.00 | 1000.00 | 1000.00 | 2190.00 | 2190.00 | 600.00 | Genesis
156.00 | (b) 3.5x50 sqmm | 1.00 | Each | 10.00 | 900.00 | 900.00 | 800.00 | 800.00 | 700.00 | 700.00 | 1610.70 | 1610.70 | 3200.00 | 3200.00 | 1000.00 | 1000.00 | 3000.00 | 3000.00 | 700.00 | Genesis
157.00 | (c) 3.5x70 sqmm | 1.00 | Each | 10.00 | 1100.00 | 1100.00 | 800.00 | 800.00 | 800.00 | 800.00 | 2185.95 | 2185.95 | 3900.00 | 3900.00 | 1000.00 | 1000.00 | 3800.00 | 3800.00 | 800.00 | DEEPAKELECTRICALS, Genesis
158.00 | (d) 3.5x95 sqmm | 1.00 | Each | 10.00 | 1300.00 | 1300.00 | 900.00 | 900.00 | 900.00 | 900.00 | 2286.05 | 2286.05 | 3500.00 | 3500.00 | 1500.00 | 1500.00 | 4500.00 | 4500.00 | 900.00 | DEEPAKELECTRICALS, Genesis
159.00 | (e) 3.5x120 sqmm | 1.00 | Each | 10.00 | 1500.00 | 1500.00 | 1000.00 | 1000.00 | 1000.00 | 1000.00 | 2949.70 | 2949.70 | 3600.00 | 3600.00 | 2000.00 | 2000.00 | 5200.00 | 5200.00 | 1000.00 | DEEPAKELECTRICALS, Genesis
160.00 | (f) 3.5x150 sqmm | 1.00 | Each | 10.00 | 1800.00 | 1800.00 | 1400.00 | 1400.00 | 1200.00 | 1200.00 | 2949.70 | 2949.70 | 3700.00 | 3700.00 | 2000.00 | 2000.00 | 5850.00 | 5850.00 | 1200.00 | Genesis
161.00 | (g) 3.5x185 sqmm | 1.00 | Each | 10.00 | 1900.00 | 1900.00 | 2400.00 | 2400.00 | 1400.00 | 1400.00 | 2949.70 | 2949.70 | 3800.00 | 3800.00 | 2000.00 | 2000.00 | 6500.00 | 6500.00 | 1400.00 | Genesis
162.00 | (h) 3.5x240 sqmm | 1.00 | Each | 10.00 | 1900.00 | 1900.00 | 2800.00 | 2800.00 | 1500.00 | 1500.00 | 3197.35 | 3197.35 | 3800.00 | 3800.00 | 3000.00 | 3000.00 | 7499.00 | 7499.00 | 1500.00 | Genesis
163.00 | (i) 3.5x300 sqmm | 1.00 | Each | 10.00 | 2500.00 | 2500.00 | 3300.00 | 3300.00 | 1600.00 | 1600.00 | 3969.55 | 3969.55 | 4350.00 | 4350.00 | 3500.00 | 3500.00 | 8000.00 | 8000.00 | 1600.00 | Genesis
164.00 | (j) 3.5x400 sqmm | 1.00 | Each | 10.00 | 3000.00 | 3000.00 | 3800.00 | 3800.00 | 1800.00 | 1800.00 | 5177.50 | 5177.50 | 4500.00 | 4500.00 | 3000.00 | 3000.00 | 11000.00 | 11000.00 | 1800.00 | Genesis
165.00 | (k) 4x16 sqmm | 1.00 | Each | 10.00 | 600.00 | 600.00 | 800.00 | 800.00 | 1800.00 | 1800.00 | 1409.20 | 1409.20 | 1300.00 | 1300.00 | 1000.00 | 1000.00 | 1890.00 | 1890.00 | 600.00 | Avion industries
166.00 | (l) 4x25 sqmm | 1.00 | Each | 10.00 | 800.00 | 800.00 | 800.00 | 800.00 | 2000.00 | 2000.00 | 1610.70 | 1610.70 | 1700.00 | 1700.00 | 1000.00 | 1000.00 | 2100.00 | 2100.00 | 800.00 | Avion industries, DEEPAKELECTRICALS
167.00 | Dismantling of pole/ street light standard/ strut embedded in cement concrete foundation etc. as required. | 10.00 | Each | 10.00 | 100.00 | 1000.00 | 500.00 | 5000.00 | 1000.00 | 10000.00 | 1597.20 | 15972.00 | 1500.00 | 15000.00 | 2000.00 | 20000.00 | 1150.00 | 11500.00 | 1000.00 | Avion industries
168.00 | Supply and drawing of 1.5 sq.mm. PVC insulated copper conductor 3 core unarmoured cable, in the existing GI pipe bracket for Control wirings from cable Loopin/Loopout box to light fixture etc. complete as required. | 300.00 | Mtr | 10.00 | 60.00 | 18000.00 | 95.00 | 28500.00 | 50.00 | 15000.00 | 54.00 | 16200.00 | 70.00 | 21000.00 | 80.00 | 24000.00 | 98.00 | 29400.00 | 15000.00 | Genesis
169.00 | Supply and fixing of dust free, jet water free, weather proof corrosion insulated IP 65 protection "loop-in-loop-out" type cable junction box of size 210x310x117 mm deep ( suitable for 2 Nos 4x16 sqmm cable , halogen free, outdoor type suitable for street light made of thermoplastic polycarbonate having 3 groomets, 5 Nos terminals to accomodate all incoming and outgoing cables, providing and fixing 1 No 02 Amp SPMCB and , fixing on existing pole with suitable 02 no clamps with all interconnection etc as required and equivalent to Hensel make and model KM8500. | 50.00 | Each | 10.00 | 4200.00 | 210000.00 | 1550.00 | 77500.00 | 1200.00 | 60000.00 | 2386.00 | 119300.00 | 6700.00 | 335000.00 | 5600.00 | 280000.00 | 1050.00 | 52500.00 | 52500.00 | Shiva Enterprises
170.00 | SITC of 30 watt to 40 watt LED post top luminaries pole mounted type decorative post top with acrylic diffuser, IP-65 protection suitable for operation on 230 Volt , 50 HZ AC supply on the existing GI pole with fixing arrangements (reducer etc.) and making electrical connections etc complete as required. | 25.00 | Each | 10.00 | 3900.00 | 97500.00 | 5500.00 | 137500.00 | 3800.00 | 95000.00 | 7100.00 | 177500.00 | 3300.00 | 82500.00 | 4000.00 | 100000.00 | 4500.00 | 112500.00 | 82500.00 | Awasthi Electric Works
171.00 | Erection of metallic pole of following lentgh in cement concrete 1:3:6 (1 cement : 3 coarse sand:6 grade stone aggregate 40 mm nominal size) including making of 0.5 meter dia round shaped foundation with total height of 0.8 meter (0.5 meter in height above ground level)(approx.) by formwork shuttering including excavation, refilling work, making in good shape, strenghtening, plastering, required curing and painting in yellow black colour etc. complete as required.
172.00 | (a) Above 4.5 metre and upto 6.5 metre | 5.00 | Each | 10.00 | 800.00 | 4000.00 | 2500.00 | 12500.00 | 3000.00 | 15000.00 | 3328.65 | 16643.25 | 2000.00 | 10000.00 | 5000.00 | 25000.00 | 4020.00 | 20100.00 | 4000.00 | Avion industries
173.00 | (b) Above 6.5 metre and upto 8.0 metre | 5.00 | Each | 10.00 | 800.00 | 4000.00 | 2700.00 | 13500.00 | 5000.00 | 25000.00 | 3942.90 | 19714.50 | 2300.00 | 11500.00 | 5000.00 | 25000.00 | 4900.00 | 24500.00 | 4000.00 | Avion industries
174.00 | Supplying and embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape, complete as required. (a) 40 mm dia | 30.00 | Mtr | 10.00 | 415.00 | 12450.00 | 800.00 | 24000.00 | 300.00 | 9000.00 | 285.00 | 8550.00 | 500.00 | 15000.00 | 500.00 | 15000.00 | 585.00 | 17550.00 | 8550.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
175.00 | Providing and making 0.5 meter dia (approx.) round shaped foundation for existing street light with total height of 0.8 meter (0.5 meter in height above ground level)(approx) by formwork shuttering by cement concrete 1:3:6 (1 cement : 3 coarse sand:6 grade stone aggregate 40 mm nominal size) by formwork shuttering, excavation and refilling work, making good shape, strenghtening, plastering, required curing, painting in yellow black colour, including excavation of cable at pole for proper end termination etc complete as required. | 30.00 | Each | 10.00 | 500.00 | 15000.00 | 2500.00 | 75000.00 | 1000.00 | 30000.00 | 3000.00 | 90000.00 | 1500.00 | 45000.00 | 5000.00 | 150000.00 | 3200.00 | 96000.00 | 15000.00 | Avion industries
176.00 | Supply of 10 feet height Heavy duty Aluminium Alloy, general purpose standard folding ladder with self supporting stool with platform, made out of Aluminium Ladder Sections of size 66mm (2.5/8”) x 31mm (1.1/4”) x 3mm (1/8”) thick approx. with steps made of Aluminium 63mm (H) on both side at required distance of 12” (300mm) apart to make the Ladder strong and sturdy with servicemen’s platform at the top and rubber shoes at four legs bottom ends to make the ladder non-slippery, insulated and durable etc complete as required and confirming to technical specifications enclosed. | 2.00 | Each | 10.00 | 15000.00 | 30000.00 | 7800.00 | 15600.00 | 5500.00 | 11000.00 | 8700.00 | 17400.00 | 17000.00 | 34000.00 | 13500.00 | 27000.00 | 8950.00 | 17900.00 | 11000.00 | Genesis
177.00 | Supply of Aluminium Extensible, Tiltable Tower Ladder as per the following specification and size:- Closed Height :- 20 Ft, Extension Height:- 50 Ft, Plat Form Height :- 47 Ft, Sides :- Aluminium "C" Shaped section 66 x 31x3 mm as per IS:733-1983 temper T-6 Steps :- Aluminium 25 mm corrugateed fluited as per IS 733-1983 - T-6 Cross:- MS (scissor cross type) Platform size :- 24" x 24" shall be 3ft below from the top Trolley:- Made of MS Channel 125x62mm and angle 50x50x5mm Trolley size:- 4.5 Ft x 10 Ft Tilting Height - 6 ft Winch - 2 nos Hand operated heavy duty winch gear system shall be provided. One for extend and lower the ladder and another for tilting the ladder Rope:- 8 mm Double steel wire rope (load tested ) Wheels :- 4 Nos , rubber wheels with double ball bearing on caster clamp 2 fix 2 revolving of size 12" x 3". (Brake shall be provided in 2 wheels) Jack:- 4 Nos. Extended screw jack for better stability. Ladder shall be in 3 folds | 2.00 | Each | 10.00 | 165000.00 | 330000.00 | 225000.00 | 450000.00 | 58000.00 | 116000.00 | 180000.00 | 360000.00 | 210000.00 | 420000.00 | 23000.00 | 46000.00 | 145000.00 | 290000.00 | 46000.00 | SAURABH ENTERPRISES
178.00 | Supplying of 25 HP, 6 stage submersible pump motor set suitable for operation on 415 Volts three phase AC supply having delivery dia 100 mm & equivalent to KS7P-2506 submersible pump set complete as required. | 3.00 | Each | 10.00 | 80000.00 | 240000.00 | 120000.00 | 360000.00 | 104000.00 | 312000.00 | 66526.00 | 199578.00 | 87000.00 | 261000.00 | 65000.00 | 195000.00 | 75000.00 | 225000.00 | 195000.00 | SAURABH ENTERPRISES
179.00 | Supply of heavey fully automatic star-delta starter in sheet-steel enclosure suitable for 25 HP submersible pump motor rating AC-3 Duty, 415 V, 50Hz, 3-Ph with relay Max. Range (14-23 Amp) etc complete as required. L&T Model no. MN 25 FASD or its equivalent make and model. | 1.00 | Each | 10.00 | 17000.00 | 17000.00 | 25000.00 | 25000.00 | 24000.00 | 24000.00 | 11904.00 | 11904.00 | 14200.00 | 14200.00 | 11500.00 | 11500.00 | 20000.00 | 20000.00 | 11500.00 | SAURABH ENTERPRISES
180.00 | Dismantling of existing 415 volt, 50Hz LT panels/AMF with accessories by disconnecting electrical connections, earthing connections of panels and transporting the upto AAI store by engaging skilled and unskilled manpower, mechanical means with required T & P etc complete as required.
181.00 | (a) Colony Essential Panel (approx. size 13.2x2.4x1.0 mtr ) | 1.00 | Job | 10.00 | 11000.00 | 11000.00 | 2000.00 | 2000.00 | 800.00 | 800.00 | 500.00 | 500.00 | 10000.00 | 10000.00 | 5000.00 | 5000.00 | 21000.00 | 21000.00 | 500.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
182.00 | (b) Colony Non Ess. Panel / Feeder Pillar (approx. size 2.3x2.1x1.1 mtr ) | 15.00 | Job | 10.00 | 1500.00 | 22500.00 | 2300.00 | 34500.00 | 800.00 | 12000.00 | 650.00 | 9750.00 | 2500.00 | 37500.00 | 3000.00 | 45000.00 | 5500.00 | 82500.00 | 9750.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
183.00 | Dismantling of following LT cables from ground/open masonry duct and transporting the upto AAI store by engaging skilled and unskilled manpower, mechanical means with required T & P etc complete as required.
184.00 | (a) up to 95 sqmm | 50.00 | Mtr | 10.00 | 10.00 | 500.00 | 23.00 | 1150.00 | 100.00 | 5000.00 | 2.00 | 100.00 | 100.00 | 5000.00 | 50.00 | 2500.00 | 75.00 | 3750.00 | 100.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
185.00 | (b) Above 95 sq. mm and upto 185 sq. mm | 25.00 | Mtr | 10.00 | 10.00 | 250.00 | 23.00 | 575.00 | 80.00 | 2000.00 | 2.00 | 50.00 | 130.00 | 3250.00 | 50.00 | 1250.00 | 160.00 | 4000.00 | 50.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
186.00 | © Above 185 sq. mm and upto 400 sq. mm | 25.00 | Mtr | 10.00 | 10.00 | 250.00 | 34.00 | 850.00 | 80.00 | 2000.00 | 2.00 | 50.00 | 150.00 | 3750.00 | 50.00 | 1250.00 | 190.00 | 4750.00 | 50.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
| Total in Figures |  |  |  |  | 4565960.00 |  | 4999999.00 |  | 4797244.00 |  | 4578520.43 |  | 5596830.00 |  | 5396800.00 |  | 4545454.00
Lowest Amount Quoted BY: Shiva Enterprises(4545454.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of existing LT Panels of residential colony and allied works at CATC Prayagraj Tender ID: 2024_AAI_209020_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -760165) | 4545454.00 | L1
| 2 | Avion industries (BID ID -758702) | 4565960.00 | L2
| 3 | MANNA ELECTRONICS AND ELECTRICAL WORKS (BID ID -760055) | 4578520.43 | L3
| 4 | Genesis (BID ID -760000) | 4797244.00 | L4
| 5 | DEEPAKELECTRICALS (BID ID -759113) | 4999999.00 | L5
| 6 | SAURABH ENTERPRISES (BID ID -759707) | 5396800.00 | L6
| 7 | Awasthi Electric Works (BID ID -760299) | 5596830.00 | L7