## BoQ1
Government eProcurement System Created By: Sujit Kumar Modak Created Date/Time: 03-Dec-2024 04:31 PM Tender Title: R and M Other Electrical Works at NSCBI Airport, Kolkata SH Operation and Day to Day Maintenance of Water Treatment Plant , Water Body and Bore-Wells Pumps etc. Tender ID: 2024_AAI_210053_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: R & M Other Electrical Works at NSCBI Airport, Kolkata. SH: Operation & Day to Day Maintenance of Water Treatment Plant (WTP), Water Body (WB) & Bore-Wells Pumps etc.
Contract No: 2024_AAI_210053_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | KAKOLIL TRADE AGENCIES (GSTN-35AAHFK0831G1ZN) BID ID -760767 |  | M/s SOM Engineering Works (GSTN-NA) BID ID -759845
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Operation & daily Maintenance of WTP, WB & Bore Well Pumps
2.00 | Manpower for Round the clock (24x7) Operation & Maintenance of Water Treatment Plant(WTP), Water Bodies(WB) & Bore Well etc. along with its associated system accessories including carrying out regular inspection & testing,Preventive Maintenance, monthly water testing, documentation, deployment of required manpower etc. in accordance to the special conditions of contract at NSCBI Airport, Kolkata.
3.00 | a) First Year | 12.00 | Month |  | 97500.00 | 1170000.00 | 452300.00 | 5427600.00 | 1170000.00 | KAKOLIL TRADE AGENCIES
4.00 | b) Second Year | 12.00 | Month |  | 107250.00 | 1287000.00 | 452300.00 | 5427600.00 | 1287000.00 | KAKOLIL TRADE AGENCIES
5.00 | SH-II: Replacement of media in ACF, OC & PSF
6.00 | Complete Removal and dismantling of old media from existing Pressure Sand Filter of WTP, including cleaning the same, check for any cracks and making good the same through welding, painting the same with two coats of anti corrosive paint and topping up the PSF with new media including supply of new media and replacement of all old PVC stainer with new as per site requirement & Manufacturer's standard complete etc. as required for followings. WTP-Specifications of existing PSF:- Diameter: 2.6 meters Height on straight: 1500 mm Maximum pressure: 4.5kg/cm2 Minimum pressure: 1.0kg/cm2 Average:flow(Each): 45,000 LPH Media quantity: As per OEM requirement
7.00 | a) First Year | 2.00 | Job |  | 99320.00 | 198640.00 | 36000.00 | 72000.00 | 72000.00 | M/s SOM Engineering Works
8.00 | b) Second Year | 2.00 | Job |  | 100313.00 | 200626.00 | 36000.00 | 72000.00 | 72000.00 | M/s SOM Engineering Works
9.00 | Complete Removal and dismantling of old media from existing Activated Carbon Filter of WTP, including cleaning the same, check for any cracks and making good the same through welding, painting the same with two coats of anti corrosive paint and topping up the ACF with new media including supply of new media including supply of new media and replacement of all old PVC stainer with new as per site requirement & Manufacturer's standard complete as required. WTP-Specifications of existing ACF:- Diameter: 1.0 meters Height on straight: 2000 mm maximum Maximum pressure: 4.5kg/cm2 Minimum pressure: 1.0kg/cm2 Average:flow(Each): 45,000 LPH Media quantity: As per OEM requirement
10.00 | a) First Year | 1.00 | Job |  | 105690.00 | 105690.00 | 39501.00 | 39501.00 | 39501.00 | M/s SOM Engineering Works
11.00 | b) Second Year | 1.00 | Job |  | 106747.00 | 106747.00 | 39501.00 | 39501.00 | 39501.00 | M/s SOM Engineering Works
12.00 | Complete Removal & dismantling of old media from existing softner tank with new media including cleaning the same, check for any cracks and making good the same through welding, painting the same with two coats of anti corrosive paint and topping up the softner tank with new media including supply of new media and replacement of all old PVC stainer with new one & ION exchange resins as per site requirement & Manufacturer's standard complete as required. Specifications of existing Softner at WTP Expected Raw Water Hardness:- 500 ppm Expected Treated Water Hardness:- Less than 5 ppm Min. Expected Rate of flow: 60 Cub. Mtr./Hr. Media quantity: As per requirement & OEM Standard and as per instruction of EIC
13.00 | a) First Year | 2.00 | Job |  | 795925.00 | 1591850.00 | 445740.00 | 891480.00 | 891480.00 | M/s SOM Engineering Works
14.00 | b) Second Year | 2.00 | Job |  | 803884.00 | 1607768.00 | 445740.00 | 891480.00 | 891480.00 | M/s SOM Engineering Works
15.00 | Complete Removal and dismantling of old media from existing Oxidation Chamber of Water Treatment Plant, cleaning the same, check for any cracks and making good the damages through welding, painting the same with two coats of anti corossive paint and topping up the OC with new media including supply of new media as per site requirement & Manufacturer's standard complete as required. Specifications of existing OC:- Capacity: 95 cum/hr, 40,000 ltr/sqm/hr. Media quantity: As per OEM requirement and as per instruction of E-I-C.
16.00 | a) First Year | 2.00 | Job |  | 112320.00 | 224640.00 | 38001.00 | 76002.00 | 76002.00 | M/s SOM Engineering Works
17.00 | b) Second Year | 2.00 | Job |  | 113443.00 | 226886.00 | 38001.00 | 76002.00 | 76002.00 | M/s SOM Engineering Works
18.00 | Complete Removal and dismantling of old media from existing FRP Bobbin Wound Filter With Sand & Multiport Valve Top Mount of Water Body, including cleaning the same, check for any cracks and making good the same and supply and topping up the filter with new media and replacement of all old PVC stainer with new as per site requirement & Manufacturer's standard etc. complete as required to make serviceable.
19.00 | a) First Year | 5.00 | Job |  | 45500.00 | 227500.00 | 1000.00 | 5000.00 | 5000.00 | M/s SOM Engineering Works
20.00 | b) Second Year | 5.00 | Job |  | 45955.00 | 229775.00 | 1000.00 | 5000.00 | 5000.00 | M/s SOM Engineering Works
21.00 | SH-III : Cleaning works for Water Tanks
22.00 | Complete dewatering and cleaning of storage tanks (having depth of 8 mtrs./2 mtrs. approx.) through high pressure mechanized cleaning of water tank to get rid of calcination, algae, sludge, sediment and other contaminants by bleaching solution, sodium hypochlorite and other standard chemical treatment to arrest microbiological contaminants etc. as required and as per instruction of Engineer-in-Charge of following volumes (approx.) including providing relevant safety kit and breathing appratus (oxygen mask, cylinder etc.) to cleaning personnel:
23.00 | 2.47 lakh litres volume of water
24.00 | a) First Year | 1.00 | Job |  | 29017.00 | 29017.00 | 8817.00 | 8817.00 | 8817.00 | M/s SOM Engineering Works
25.00 | b) Second Year | 1.00 | Job |  | 29307.00 | 29307.00 | 8817.00 | 8817.00 | 8817.00 | M/s SOM Engineering Works
26.00 | 14.29 lakh litres volume of water
27.00 | a) First Year | 2.00 | Job |  | 85293.00 | 170586.00 | 43727.00 | 87454.00 | 87454.00 | M/s SOM Engineering Works
28.00 | b) Second Year | 2.00 | Job |  | 86145.00 | 172290.00 | 43727.00 | 87454.00 | 87454.00 | M/s SOM Engineering Works
29.00 | 19.09 lakh litres volume of water
30.00 | a) First Year | 2.00 | Job |  | 113981.00 | 227962.00 | 58415.00 | 116830.00 | 116830.00 | M/s SOM Engineering Works
31.00 | b) Second Year | 2.00 | Job |  | 115121.00 | 230242.00 | 58415.00 | 116830.00 | 116830.00 | M/s SOM Engineering Works
32.00 | 6.46 lakh litres volume of water
33.00 | a) First Year | 1.00 | Job |  | 40965.00 | 40965.00 | 19769.00 | 19769.00 | 19769.00 | M/s SOM Engineering Works
34.00 | b) Second Year | 1.00 | Job |  | 41375.00 | 41375.00 | 19769.00 | 19769.00 | 19769.00 | M/s SOM Engineering Works
35.00 | 8.00 lakh litres volume of water
36.00 | a) First Year | 1.00 | Job |  | 47793.00 | 47793.00 | 24480.00 | 24480.00 | 24480.00 | M/s SOM Engineering Works
37.00 | b) Second Year | 1.00 | Job |  | 48271.00 | 48271.00 | 24480.00 | 24480.00 | 24480.00 | M/s SOM Engineering Works
38.00 | SH-IV Electrical Work
39.00 | Supply, installation, testing & commissioning of Star Delta starter's on delay timer having range upto 120 sec and operating voltage 110-415 V AC, 30V DC and suitable current upto 5A.
40.00 | a) First Year | 3.00 | Job |  | 2364.00 | 7092.00 | 600.00 | 1800.00 | 1800.00 | M/s SOM Engineering Works
41.00 | b) Second Year | 3.00 | Job |  | 2626.00 | 7878.00 | 600.00 | 1800.00 | 1800.00 | M/s SOM Engineering Works
42.00 | Supply, installation, testing & commissioning of Overload Relay having Ampere range upto 10 Amp, operating voltage 110V - 415 V AC.
43.00 | a) First Year | 3.00 | Job |  | 2626.00 | 7878.00 | 900.00 | 2700.00 | 2700.00 | M/s SOM Engineering Works
44.00 | b) Second Year | 3.00 | Job |  | 2626.00 | 7878.00 | 900.00 | 2700.00 | 2700.00 | M/s SOM Engineering Works
45.00 | Complete rewinding the following capacity defective motor suitable for 230/415 volts with necessary copper winding and heat varnishing, replacement of bearing etc. complete as required including dismantling and reinstallation of the same at site.
46.00 | Upto 10 KW
47.00 | a) First Year | 8.00 | Job |  | 17069.00 | 136552.00 | 2700.00 | 21600.00 | 21600.00 | M/s SOM Engineering Works
48.00 | b) Second Year | 8.00 | Job |  | 17239.00 | 137912.00 | 2700.00 | 21600.00 | 21600.00 | M/s SOM Engineering Works
49.00 | Above 10 KW to 20 KW
50.00 | a) First Year | 10.00 | Job |  | 26260.00 | 262600.00 | 17001.00 | 170010.00 | 170010.00 | M/s SOM Engineering Works
51.00 | b) Second Year | 10.00 | Job |  | 26522.00 | 265220.00 | 17001.00 | 170010.00 | 170010.00 | M/s SOM Engineering Works
52.00 | Above 20 KW to 30 KW
53.00 | a) First Year | 1.00 | Job |  | 32825.00 | 32825.00 | 1000.00 | 1000.00 | 1000.00 | M/s SOM Engineering Works
54.00 | b) Second Year | 1.00 | Job |  | 33893.00 | 33893.00 | 1000.00 | 1000.00 | 1000.00 | M/s SOM Engineering Works
55.00 | Above 30 KW to 40 KW
56.00 | a) First Year | 3.00 | Job |  | 39390.00 | 118170.00 | 1500.00 | 4500.00 | 4500.00 | M/s SOM Engineering Works
57.00 | b) Second Year | 3.00 | Job |  | 39783.00 | 119349.00 | 1500.00 | 4500.00 | 4500.00 | M/s SOM Engineering Works
58.00 | SH-V : Supply of minor spares for Pumps for replacement.
59.00 | Providing & fixing of suitable size o-ring rubber for following capacity water pump as and when required
60.00 | for 0.75 hp pump
61.00 | a) First Year | 2.00 | Each |  | 260.00 | 520.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
62.00 | b) Second Year | 2.00 | Each |  | 263.00 | 526.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
63.00 | for 1 hp pump
64.00 | a) First Year | 12.00 | Each |  | 325.00 | 3900.00 | 5.00 | 60.00 | 60.00 | M/s SOM Engineering Works
65.00 | b) Second Year | 12.00 | Each |  | 329.00 | 3948.00 | 5.00 | 60.00 | 60.00 | M/s SOM Engineering Works
66.00 | for 2 hp pump
67.00 | a) First Year | 14.00 | Each |  | 390.00 | 5460.00 | 10.00 | 140.00 | 140.00 | M/s SOM Engineering Works
68.00 | b) Second Year | 14.00 | Each |  | 394.00 | 5516.00 | 10.00 | 140.00 | 140.00 | M/s SOM Engineering Works
69.00 | for 3 hp pump
70.00 | a) First Year | 4.00 | Each |  | 455.00 | 1820.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
71.00 | b) Second Year | 4.00 | Each |  | 460.00 | 1840.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
72.00 | for 5 hp pump
73.00 | a) First Year | 2.00 | Each |  | 520.00 | 1040.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
74.00 | b) Second Year | 2.00 | Each |  | 525.00 | 1050.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
75.00 | for 7.5 hp pump
76.00 | a) First Year | 4.00 | Each |  | 585.00 | 2340.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
77.00 | b) Second Year | 4.00 | Each |  | 592.00 | 2368.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
78.00 | for 10 hp pump
79.00 | a) First Year | 4.00 | Each |  | 650.00 | 2600.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
80.00 | b) Second Year | 4.00 | Each |  | 656.00 | 2624.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
81.00 | for 13 hp pump
82.00 | a) First Year | 2.00 | Each |  | 1690.00 | 3380.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
83.00 | b) Second Year | 2.00 | Each |  | 1707.00 | 3414.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
84.00 | for 15 hp pump
85.00 | a) First Year | 11.00 | Each |  | 1755.00 | 19305.00 | 40.00 | 440.00 | 440.00 | M/s SOM Engineering Works
86.00 | b) Second Year | 11.00 | Each |  | 1774.00 | 19514.00 | 40.00 | 440.00 | 440.00 | M/s SOM Engineering Works
87.00 | for 20 hp pump
88.00 | a) First Year | 4.00 | Each |  | 1950.00 | 7800.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
89.00 | b) Second Year | 4.00 | Each |  | 1969.00 | 7876.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
90.00 | for 30 hp pump
91.00 | a) First Year | 4.00 | Each |  | 2015.00 | 8060.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
92.00 | b) Second Year | 4.00 | Each |  | 2036.00 | 8144.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
93.00 | for 50 hp pump
94.00 | a) First Year | 3.00 | Each |  | 2080.00 | 6240.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
95.00 | b) Second Year | 3.00 | Each |  | 2100.00 | 6300.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
96.00 | Providing & fixing of suitable size Mechanical seal for following capacity water as and when requiredpump
97.00 | for 0.75 hp pump
98.00 | a) First Year | 2.00 | Each |  | 390.00 | 780.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
99.00 | b) Second Year | 2.00 | Each |  | 393.00 | 786.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
100.00 | for 1 hp pump
101.00 | a) First Year | 12.00 | Each |  | 585.00 | 7020.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
102.00 | b) Second Year | 12.00 | Each |  | 630.00 | 7560.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
103.00 | for 2 hp pump
104.00 | a) First Year | 14.00 | Each |  | 650.00 | 9100.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
105.00 | b) Second Year | 14.00 | Each |  | 656.00 | 9184.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
106.00 | for 3 hp pump
107.00 | a) First Year | 4.00 | Each |  | 1560.00 | 6240.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
108.00 | b) Second Year | 4.00 | Each |  | 1575.00 | 6300.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
109.00 | for 5 hp pump
110.00 | a) First Year | 2.00 | Each |  | 1560.00 | 3120.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
111.00 | b) Second Year | 2.00 | Each |  | 1575.00 | 3150.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
112.00 | for 7.5 hp pump
113.00 | a) First Year | 4.00 | Each |  | 1820.00 | 7280.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
114.00 | b) Second Year | 4.00 | Each |  | 1838.00 | 7352.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
115.00 | for 10 hp pump
116.00 | a) First Year | 4.00 | Each |  | 1950.00 | 7800.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
117.00 | b) Second Year | 4.00 | Each |  | 1969.00 | 7876.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
118.00 | for 13 hp pump
119.00 | a) First Year | 2.00 | Each |  | 2340.00 | 4680.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
120.00 | b) Second Year | 2.00 | Each |  | 2364.00 | 4728.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
121.00 | for 15 hp pump
122.00 | a) First Year | 11.00 | Each |  | 2600.00 | 28600.00 | 977.00 | 10747.00 | 10747.00 | M/s SOM Engineering Works
123.00 | b) Second Year | 11.00 | Each |  | 2626.00 | 28886.00 | 977.00 | 10747.00 | 10747.00 | M/s SOM Engineering Works
124.00 | for 20 hp pump
125.00 | a) First Year | 4.00 | Each |  | 2860.00 | 11440.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
126.00 | b) Second Year | 4.00 | Each |  | 2888.00 | 11552.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
127.00 | for 30 hp pump
128.00 | a) First Year | 4.00 | Each |  | 2990.00 | 11960.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
129.00 | b) Second Year | 4.00 | Each |  | 3019.00 | 12076.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
130.00 | for 50 hp pump
131.00 | a) First Year | 3.00 | Each |  | 4550.00 | 13650.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
132.00 | b) Second Year | 3.00 | Each |  | 4595.00 | 13785.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
133.00 | Providing & fixing of suitable size Bush for following capacity water pump as and when required
134.00 | for 0.75 hp pump
135.00 | a) First Year | 2.00 | Each |  | 390.00 | 780.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
136.00 | b) Second Year | 2.00 | Each |  | 394.00 | 788.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
137.00 | for 1 hp pump
138.00 | a) First Year | 12.00 | Each |  | 455.00 | 5460.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
139.00 | b) Second Year | 12.00 | Each |  | 460.00 | 5520.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
140.00 | for 2 hp pump
141.00 | a) First Year | 14.00 | Each |  | 1560.00 | 21840.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
142.00 | b) Second Year | 14.00 | Each |  | 1576.00 | 22064.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
143.00 | for 3 hp pump
144.00 | a) First Year | 4.00 | Each |  | 1625.00 | 6500.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
145.00 | b) Second Year | 4.00 | Each |  | 1642.00 | 6568.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
146.00 | for 5 hp pump
147.00 | a) First Year | 2.00 | Each |  | 1690.00 | 3380.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
148.00 | b) Second Year | 2.00 | Each |  | 1706.00 | 3412.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
149.00 | for 7.5 hp pump
150.00 | a) First Year | 4.00 | Each |  | 1765.00 | 7060.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
151.00 | b) Second Year | 4.00 | Each |  | 1773.00 | 7092.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
152.00 | for 10 hp pump
153.00 | a) First Year | 4.00 | Each |  | 2340.00 | 9360.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
154.00 | b) Second Year | 4.00 | Each |  | 2364.00 | 9456.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
155.00 | for 13 hp pump
156.00 | a) First Year | 2.00 | Each |  | 2405.00 | 4810.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
157.00 | b) Second Year | 2.00 | Each |  | 2429.00 | 4858.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
158.00 | for 15 hp pump
159.00 | a) First Year | 11.00 | Each |  | 2470.00 | 27170.00 | 750.00 | 8250.00 | 8250.00 | M/s SOM Engineering Works
160.00 | b) Second Year | 11.00 | Each |  | 2495.00 | 27445.00 | 750.00 | 8250.00 | 8250.00 | M/s SOM Engineering Works
161.00 | for 20 hp pump
162.00 | a) First Year | 4.00 | Each |  | 2600.00 | 10400.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
163.00 | b) Second Year | 4.00 | Each |  | 2626.00 | 10504.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
164.00 | for 30 hp pump
165.00 | a) First Year | 4.00 | Each |  | 2730.00 | 10920.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
166.00 | b) Second Year | 4.00 | Each |  | 2758.00 | 11032.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
167.00 | for 50 hp pump
168.00 | a) First Year | 3.00 | Each |  | 2860.00 | 8580.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
169.00 | b) Second Year | 3.00 | Each |  | 2889.00 | 8667.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
170.00 | Providing & fixing of suitable size Coupling for following capacity water pump as and when required
171.00 | for 0.75 hp pump
172.00 | a) First Year | 2.00 | Each |  | 650.00 | 1300.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
173.00 | b) Second Year | 2.00 | Each |  | 656.00 | 1312.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
174.00 | for 1 hp pump
175.00 | a) First Year | 12.00 | Each |  | 780.00 | 9360.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
176.00 | b) Second Year | 12.00 | Each |  | 788.00 | 9456.00 | 1.00 | 12.00 | 12.00 | M/s SOM Engineering Works
177.00 | for 2 hp pump
178.00 | a) First Year | 14.00 | Each |  | 910.00 | 12740.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
179.00 | b) Second Year | 14.00 | Each |  | 919.00 | 12866.00 | 1.00 | 14.00 | 14.00 | M/s SOM Engineering Works
180.00 | for 3 hp pump
181.00 | a) First Year | 4.00 | Each |  | 1170.00 | 4680.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
182.00 | b) Second Year | 4.00 | Each |  | 1181.00 | 4724.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
183.00 | for 5 hp pump
184.00 | a) First Year | 2.00 | Each |  | 1560.00 | 3120.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
185.00 | b) Second Year | 2.00 | Each |  | 1576.00 | 3152.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
186.00 | for 7.5 hp pump
187.00 | a) First Year | 4.00 | Each |  | 2860.00 | 11440.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
188.00 | b) Second Year | 4.00 | Each |  | 2888.00 | 11552.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
189.00 | for 10 hp pump
190.00 | a) First Year | 4.00 | Each |  | 3120.00 | 12480.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
191.00 | b) Second Year | 4.00 | Each |  | 3151.00 | 12604.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
192.00 | for 13 hp pump
193.00 | a) First Year | 2.00 | Each |  | 3900.00 | 7800.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
194.00 | b) Second Year | 2.00 | Each |  | 3939.00 | 7878.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
195.00 | for 15 hp pump
196.00 | a) First Year | 11.00 | Each |  | 4290.00 | 47190.00 | 1.00 | 11.00 | 11.00 | M/s SOM Engineering Works
197.00 | b) Second Year | 11.00 | Each |  | 4333.00 | 47663.00 | 1.00 | 11.00 | 11.00 | M/s SOM Engineering Works
198.00 | for 20 hp pump
199.00 | a) First Year | 4.00 | Each |  | 5200.00 | 20800.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
200.00 | b) Second Year | 4.00 | Each |  | 5257.00 | 21028.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
201.00 | for 30 hp pump
202.00 | a) First Year | 4.00 | Each |  | 6500.00 | 26000.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
203.00 | b) Second Year | 4.00 | Each |  | 6565.00 | 26260.00 | 1.00 | 4.00 | 4.00 | M/s SOM Engineering Works
204.00 | for 50 hp pump
205.00 | a) First Year | 3.00 | Each |  | 7150.00 | 21450.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
206.00 | b) Second Year | 3.00 | Each |  | 7221.00 | 21663.00 | 1.00 | 3.00 | 3.00 | M/s SOM Engineering Works
207.00 | Providing & fixing of suitable size oil seal for following capacity water pump as and when required
208.00 | for 13 hp pump
209.00 | a) First Year | 2.00 | Each |  | 13650.00 | 27300.00 | 1999.00 | 3998.00 | 3998.00 | M/s SOM Engineering Works
210.00 | b) Second Year | 2.00 | Each |  | 13786.00 | 27572.00 | 1999.00 | 3998.00 | 3998.00 | M/s SOM Engineering Works
211.00 | Providing & fixing of suitable size moisture sensor for following capacity water pump as and when required.
212.00 | for 13 hp pump
213.00 | a) First Year | 2.00 | Each |  | 13000.00 | 26000.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
214.00 | b) Second Year | 2.00 | Each |  | 13130.00 | 26260.00 | 1.00 | 2.00 | 2.00 | M/s SOM Engineering Works
215.00 | SH-VI : Miscellaneous works
216.00 | Supply, installation, testing & commissioning of Water Pressure Gauge having pressure range upto 16 kg/cm2 and suitable size as per site condition.
217.00 | a) First Year | 5.00 | Job |  | 1576.00 | 7880.00 | 200.00 | 1000.00 | 1000.00 | M/s SOM Engineering Works
218.00 | b) Second Year | 5.00 | Job |  | 1591.00 | 7955.00 | 200.00 | 1000.00 | 1000.00 | M/s SOM Engineering Works
219.00 | Scrubbing, cleaning the existing surface of cubicle panels / MS pipes and spray painting the same with two coats of synthetic enamel paint of approved brand and manufacturer of required colour over one coat of red oxide metal primer etc. to give an even shade as required.
220.00 | a) First Year | 1000.00 | sq. mtrs. |  | 276.00 | 276000.00 | 109.00 | 109000.00 | 109000.00 | M/s SOM Engineering Works
221.00 | b) Second Year | 1000.00 | sq. mtrs. |  | 279.00 | 279000.00 | 109.00 | 109000.00 | 109000.00 | M/s SOM Engineering Works
222.00 | Supply, installation, testing & commissioning of 6 lph @ 4 kg/cm2 dosing pump complete etc. as required.
223.00 | a) First Year | 1.00 | Each |  | 11686.00 | 11686.00 | 4500.00 | 4500.00 | 4500.00 | M/s SOM Engineering Works
224.00 | b) Second Year | 1.00 | Each |  | 11802.00 | 11802.00 | 4500.00 | 4500.00 | 4500.00 | M/s SOM Engineering Works
225.00 | Replacement of damaged old RO membrane from RO water Generation plant and installation of new RO membrance (8 inch dia DOW RO membrance BW 30-365), testing & commissioning of the same complete etc as required.
226.00 | a) First Year | 10.00 | Each |  | 51207.00 | 512070.00 | 34500.00 | 345000.00 | 345000.00 | M/s SOM Engineering Works
227.00 | b) Second Year | 10.00 | Each |  | 51719.00 | 517190.00 | 34500.00 | 345000.00 | 345000.00 | M/s SOM Engineering Works
228.00 | Supply of NACL (Iodind Free)
229.00 | a) First Year | 250000.00 | Kg |  | 10.00 | 2500000.00 | 5.00 | 1250000.00 | 1250000.00 | M/s SOM Engineering Works
230.00 | b) Second Year | 250000.00 | Kg |  | 11.00 | 2750000.00 | 5.00 | 1250000.00 | 1250000.00 | M/s SOM Engineering Works
231.00 | Supply of Sodium Hypochlorite (NaOCl 8% free chlorine)
232.00 | a) First Year | 25000.00 | Ltr. |  | 67.00 | 1675000.00 | 25.00 | 625000.00 | 625000.00 | M/s SOM Engineering Works
233.00 | b) Second Year | 25000.00 | Ltr. |  | 68.00 | 1700000.00 | 25.00 | 625000.00 | 625000.00 | M/s SOM Engineering Works
234.00 | Supply of Sodium Metabisulphite (SMBS) food grade
235.00 | a) First Year | 150.00 | Kg |  | 301.00 | 45150.00 | 66.00 | 9900.00 | 9900.00 | M/s SOM Engineering Works
236.00 | b) Second Year | 150.00 | Kg |  | 305.00 | 45750.00 | 66.00 | 9900.00 | 9900.00 | M/s SOM Engineering Works
237.00 | Supply of RO Antiscalant food grade
238.00 | a) First Year | 230.00 | Ltr. |  | 880.00 | 202400.00 | 253.00 | 58190.00 | 58190.00 | M/s SOM Engineering Works
239.00 | b) Second Year | 230.00 | Ltr. |  | 890.00 | 204700.00 | 253.00 | 58190.00 | 58190.00 | M/s SOM Engineering Works
240.00 | Supply of TCCA 90 granular
241.00 | a) First Year | 75.00 | Kg |  | 657.00 | 49275.00 | 203.00 | 15225.00 | 15225.00 | M/s SOM Engineering Works
242.00 | b) Second Year | 75.00 | Kg |  | 664.00 | 49800.00 | 203.00 | 15225.00 | 15225.00 | M/s SOM Engineering Works
243.00 | Supply of TASKI R2 (Cleaning chemical agent) or approved equivalent.
244.00 | a) First Year | 75.00 | Ltr. |  | 432.00 | 32400.00 | 189.00 | 14175.00 | 14175.00 | M/s SOM Engineering Works
245.00 | b) Second Year | 75.00 | Ltr. |  | 437.00 | 32775.00 | 189.00 | 14175.00 | 14175.00 | M/s SOM Engineering Works
246.00 | Supply of TASKI R3 (Cleaning chemical agent) or approved equivalent.
247.00 | a) First Year | 75.00 | Ltr. |  | 368.00 | 27600.00 | 255.00 | 19125.00 | 19125.00 | M/s SOM Engineering Works
248.00 | b) Second Year | 75.00 | Ltr. |  | 372.00 | 27900.00 | 255.00 | 19125.00 | 19125.00 | M/s SOM Engineering Works
249.00 | Supply of SUMA Inox D7.1 (Cleaning chemical agent) or approved equivalent.
250.00 | a) First Year | 150.00 | Ltr. |  | 749.00 | 112350.00 | 336.00 | 50400.00 | 50400.00 | M/s SOM Engineering Works
251.00 | b) Second Year | 150.00 | Ltr. |  | 757.00 | 113550.00 | 336.00 | 50400.00 | 50400.00 | M/s SOM Engineering Works
252.00 | Dismantling the existing panel and Supply, installation, testing, commissioning of indoor type wall mounted starter panel made out of 2 mm thickness CRCA sheet for suitable size confirming to IP 54, including hinged lockable double doors on the size of panel door & Framing & finishing with powder coating color shade RAL 7032 with complete wiring. The Panel Consists of 1. Provision of 7.5 Hp Star-Delta Starter-2 Nos. and 2 nos. DOL Starter with all accessories. 2. Emergency Switch 3. R Y B Indication Lamp for main line installed after MCCB 4. ON, OFF, TRIP indication lamp for each pump 5. Ammeter & Volt meter in main line 6.Ammeter for each pump 7. Exhaust Fan for panel cooling 8. Main Switch (100A TPN MCCB) 9. 2 nos. Selector Switch 1no. for volt meter and 1 no. for Ammeter 10. All pump will have separate MCB 11. Single phase 2 nos. spare terminal with 16A MCB. Panel are completely wiring with suitable size copper wire. | 1.00 | Job |  | 78520.00 | 78520.00 | 41801.00 | 41801.00 | 41801.00 | M/s SOM Engineering Works
253.00 | Supply, installation, testing, commissioning of outdoor type SMPS panel made out of 2 mm thickness CRCA sheet for suitable size confirming to IP 65, including hinged lockable double doors( inner & outer) on the suitable size of panel door & Framing & finishing with powder coating color shade RAL 7032 with complete wiring. The Panel Consists of 1. 3 Nos. SMPS operating in 220V AC input and 18V/15A DC output having 3 nos. (+ve) terminal and 3nos. (-ve) terminal each 2. Single phase 16A MCB for panel switching 3. "ON" indication light 4. Panel Base frame (minimum height 2 ft. from ground) 5. Terminal Block (all DC terminal should connect in terminal block) Panel are completely wiring with suitable size copper wire. | 1.00 | Job |  | 61360.00 | 61360.00 | 33000.00 | 33000.00 | 33000.00 | M/s SOM Engineering Works
254.00 | Supply and laying on surface/ trench etc. as per site conditions of 1100 volt grade PVC sheathed/XLPE 4 core 25 Sq. mm aluminium armoured conductor cable conforming to IS 7098 (Part-I) 1988. | 100.00 | Mtrs. |  | 703.00 | 70300.00 | 234.00 | 23400.00 | 23400.00 | M/s SOM Engineering Works
255.00 | Supply, installation, testing & commissioning of online digital Flow meter with recording & monitoring device and other necessary equipment as required of INLET & OUTLET of WTP plant having suitable up to 200 mm dia pipe. | 2.00 | Each |  | 24050.00 | 48100.00 | 65001.00 | 130002.00 | 48100.00 | KAKOLIL TRADE AGENCIES
256.00 | RO FEED PUMPS :
257.00 | Supply, installation, testing and commissioning of vertical Multistage Inline Pump (SS 316 Impeller & Chamber) with 3 kw IE5 efficiency motor inbuild VFD & Pump Controller (anti hammering facility available) making base with concrete foundation etc. complete as required | 2.00 | SET |  | 725200.00 | 1450400.00 | 496335.00 | 992670.00 | 992670.00 | M/s SOM Engineering Works
258.00 | Capacity 20 M3/Hr.
259.00 | Head-30mtr
260.00 | Quantity-2 Nos(1W+1S)
261.00 | Supply, installation, testing and commissioning of down flow ACTIVATED CARBON FILTER having capacity 20000 LPH consisting vertical cylindrical mild steel pressure vessel with dished end, having size of 1200 mm dia X 1875mm height Vertical type one set of 80 mm dia nominal bore frontal mild steel pipe work for inlet, outlet, back wash and rinse line and 5 No butterfly valve having hand lever type complete all as specified and directed. | 1.00 | SET |  | 695800.00 | 695800.00 | 373521.00 | 373521.00 | 373521.00 | M/s SOM Engineering Works
262.00 | Note: - (i) The pressure vessel shall be made of medium Grade MS Sheet 5 mm thick
263.00 | (ii) Dished ends shall be machine made of medium Grade MS Sheet 5 mm thick
264.00 | (iii) The filter plant shall ensure even distribution across the surface area of the filter bed, header, lateral system & bottom collecting system.
265.00 | (iv) The plant shall have Air release arrangement with 2 No pressure gauge to monitor head loss across the filter and sampling cocks on inlet and outlet ends. The filter plant shall have full charge of filter media as per manufacturer’s design
266.00 | (v) Depth of filter media shall 1000 mm and total media quantity shall 1130 kgs (Gravels, Pebbels, Silex, Core Silex & Activated Carbon).
267.00 | (vi) The filter have man hole, hand hole and supporting legs.
268.00 | (vii) The job shall include necessary surface dressing, PCC/RCC foundation as required complete all as specified & as directed by manufacturer & the same duly approved by officer.
269.00 | (viii) The vessel shall be painted internally with 2 coats of anticorrosive and non toxic black bituminous paint (compatible with drinking water) and external surface shall be painted with 2 coats of Synthetic Enamel paint over a coat of red oxide primer
270.00 | (xviii) The plant shall be designed for a flow of 20000 LPH
271.00 | (xxi) The backwash frequency shall be every 12 hours (twice a day) for continuous operating unit. If unit is operated intermittently, the total operating time in service cycles shall be limited to 5-6 hours before next back wash & back wash time 15-20 minutes.
272.00 | ACTIVTAED CARBON FILTER - ACF1200
273.00 | FLOW RATE(m3/hr) - 20
274.00 | QUANTITY(NOS) - 1
275.00 | FILTER DIA(MM) - 1200
276.00 | FILTER HEIGHT(MM) - 1875
277.00 | SHELL THICKNESS(MM) - 5
278.00 | DISHEND THICKNESS(MM) - 5
279.00 | FRONTAL PIPE WORK(MM) - 80
280.00 | MEDIA DEPTH(MM) - 1000
281.00 | MEDIA QUANTITY - 1130
282.00 | BACKWASH TIME - 20-30MINUTES
283.00 | Supply, Installation, Testing & Commisioning of 10M3/HR RO plant system shall be having capacity to treat the raw water. The treated water should have TDS less as per WHO standards. The operating voltage to 230 volt AC +/- 10% alongwith required capacity high pressure pump and solenoid valves, dry run protection of pump, automatic tank level control, inbuilt auto flush timer for periodic flushing of membranes, over voltage and over current protection with switch mode power supply system complete in all respects including installation, fittings etc. complete as required. | 1.00 | SET |  | 2593500.00 | 2593500.00 | 1273825.00 | 1273825.00 | 1273825.00 | M/s SOM Engineering Works
284.00 | Capacity-10m3/hr
285.00 | Maximum Permate Flow-10m3/hr
286.00 | Array-1:0
287.00 | Membrane Quantity-10 Nos
288.00 | Membrane Size-8 inch
289.00 | Number of Pressure Tube-2Nos
290.00 | Pressure Tube Rating-250PSI
291.00 | Size of Pressure Tube-8 Inch
292.00 | Element of Pressure Tube-5 nos
293.00 | Membrane -Hydramem
294.00 | Recovery of RO plant-50% to 75%
295.00 | High Presure Pump-2 nos(1W+1S)
296.00 | Capacity of High Pressure Pump-14.5m3/hr
297.00 | Head of High Pressure Pump-170mtr
298.00 | MOC of High Pressure Pump-SS316
299.00 | Motor Rating of High Pressure Pump-11KW
300.00 | Motor Speed of High Pressure Pump-2900 RPM
301.00 | Micron Cartrige Filter-2 nos
302.00 | Micron Cartridge Size-Jumbo 20" Long
303.00 | Micron Cartridge MOC-PP
304.00 | Micron CartridgeElement/Type-PP Spiral Wound
305.00 | Micron Cartridge Rating-5 Microns
306.00 | Electrical Panel-1Set
307.00 | ORP Meter-1et
308.00 | Drump Valve-1 Set
309.00 | Instrument List
310.00 | Pressure Gauge Quantity in Nos-1Nos
311.00 | Pressure Gauge Type-Bourdon with Glycerine Filled
312.00 | Pressure Size-150mm
313.00 | Pressure Range-0-40kg/cm2
314.00 | Location-RO Wet Panel
315.00 | Low Pressure Switch Quantity-1 Nos
316.00 | Low Pressure Switch Type-Spring Actuated
317.00 | Low Pressure Location-RO Feed
318.00 | High Pressure Switch Quantity-1 Nos
319.00 | High Pressure Switch Type-Spring Actuated
320.00 | High Pressure Location-High Pressure Pump Delivery
321.00 | Conductivity Indicator Quantity-1 NOs
322.00 | Type-Digital Indicator
323.00 | Location-RO Permate Outlet
324.00 | The complete set should be factory assembled and tested .
325.00 | ALL NECESSARY INTER CONNECTING PIPING
326.00 | Providing and fixing all piping (as described below) and isolation control valves, non return valves etc. complete as required for making the system complete in all respect. | 1.00 | Lot |  | 100000.00 | 100000.00 | 75000.00 | 75000.00 | 75000.00 | M/s SOM Engineering Works
327.00 | UPVC piping (Schedule 40 PVC) - For all interconnecting piping for RO plant (Approx qty. 75 mtr)
328.00 | MS CLASS B - For all interconnecting piping for filter plant (Approx qty. 75 mtr)
329.00 | RO WATER DOMESTIC SUPPLY
330.00 | Supply & installation, testing and commissioning of 2 nos Vertical Multistage Inline Pump (SS 316 Impeller & Chamber) with 2.2 kw IE5 efficiency motor, inbuild VFD & Pump Controller (anti hammering facility available),With Modbus for BMS. base frame, SS 316 Suction & Discharge Manifold, Pressure Transmitter,Pressure Gauge & 200 LTR PN 10 Pressure tank etc. complete as required. | 1.00 | SET |  | 1017030.00 | 1017030.00 | 507501.00 | 507501.00 | 507501.00 | M/s SOM Engineering Works
331.00 | Capacity-6.5m3/hr
332.00 | Head-60mtr
333.00 | Quantity-2 Nos(1W+1S)
334.00 | RO WATER INTERNATIONAL SUPPLY
335.00 | Supply & installation, testing and commissioning of 2 nos Vertical Multistage Inline Pump (SS 316 Impeller & Chamber) with 2.2 kw IE5 efficiency motor, inbuild VFD & Pump Controller (anti hammering facility available),With Modbus for BMS. base frame, SS 316 Suction & Discharge Manifold, Pressure Transmitter,Pressure Gauge & 200 LTR PN 10 Pressure tank etc. complete as required. | 1.00 | SET |  | 987638.00 | 987638.00 | 507501.00 | 507501.00 | 507501.00 | M/s SOM Engineering Works
336.00 | Capacity-1.2m3/hr
337.00 | Head-40mtr
338.00 | Quantity-2 Nos(1W+1S)
339.00 | Supply & installation, testing and commissioning of horizontal centrifugal pump motor set with Stainless Steel SS 304 stage casing,impellers,shaft,sucton & discharge casing as per IEC standrads of handing salt water suitable operation on 3phase,50Hz,415+/- volts AC supply set with IE3 induction motor including mounting baseframe & including all neccessary accessories complete as required. | 2.00 | SET |  | 300000.00 | 600000.00 | 134996.00 | 269992.00 | 269992.00 | M/s SOM Engineering Works
340.00 | Capacity-20m3/hr
341.00 | Head-18mtr
342.00 | Quantity-2 Nos(1W+1S)
343.00 | Dismalting of Salt suction pump with other accessories and including lifting, cutting, grinding, breaking etc. complete as required. | 1.00 | SET |  | 2000.00 | 2000.00 | 505.00 | 505.00 | 505.00 | M/s SOM Engineering Works
344.00 | Supply & installation, testing and commissioning of continues type twin rotary Air Blower with construction in cast iron with V belt drive of capacity 200 cum/hr ,pressure 0.42kg/cm2 suitable for operation on 3 phase,50HZ,415+/- ac supply with suitable IE3motor 4 pole mounted on a channel base plate including all necessary accessories compete as required in compliance to the SCC & GCC and as per direction and complete satifaction of the Enginneering in Charge. | 1.00 | SET |  | 250000.00 | 250000.00 | 74325.00 | 74325.00 | 74325.00 | M/s SOM Engineering Works
345.00 | Dismalting of Existing Air blower with other accessories and including lifting, cutting, grinding, breaking etc. complete as required. | 1.00 | SET |  | 5000.00 | 5000.00 | 500.00 | 500.00 | 500.00 | M/s SOM Engineering Works
346.00 | Softener feed pump Supply & installation, testing and commissioning of vertical inline multistage centrifugal pump motor set with SS04 stage casing,impellers,shaft,uction,& discharge casing as per IEC standards of capacity 64.8m3/hr & head-40m suitable for operation on 3phase ,50hz415+/- AC supply set with suitable IE5 motor of 2pole 15kw including all necessary accessories complete as required in complaince to the SCC & GCC and as per direction and complete satisfaction of the Engineer in Charge. | 2.00 | Nos |  | 908138.00 | 1816276.00 | 169506.00 | 339012.00 | 339012.00 | M/s SOM Engineering Works
347.00 | Dismalting of Existing Softener Feed Pump with other accessories and including lifting, cutting, grinding, breaking etc. complete as required. | 2.00 | Nos |  | 2000.00 | 4000.00 | 500.00 | 1000.00 | 1000.00 | M/s SOM Engineering Works
| Total in Figures |  |  |  |  | 31374140.00 |  | 23635355.00
Lowest Amount Quoted BY: M/s SOM Engineering Works(23635355.00)

## BOQ Summary
BOQ Summary Details Tender Title: R and M Other Electrical Works at NSCBI Airport, Kolkata SH Operation and Day to Day Maintenance of Water Treatment Plant , Water Body and Bore-Wells Pumps etc. Tender ID: 2024_AAI_210053_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s SOM Engineering Works (BID ID -759845) | 23635355.00 | L1
| 2 | KAKOLIL TRADE AGENCIES (BID ID -760767) | 31374140.00 | L2