## BoQ1
Government eProcurement System Created By: Sumit Gupta Created Date/Time: 23-Dec-2024 05:11 PM Tender Title: Construction of New Fire station at R.B. Airport, Bhopal. SH- SITC of VRF/VRV Air-conditioning system Tender ID: 2024_AAI_212121_1
Tender Inviting Authority: SM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Construction of New Fire station at R.B. Airport, Bhopal. SH: SITC of VRF/VRV Air-conditioning system.
Contract No: AAI/BPL/ENGG(E)/NIT-10/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Ingenious Industries (GSTN-27AADFI4734Q1ZV) BID ID -764815 |  | Weartech Engineers Pvt Ltd (GSTN-23AABCW1561C1ZV) BID ID -765054 |  | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (GSTN-24AAHCP2093C1ZP) BID ID -765963 |  | NAQVI BROTHERS (GSTN-09ADHPN6210D1ZT) BID ID -764663 |  | Anoop Refrigeration (GSTN-09AAGFA4646N1Z1) BID ID -766507 |  | VOLGA AIR TECHNOLOGIES (GSTN-NA) BID ID -766490
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with Ecofriendly Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. 100 HP ODU | 1.00 | Each |  | 2157026.00 | 2157026.00 | 1575000.00 | 1575000.00 | 2450000.00 | 2450000.00 | 1932190.00 | 1932190.00 | 1595328.00 | 1595328.00 | 1529658.00 | 1529658.00 | 1529658.00 | VOLGA AIR TECHNOLOGIES
2.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 2 TR | 16.00 | Each |  | 52984.00 | 847744.00 | 33000.00 | 528000.00 | 44500.00 | 712000.00 | 39025.00 | 624400.00 | 34375.00 | 550000.00 | 37460.00 | 599360.00 | 528000.00 | Weartech Engineers Pvt Ltd
3.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 2.8 TR | 4.00 | Each |  | 59496.00 | 237984.00 | 35000.00 | 140000.00 | 47500.00 | 190000.00 | 43648.00 | 174592.00 | 38700.00 | 154800.00 | 36601.00 | 146404.00 | 140000.00 | Weartech Engineers Pvt Ltd
4.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 3.6 TR | 6.00 | Each |  | 60680.00 | 364080.00 | 36500.00 | 219000.00 | 49500.00 | 297000.00 | 45080.00 | 270480.00 | 42300.00 | 253800.00 | 39949.00 | 239694.00 | 219000.00 | Weartech Engineers Pvt Ltd
5.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 4 TR | 4.00 | Meter |  | 60680.00 | 242720.00 | 37500.00 | 150000.00 | 51000.00 | 204000.00 | 45557.00 | 182228.00 | 44540.00 | 178160.00 | 37657.00 | 150628.00 | 150000.00 | Weartech Engineers Pvt Ltd
6.00 | Supply, Installation ,testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft / hard drawn copper refrigerant piping for VRV / VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing / brazing including accessories, insulated with XPLE Class-O tubular insulation / with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
6.01 | 6.4 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 25.00 | RMT |  | 513.00 | 12825.00 | 280.00 | 7000.00 | 300.00 | 7500.00 | 560.00 | 14000.00 | 1400.00 | 35000.00 | 251.00 | 6275.00 | 6275.00 | VOLGA AIR TECHNOLOGIES
6.02 | 9.5 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 125.00 | RMT |  | 606.00 | 75750.00 | 440.00 | 55000.00 | 470.00 | 58750.00 | 700.00 | 87500.00 | 1600.00 | 200000.00 | 368.00 | 46000.00 | 46000.00 | VOLGA AIR TECHNOLOGIES
6.03 | 12.7 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 30.00 | RMT |  | 703.00 | 21090.00 | 600.00 | 18000.00 | 620.00 | 18600.00 | 840.00 | 25200.00 | 1890.00 | 56700.00 | 478.00 | 14340.00 | 14340.00 | VOLGA AIR TECHNOLOGIES
6.04 | 15.86 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 125.00 | RMT |  | 936.00 | 117000.00 | 900.00 | 112500.00 | 790.00 | 98750.00 | 980.00 | 122500.00 | 2200.00 | 275000.00 | 578.00 | 72250.00 | 72250.00 | VOLGA AIR TECHNOLOGIES
6.05 | 19 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 50.00 | RMT |  | 1064.00 | 53200.00 | 1000.00 | 50000.00 | 950.00 | 47500.00 | 1120.00 | 56000.00 | 2500.00 | 125000.00 | 758.00 | 37900.00 | 37900.00 | VOLGA AIR TECHNOLOGIES
6.06 | 22.2 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 50.00 | RMT |  | 1185.00 | 59250.00 | 1200.00 | 60000.00 | 1085.00 | 54250.00 | 1260.00 | 63000.00 | 2800.00 | 140000.00 | 961.00 | 48050.00 | 48050.00 | VOLGA AIR TECHNOLOGIES
6.07 | 25.4 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 25.00 | RMT |  | 1321.00 | 33025.00 | 1350.00 | 33750.00 | 1250.00 | 31250.00 | 1400.00 | 35000.00 | 3200.00 | 80000.00 | 975.00 | 24375.00 | 24375.00 | VOLGA AIR TECHNOLOGIES
6.08 | 28.58 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 75.00 | RMT |  | 1443.00 | 108225.00 | 1500.00 | 112500.00 | 1415.00 | 106125.00 | 1680.00 | 126000.00 | 3500.00 | 262500.00 | 1472.00 | 110400.00 | 106125.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
6.09 | 34.9 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 24.00 | RMT |  | 1952.00 | 46848.00 | 1900.00 | 45600.00 | 2185.00 | 52440.00 | 1960.00 | 47040.00 | 3800.00 | 91200.00 | 1804.00 | 43296.00 | 43296.00 | VOLGA AIR TECHNOLOGIES
6.10 | 38.1 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 30.00 | RMT |  | 2212.00 | 66360.00 | 2100.00 | 63000.00 | 2420.00 | 72600.00 | 2240.00 | 67200.00 | 4400.00 | 132000.00 | 1927.00 | 57810.00 | 57810.00 | VOLGA AIR TECHNOLOGIES
6.11 | 41.27 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 30.00 | RMT |  | 2544.00 | 76320.00 | 2500.00 | 75000.00 | 2350.00 | 70500.00 | 2520.00 | 75600.00 | 4700.00 | 141000.00 | 2168.00 | 65040.00 | 65040.00 | VOLGA AIR TECHNOLOGIES
6.12 | 44 mm dia(OD) (Softdrawn) with tube thickness 1.2 mm with 19 mm thick insulation. | 25.00 | RMT |  | 3235.00 | 80875.00 | 2300.00 | 57500.00 | 2850.00 | 71250.00 | 2800.00 | 70000.00 | 4900.00 | 122500.00 | 1638.00 | 40950.00 | 40950.00 | VOLGA AIR TECHNOLOGIES
7.00 | Supply, installation, testing & commissioning of ref nut / Y-joints of brass for indoor and outdoor units of suitable size as per requirement. For Outdoor Unit | 8.00 | Each |  | 4200.00 | 33600.00 | 3100.00 | 24800.00 | 9900.00 | 79200.00 | 7840.00 | 62720.00 | 4500.00 | 36000.00 | 6038.00 | 48304.00 | 24800.00 | Weartech Engineers Pvt Ltd
8.00 | Supply, installation, testing & commissioning of Ref nut / Y-joints of brass for indoor and outdoor units of suitable size as per requirement. For Indoor Unit | 54.00 | Each |  | 4200.00 | 226800.00 | 1600.00 | 86400.00 | 4000.00 | 216000.00 | 3500.00 | 189000.00 | 4500.00 | 243000.00 | 4428.00 | 239112.00 | 86400.00 | Weartech Engineers Pvt Ltd
9.00 | Supply and fixing of drain piping in hard PVC with all fittings, supports and clamps, including drilling hole in wall to route the drain pipe with 6mm thick nitrile rubber insulation. 25mm | 80.00 | RMT |  | 210.00 | 16800.00 | 140.00 | 11200.00 | 110.00 | 8800.00 | 140.00 | 11200.00 | 120.00 | 9600.00 | 188.00 | 15040.00 | 8800.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
10.00 | Supply and fixing of drain piping in hard PVC with all fittings, supports and clamps, including drilling hole in wall to route the drain pipe with 6mm thick nitrile rubber insulation. 32mm | 55.00 | RMT |  | 285.00 | 15675.00 | 170.00 | 9350.00 | 140.00 | 7700.00 | 210.00 | 11550.00 | 145.00 | 7975.00 | 120.00 | 6600.00 | 6600.00 | VOLGA AIR TECHNOLOGIES
16.00 | Supply and fixing of drain piping in hard PVC with all fittings, supports and clamps, including drilling hole in wall to route the drain pipe with 6mm thick nitrile rubber insulation. 40mm | 20.00 | RMT |  | 370.00 | 7400.00 | 220.00 | 4400.00 | 170.00 | 3400.00 | 280.00 | 5600.00 | 150.00 | 3000.00 | 100.00 | 2000.00 | 2000.00 | VOLGA AIR TECHNOLOGIES
17.00 | Supply and drawing Control Cable in suitable size PVC conduit between the indoor units & outdoor units. 2C x 0.75 Sq.mm Shielded Braided PVC inner sheathed, copper conductor, communication cable from indoor to outdoor units & between central controller. | 750.00 | Meter |  | 165.00 | 123750.00 | 80.00 | 60000.00 | 140.00 | 105000.00 | 140.00 | 105000.00 | 80.00 | 60000.00 | 110.00 | 82500.00 | 60000.00 | Weartech Engineers Pvt Ltd, Anoop Refrigeration
18.00 | Supply, fabrication and installation at proposed location of MS base frame ( for VRF machine Out Door Unit).The same shall be fabricated form 100mm wide "C" channels & shall be painted with one coat of primer and 02 coat of black enamel paint. | 300.00 | KG |  | 125.00 | 37500.00 | 100.00 | 30000.00 | 210.00 | 63000.00 | 140.00 | 42000.00 | 175.00 | 52500.00 | 100.00 | 30000.00 | 30000.00 | Weartech Engineers Pvt Ltd, VOLGA AIR TECHNOLOGIES
| Total in Figures |  |  |  |  | 5061847.00 |  | 3528000.00 |  | 5025615.00 |  | 4400000.00 |  | 4805063.00 |  | 3655986.00
Lowest Amount Quoted BY: Weartech Engineers Pvt Ltd(3528000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Fire station at R.B. Airport, Bhopal. SH- SITC of VRF/VRV Air-conditioning system Tender ID: 2024_AAI_212121_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Weartech Engineers Pvt Ltd (BID ID -765054) | 3528000.00 | L1
| 2 | VOLGA AIR TECHNOLOGIES (BID ID -766490) | 3655986.00 | L2
| 3 | NAQVI BROTHERS (BID ID -764663) | 4400000.00 | L3
| 4 | Anoop Refrigeration (BID ID -766507) | 4805063.00 | L4
| 5 | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (BID ID -765963) | 5025615.00 | L5
| 6 | Ingenious Industries (BID ID -764815) | 5061847.00 | L6