## BoQ1
Government eProcurement System Created By: Shridhar Gupta Created Date/Time: 02-Dec-2024 04:13 PM Tender Title: Construction of New Terminal Building and Other Allied structures Phase I and II at Patna Airport SH SITC of Gas Based Fire Extinguishing System Tender ID: 2024_AAI_212335_1
Tender Inviting Authority: <SM (Engg.-Elect), JPNI Airport, Patna>
Name of Work: Construction of New Terminal Building & Other Allied structures (Phase I &II) at Patna Airport. SH: SITC of Gas Based Fire Extinguishing System.
Contract No: 2024_AAI_212335
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SVS Buildwel Pvt Ltd (GSTN-07AALCS7473H1ZU) BID ID -761651 |  | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -766108 |  | Vimal Fire Controls private Limited (GSTN-24AAACV9204C1ZR) BID ID -766770
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SUB-HEAD - GAS SUPPRESSION :
1.01 | Supply, Installation, Testing & Commissioning of 34 Litres Capacity Seamless UL/FM/VDS listed Cylinder CCOE/PESO Approved, complete with valve assembly and pressure gauge with a safety burst disc for 25-70Bar pressure system. | 1.00 | Nos. |  | 130045.00 | 130045.00 | 82730.00 | 82730.00 | 108000.00 | 108000.00 | 82730.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.02 | Supply, Installation, Testing & Commissioning of 80 Litres Capacity Seamless UL/FM/VDS listed Cylinder CCOE/PESO Approved, complete with valve assembly and pressure gauge with a safety burst disc for 25-70Bar pressure system. | 2.00 | Nos. |  | 136181.00 | 272362.00 | 119510.00 | 239020.00 | 149400.00 | 298800.00 | 239020.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.03 | Supply, Installation, Testing & Commissioning of 120 Litres Capacity Seamless UL/FM/VDS listed Cylinder CCOE/PESO Approved, complete with valve assembly and pressure gauge with a safety burst disc for 25-70Bar pressure system. | 4.00 | Nos. |  | 153055.00 | 612220.00 | 120580.00 | 482320.00 | 162000.00 | 648000.00 | 482320.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.04 | Supply, Installation, Testing & Commissioning of 140 Litres Capacity Seamless UL/FM/VDS listed Cylinder CCOE/PESO Approved, complete with valve assembly and pressure gauge with a safety burst disc for 25-70Bar pressure system. | 28.00 | Nos. |  | 156123.00 | 4371444.00 | 124570.00 | 3487960.00 | 171000.00 | 4788000.00 | 3487960.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.05 | Supply of Cylinder Protective Cap for 25-70 Bar System | 35.00 | Nos. |  | 8207.00 | 287245.00 | 500.00 | 17500.00 | 9.00 | 315.00 | 315.00 | Vimal Fire Controls private Limited
1.06 | FK-5-1-12 Fire Protection fluid compound of carbon, fluorine and oxygen (CF3CF2C(O)CF(CF3)2). UL/FM/VDS listed , 25-70Bar pressure system. | 4191.00 | Kg |  | 1956.00 | 8197596.00 | 1550.00 | 6496050.00 | 1710.00 | 7166610.00 | 6496050.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.07 | Supply, Installation, Testing & Commissioning of Electric Control Head operated electrically from the Detection & Control System or locally with a manual lever on the control head for 25-70Bar pressure system. Shall be of the same make as of FACP & Suppression Panel. | 9.00 | Nos. |  | 43566.00 | 392094.00 | 16940.00 | 152460.00 | 9.00 | 81.00 | 81.00 | Vimal Fire Controls private Limited
1.08 | Supply, Installation, Testing & Commissioning of Pressure Operated Control Head which allows for pressure actuation slave cylinders and is mounted directly on top of the slave cylinders valve. Shall be of the same make as of FACP & Suppression Panel. | 26.00 | Nos. |  | 2915.00 | 75790.00 | 9190.00 | 238940.00 | 4500.00 | 117000.00 | 75790.00 | SVS Buildwel Pvt Ltd
1.09 | Supply, Installation, Testing & Commissioning of Discharge Nozzles are designed to provide the proper flow rate and distribution of FK-5-1-12 to total flood a hazard area : 180 deg./ 360 deg., 13m X 13 m coverage | 13.00 | Nos. |  | 3221.00 | 41873.00 | 5500.00 | 71500.00 | 10800.00 | 140400.00 | 41873.00 | SVS Buildwel Pvt Ltd
1.10 | Supply, Installation, Testing and Commissioning of Discharge Hose, 1-1/2” (use with 34, 80, 120 & 140 Ltr. Cylinders) | 35.00 | Nos. |  | 16260.00 | 569100.00 | 14110.00 | 493850.00 | 28800.00 | 1008000.00 | 493850.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.11 | Supply, Installation, Testing and Commissioning of Flexible Actuation Hose (Pilot pressure is directed to a pressure operated control head on each cylinder valve using 1/4 inch actuation hose) | 26.00 | Nos. |  | 3682.00 | 95732.00 | 6040.00 | 157040.00 | 4500.00 | 117000.00 | 95732.00 | SVS Buildwel Pvt Ltd
1.12 | Supply, Installation, Testing and Commissioning of Master Cylinder Adapter Kit used to actuate the Slave Cylinder. | 4.00 | Nos. |  | 384.00 | 1536.00 | 30020.00 | 120080.00 | 9.00 | 36.00 | 36.00 | Vimal Fire Controls private Limited
1.13 | Supply, Installation, Testing and Commissioning of 2" Manifold Check Valve installed at the discharge manifold to allow removal of any FK-5-1-12 cylinder from the manifold while still retaining a closed system. | 9.00 | Nos. |  | 19328.00 | 173952.00 | 10030.00 | 90270.00 | 27000.00 | 243000.00 | 90270.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.14 | Supply, Installation, Testing and Commissioning of Manifold Supervisory Switch for indication of discharge of system. | 9.00 | Nos. |  | 21476.00 | 193284.00 | 0.00 | 0.00 | 27000.00 | 243000.00 | 0.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.15 | Supply, Installation, Testing and Commissioning of Cylinder Strap for Cylinder. | 35.00 | Nos. |  | 8182.00 | 286370.00 | 1100.00 | 38500.00 | 900.00 | 31500.00 | 31500.00 | Vimal Fire Controls private Limited
1.16 | Supply, Installation, Testing and Commissioning of Brass Male Elbow. | 4.00 | Nos. |  | 1227.00 | 4908.00 | 0.00 | 0.00 | 9.00 | 36.00 | 0.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.17 | Supply, Installation, Testing and Commissioning of Brass Male TEE. | 22.00 | Nos. |  | 1074.00 | 23628.00 | 0.00 | 0.00 | 9.00 | 198.00 | 0.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.18 | Supply, Installation, Testing and Commissioning of Seamless pipes along with Elbow, T Joints, connectors, Hangers and its accessories for Suppression System. | 9.00 | Lot |  | 53690.00 | 483210.00 | 11560.00 | 104040.00 | 207000.00 | 1863000.00 | 104040.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.19 | Supply, Installation, Testing and Commissioning of Cylinder Bank with all accessories for Suppression System | 9.00 | Lot |  | 434600.00 | 3911400.00 | 12000.00 | 108000.00 | 90000.00 | 810000.00 | 108000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.20 | Disconnecting Switch for time of mantanance. | 9.00 | Nos. |  | 64428.00 | 579852.00 | 2500.00 | 22500.00 | 9.00 | 81.00 | 81.00 | Vimal Fire Controls private Limited
2.00 | SUB-HEAD - FIRE DETECTION :
2.01 | Supply, Installation, Testing and Commissioning of UL Listed Addressable Main Fire Alarm 1 Loop. Capable of detection and sending the cross zone signals to the respective Gas release panel. UL Listed & FM approved. The Panel shall be of the same make as the main FACP & GSS. | 9.00 | Nos. |  | 296829.00 | 2671461.00 | 73920.00 | 665280.00 | 207000.00 | 1863000.00 | 665280.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.02 | Supply, installation, testing and commissioning addressable multi-criteria photo-thermal detector with sensitivity range of 0.5 to 4.0% obs/ ft. Intelligent multi criteria detection device shall include the ability to combine signal of the thermal sensor with photoelectric signal in an effort to react hastily in the event of a fire situation. Detector shall be able to distinguish between a fire and a false alarm condition. The detector shall have twin bi-color LED for 360 deg viewing. UL268, 7th Edition listed & FM approved- for detector & base | 22.00 | Nos. |  | 3758.00 | 82676.00 | 2470.00 | 54340.00 | 3600.00 | 79200.00 | 54340.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.03 | Supplying, installing, testing and commissioning approved make Addressable Manual Call Point (Break Glass Type). The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. The device shall comply UL approval. | 9.00 | Nos. |  | 6443.00 | 57987.00 | 3290.00 | 29610.00 | 7200.00 | 64800.00 | 29610.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.04 | Supply, Installation, Testing and Commissioning of Manual Release Switch used as electrical activation device for gas extinguishing systems complete etc as required. UL listed & FM approved. The device shall be of the same make as the main FACP & GSS. | 9.00 | Nos. |  | 25311.00 | 227799.00 | 3870.00 | 34830.00 | 10800.00 | 97200.00 | 34830.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.05 | Supply, Installation, Testing and Commissioning of Manual Abort Switch used as electrical activation device for gas extinguishing systems complete etc as required. UL listed & FM approved. The device shall be of the same make as the main FACP & GSS. | 9.00 | Nos. |  | 25311.00 | 227799.00 | 3870.00 | 34830.00 | 10800.00 | 97200.00 | 34830.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.06 | Supply, installation, testing & commissioning of Sounder cum Strobe rated at 84 dBA @ 3m for Audible annunciation and 115cd flashintg at 1 Hz for visual indication. UL Listed | 9.00 | Nos. |  | 5982.00 | 53838.00 | 3660.00 | 32940.00 | 8100.00 | 72900.00 | 32940.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.07 | Supply, Installation, Testing and Commissioning of Addressable control module for the activation of sounder and gas release sign.UL Listed & FM approved | 9.00 | Nos. |  | 6059.00 | 54531.00 | 2850.00 | 25650.00 | 5400.00 | 48600.00 | 25650.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.08 | Supply, Installation, testing & commissioning of Addressable Relay module for 3rd Party equipment. UL Listed & FM approved | 9.00 | Nos. |  | 6059.00 | 54531.00 | 3150.00 | 28350.00 | 5400.00 | 48600.00 | 28350.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.09 | Supply, Installation, Testing and Commissioning of Battery 12V/ 7AH. | 18.00 | Nos. |  | 1687.00 | 30366.00 | 1120.00 | 20160.00 | 2070.00 | 37260.00 | 20160.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.10 | Supply, Installation, Testing and Commissioning of 24v Power Supply. | 9.00 | Nos. |  | 1687.00 | 15183.00 | 6340.00 | 57060.00 | 63000.00 | 567000.00 | 15183.00 | SVS Buildwel Pvt Ltd
2.11 | Supply, Installation, Testing and Commissioning of GAS RELEASE Signages Light | 9.00 | Nos. |  | 5062.00 | 45558.00 | 4200.00 | 37800.00 | 9000.00 | 81000.00 | 37800.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.12 | Supply, Installation, Testing and Commissioning of Photo-luminiscent Gas Release caution sign boards for approved locations. | 9.00 | Nos. |  | 5062.00 | 45558.00 | 1200.00 | 10800.00 | 7200.00 | 64800.00 | 10800.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.13 | Proving and laying of 2c x 1.5 sq mm FRLS Fire Survival armoured fire Cable along with accessories for Fire Alarm panel and other devices etc as required. | 600.00 | Mtr. |  | 192.00 | 115200.00 | 190.00 | 114000.00 | 306.00 | 183600.00 | 114000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
2.14 | Prparation of drawings, Documentation and Training Charges. | 9.00 | Lot |  | 7670.00 | 69030.00 | 20000.00 | 180000.00 | 5400.00 | 48600.00 | 48600.00 | Vimal Fire Controls private Limited
| Total in Figures |  |  |  |  | 24455158.00 |  | 13728410.00 |  | 20936817.00
Lowest Amount Quoted BY: PYROGUARD ENGINEERS PRIVATE LIMITED(13728410.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Terminal Building and Other Allied structures Phase I and II at Patna Airport SH SITC of Gas Based Fire Extinguishing System Tender ID: 2024_AAI_212335_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -766108) | 13728410.00 | L1
| 2 | Vimal Fire Controls private Limited (BID ID -766770) | 20936817.00 | L2
| 3 | SVS Buildwel Pvt Ltd (BID ID -761651) | 24455158.00 | L3