## BoQ1
Government eProcurement System Created By: Disha Bhatt Created Date/Time: 19-Dec-2024 04:18 PM Tender Title: Replacement of GLF Facilities at Hubballi Airport Tender ID: 2024_AAI_212372_1
Tender Inviting Authority: SR. MANAGER (ENGG-ELECTRICAL), AAI, HUBBALLI AIRPORT
Name of Work: Replacement of Old GLF Facilities at Hubballi Airport.
Contract No: 2024_AAI_212372_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -779679 |  | vardhman Airport solutions pvt. Ltd. (GSTN-NA) BID ID -778608
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Supply of Fixtures Supply of Bi-Directional Elevated High Intensity Halogen Type Runway Edge Light Fitting complete with prefocus lamp holder, upto 200 watt 6.6 A halogen lamp ,clear outer prismatic dome, clear inner prismatic lens, lens holding mechanism, ball joint for easy levelling, breakable coupling, central column mounting assembly, gaskets, two pin secondary lead plug suitable for connection with isolating transformer, base plate with 6 nos. M-10 stainless steel bolts, spring & plain washers & other accessories etc. and confirming to particular specification with lens including lamp etc. as required to meet latest ICAO requirement and to match with existing Youyang make fittings.
1.10 | clear lense/clear lense | 40.00 | Nos |  | 6900.00 | 276000.00 | 6500.00 | 260000.00 | 260000.00 | vardhman Airport solutions pvt. Ltd.
1.20 | clear lense/amber lense | 30.00 | Nos |  | 6900.00 | 207000.00 | 7000.00 | 210000.00 | 207000.00 | Manish Electricals
2.00 | Supply of Unidirectional Elevated Type High Intensity Approach Light Fitting suitable for use with upto 200W 6.6A halogen lamp complete with prefocus lamp holder, 200 watt 6.6 A halogen lamp , lens / spreader glass, lens holding mechanism, reflector assembly, elevation and horizontal adjustment mechanism, breakable coupling , central column mounting assembly, gaskets, two pin secondary lead plug suitable for connection with isolating transformer, base plate with 6 nos. M-10 stainless steel bolts, spring & plain washers & other accessories etc. and confirming to particular specification with following lens including lamp etc. as required to meet latest ICAO requirement.
2.10 | With Clear Lense( For Approach lights) | 40.00 | Nos |  | 8500.00 | 340000.00 | 7000.00 | 280000.00 | 280000.00 | vardhman Airport solutions pvt. Ltd.
2.20 | With Green Lense( For Threshold lights) | 20.00 | Nos |  | 8500.00 | 170000.00 | 8000.00 | 160000.00 | 160000.00 | vardhman Airport solutions pvt. Ltd.
2.30 | With Red Lense( For End lights) | 15.00 | Nos |  | 8500.00 | 127500.00 | 8000.00 | 120000.00 | 120000.00 | vardhman Airport solutions pvt. Ltd.
3.00 | Supply of following Bi-directional INSET TYPE HIRL EDGE LIGHT FITTING, matching body made of die cast aluminium, 2 x 105W 6.6Amps pre-focused Halogen lamp, connected heat resistant accessories, prism assembly, optical assembly, O-ring seal, pressure relief plug, hardware, clear/yellow lenses etc. complete as required including O-ring, gasket and one set lamps complete as required as per specifications and to suit with existing shallow base of Youyang make fitting.
3.10 | Left beam clear and right beam yellow or amber | 4.00 | Nos |  | 62000.00 | 248000.00 | 55000.00 | 220000.00 | 220000.00 | vardhman Airport solutions pvt. Ltd.
3.20 | Left beam clear and right beam clear | 4.00 | Nos |  | 62000.00 | 248000.00 | 55000.00 | 220000.00 | 220000.00 | vardhman Airport solutions pvt. Ltd.
4.00 | Supply of uni-directional INSET TYPE APPROCAH LIGHT FITTING with clear lenses, matching body made of die cast aluminium, 3 x 105W 6.6A pre-focused halogen Lamp, connected heat resistant accessories, prism assembly, optical assembly, O ring seal, pressure relief plug, hardware, clear lenses etc. complete as required to suit with existing shallow base of Youyang make fitting. | 2.00 | Nos |  | 65000.00 | 130000.00 | 57000.00 | 114000.00 | 114000.00 | vardhman Airport solutions pvt. Ltd.
5.00 | Supply of 6 sqmm , 5 KV grade, single core stranded copper conductor PVC insulated and PVC sheathed Unshielded , anti termite and anti rodent treated Airport Lighting UG Cable generally confirming to IS 1554 Part-II with up to date amendments . | 2991.00 | Mtr |  | 90.00 | 269190.00 | 90.00 | 269190.00 | 269190.00 | vardhman Airport solutions pvt. Ltd., Manish Electricals
6.00 | Supply of 16 sqmm , 5 KV grade, single core stranded copper conductor PVC insulated and PVC sheathed Unshielded , anti termite and anti rodent treated Airport Lighting UG Cable generally confirming to IS 1554 Part-II with up to date amendments . | 1000.00 | Mtr |  | 215.00 | 215000.00 | 200.00 | 200000.00 | 200000.00 | vardhman Airport solutions pvt. Ltd.
7.00 | Supply of following sizes 5 KV grade dry type Plug and Receptacle of type I, class 'B' primary connector kit with field attachment and suitable for 5 KV grade single core copper conductor, copper braided, XLPE insulated PE outer sheathed shielded cable, complete as required confirming to the technical specification.
7.10 | 16 sqmm | 20.00 | SET |  | 425.00 | 8500.00 | 400.00 | 8000.00 | 8000.00 | vardhman Airport solutions pvt. Ltd.
7.20 | 6 Sqmm | 50.00 | SET |  | 425.00 | 21250.00 | 400.00 | 20000.00 | 20000.00 | vardhman Airport solutions pvt. Ltd.
8.00 | Supply of secondary lead of size 2 x 4 sq mm multi stranded annealed conductor PCP sheathed unshielded cable of 1.1 KV grade. | 250.00 | Mtr |  | 220.00 | 55000.00 | 155.00 | 38750.00 | 38750.00 | vardhman Airport solutions pvt. Ltd.
9.00 | Supply of C.I. Isolating Transformer housing box,water tight, round type,metal container of Dimension outside height 450mm, Outside Diameter 330mm, made of 10mm thick all around,top Surface 15mm thick smoothly machined to receive base of light fixture base plate, installed underground/cc grouting for housing isolation transformer, AFL cable leads, having a clear holes centre 75mm above bottom surface suitable to receive One/two/three Nos of 50mm dia "B" class GI pipe fixed with check nuts and other holes at 250mm from the bottom of the CI Box to receive 15mm dia "B" class GI pipe with check nuts as required. CI box should have two SS earth bolts of M10 x 30mm with tapped holes inside near the hole and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface, 6 nos. M-10 taped holes at hole centre of 260 mm to receive fitting base plate and bolts as per the drawings & Technical specifications etc complete as required. | 40.00 | Nos |  | 5400.00 | 216000.00 | 5000.00 | 200000.00 | 200000.00 | vardhman Airport solutions pvt. Ltd.
10.00 | Supply of 50mm (OD) size HDPE pipe,PN4 grade, PE 63, ISI marked conforming to IS 4984:1995 complete as required. | 1500.00 | Mtr |  | 75.00 | 112500.00 | 90.00 | 135000.00 | 112500.00 | Manish Electricals
11.00 | SH-II: Supply of Spares Supply of two pin Halogen lamps suitable for Runway/approach light fittings as below.
11.10 | 200 watts, 6.6 Amps, two pin Halogen lamp suitable for the Runway /Approach light fittings at Item No 1 | 30.00 | Nos |  | 580.00 | 17400.00 | 1000.00 | 30000.00 | 17400.00 | Manish Electricals
11.20 | 200 watts, 6.6 Amps, two pin Halogen lamp suitable for the existing youyang make Runway fittings (Make/Model:OSRAM-58750) | 50.00 | Nos |  | 900.00 | 45000.00 | 1000.00 | 50000.00 | 45000.00 | Manish Electricals
11.30 | 105 watts 6.6 Amps ,two pin Halogen lamp suitable for item no 3 &4. | 30.00 | Nos |  | 580.00 | 17400.00 | 1100.00 | 33000.00 | 17400.00 | Manish Electricals
12.00 | Supply of following capacity 5KV grade, 50 Hz series type isolating transformer conforming to relevant IS, encapsulated in polyster resin finally moulded with neoprene type rubber with primary & secondary connections as specified in particular specifications complete as required.
12.10 | 200Watts, 20A/6.6 Amps. | 30.00 | Nos |  | 4800.00 | 144000.00 | 4000.00 | 120000.00 | 120000.00 | vardhman Airport solutions pvt. Ltd.
12.20 | 15 Watts 20/6.6 Amps. | 20.00 | Nos |  | 2800.00 | 56000.00 | 2500.00 | 50000.00 | 50000.00 | vardhman Airport solutions pvt. Ltd.
12.30 | 15 Watts, 6.6/6.6 Amps. | 20.00 | Nos |  | 2800.00 | 56000.00 | 2500.00 | 50000.00 | 50000.00 | vardhman Airport solutions pvt. Ltd.
13.00 | Supply of following filters suitable for aviation ground lighting system for elevated high intensity runway fittings at item No 1 confirming to relevant IS as per specifications complete as required.
13.10 | 180 deg. Yellow Inner Right filter | 5.00 | Nos |  | 3000.00 | 15000.00 | 2500.00 | 12500.00 | 12500.00 | vardhman Airport solutions pvt. Ltd.
13.20 | 180 deg. Yellow Inner Left filter | 5.00 | Nos |  | 3000.00 | 15000.00 | 2500.00 | 12500.00 | 12500.00 | vardhman Airport solutions pvt. Ltd.
13.30 | 360 deg inner clear lence | 5.00 | Nos |  | 3000.00 | 15000.00 | 2500.00 | 12500.00 | 12500.00 | vardhman Airport solutions pvt. Ltd.
14.00 | Supply of suitable Spreader lenses for the item no2.
14.10 | Clear Lense( For Approach lights) | 5.00 | Nos |  | 3000.00 | 15000.00 | 2000.00 | 10000.00 | 10000.00 | vardhman Airport solutions pvt. Ltd.
14.20 | Green Lense( For Threshold lights) | 5.00 | Nos |  | 3000.00 | 15000.00 | 4000.00 | 20000.00 | 15000.00 | Manish Electricals
14.30 | Red Lense( For End lights) | 5.00 | Nos |  | 3000.00 | 15000.00 | 4000.00 | 20000.00 | 15000.00 | Manish Electricals
15.00 | Supply of O ring seal for Item No 3 & 4 | 10.00 | Nos |  | 3000.00 | 30000.00 | 600.00 | 6000.00 | 6000.00 | vardhman Airport solutions pvt. Ltd.
16.00 | Supply of Dummy Plate 10 mm Thickness, 330 mm Dia, Including provision of 6 nos, M10 tapped holes on top and 6 nos through holes at bottom to fix M10 bolts for fixing on existing C.I. Transformer house boxes etc complete as required. | 75.00 | Nos |  | 1200.00 | 90000.00 | 800.00 | 60000.00 | 60000.00 | vardhman Airport solutions pvt. Ltd.
17.00 | SH-III:Apron,Isolation bay flood lights Supply of following capacity LED flood light fixtures of efficacy minimum 110 lm/w,, CRI ≥ 70,THD ≤10, IP65 or higher, surge protection ≥ 4 kV, P.F ≥ 0.95, High pressure diecast aluminium /standard alloy housing, warranty period of 5 years from date of completion, total power consumption of not more than 110% of rated power, any of the following make of LED - Nichia/Cree/ Osram / Lumiled (Philips)/Sharp/Seoul/ Everlite/Citizen(Japan)/ Bridgelux (USA)/Samsung and complying to the technical specifications in the tender document.
17.10 | 50 W LED Flood Light luminaire, suitable for use at Airport Apron | 25.00 | Each |  | 2500.00 | 62500.00 | 2100.00 | 52500.00 | 52500.00 | vardhman Airport solutions pvt. Ltd.
17.20 | 150 watt LED Flood light luminaire, suitable for use at Airport Apron | 10.00 | Each |  | 4500.00 | 45000.00 | 5000.00 | 50000.00 | 45000.00 | Manish Electricals
17.30 | 300 watt LED Flood light luminaire, suitable for use at Airport Apron | 10.00 | Each |  | 15000.00 | 150000.00 | 13000.00 | 130000.00 | 130000.00 | vardhman Airport solutions pvt. Ltd.
17.40 | 500 watt LED Flood light luminaire, suitable for use at Airport Apron | 3.00 | Each |  | 20000.00 | 60000.00 | 24000.00 | 72000.00 | 60000.00 | Manish Electricals
18.00 | SH-IV:ITC of Fixtures Installation, testing & commissioning of Taxiway Light Fixtures on existing transformer housing boxes I/c installation of isolating transformers, lamps,etc. as required. | 10.00 | Each |  | 300.00 | 3000.00 | 100.00 | 1000.00 | 1000.00 | vardhman Airport solutions pvt. Ltd.
19.00 | Installation, testing and commisiong of following type fittings on the existing transformer housing boxes including installation of transformer, lens, lamps gasket,nut bolts, lens holding clamp and other accessories i/c alignment, levelling,isolating transformer, connection, earth connection etc.all complete.
19.10 | HIRL elevated type(RUNWAY.Threshold/END light) | 80.00 | Each |  | 200.00 | 16000.00 | 100.00 | 8000.00 | 8000.00 | vardhman Airport solutions pvt. Ltd.
19.20 | Elevated Approach Light Fittings | 40.00 | Each |  | 200.00 | 8000.00 | 100.00 | 4000.00 | 4000.00 | vardhman Airport solutions pvt. Ltd.
20.00 | Installation of transformer housing box with a base concrete of 1:3:6 of size 630 x 630 x 100mm thick, all round concrete of 1:2:4 150mm thick. The top sloped with 1:2:4 cement concrete including providing and fixing 10" long 15mm dia "B" class GI pipe with checknuts for drainage of water including excavation of side shoulder and re-filling as per Technical specifications (wherever the CI Transformer Housing Boxes are in a line, the same has to be aligned in such a way that the centers fall in a straight line) etc. complete as required. | 40.00 | Nos |  | 2500.00 | 100000.00 | 3000.00 | 120000.00 | 100000.00 | Manish Electricals
21.00 | Making field connections of by crimping of 16 sq mm size plug & receptable with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealant material applying PVC insulation tape etc. complete as required. | 20.00 | Nos |  | 200.00 | 4000.00 | 200.00 | 4000.00 | 4000.00 | vardhman Airport solutions pvt. Ltd., Manish Electricals
22.00 | Making field connections of by crimping of 6 sq mm size plug & receptable with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealant material applying PVC insulation tape etc. complete as required. | 50.00 | Nos |  | 200.00 | 10000.00 | 200.00 | 10000.00 | 10000.00 | vardhman Airport solutions pvt. Ltd., Manish Electricals
23.00 | Excavation for cable trenches by Mechanical/Hydraulic excavator of minimum depth 80cm and minimum width of 35cm in all kind of soil including getting out the excavated soil and Refilling of available excavated earth (excluding rock) in trenches after laying of cable/ pipe etc. and disposal of surplus excavated soil as directed within a lead of 50 metres. | 2284.00 | Mtr |  | 90.00 | 205560.00 | 100.00 | 228400.00 | 205560.00 | Manish Electricals
24.00 | Laying of 50mm (OD) size HDPE,PN4 grade, PE 63 HDPE pipe along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc. in the existing trench, complete as required. | 2175.00 | Mtr |  | 30.00 | 65250.00 | 100.00 | 217500.00 | 65250.00 | Manish Electricals
25.00 | Laying/Drawing of 2 run of 6 sqmm/16 AFL Cable in the existing HDPE/RCC/ HUME/ METAL pipe as required. | 2175.00 | Mtr |  | 30.00 | 65250.00 | 15.00 | 32625.00 | 32625.00 | vardhman Airport solutions pvt. Ltd.
26.00 | SH-V:EARTHING Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia medium class including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 20.00 | Each |  | 7500.00 | 150000.00 | 7000.00 | 140000.00 | 140000.00 | vardhman Airport solutions pvt. Ltd.
27.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe medium class from earth electrode including connection with G.I. thimble excavation and refilling. | 2175.00 | Mtr |  | 30.00 | 65250.00 | 230.00 | 500250.00 | 65250.00 | Manish Electricals
28.00 | SH-VI:SIGNAGES Design, Supply, installation, testing and commissioning of guidance sign boards of various sizes (as per annexure) made of anodised 2 mm thick aluminium frame with suitable angle support with 1.5 mm thick aluminium back cover and 4 mm thick transparent poly carbonate sheet with glare free face, the letter and symbols should be screen printed(inside of polycarbonate sheet) with required colouring, suitable arrangement shall be made to function on both main and standby (runway/taxiway) circuits with internal control circuits. suitable arrangements shall be made for water tightness and locking arrangements i/c. installations of isolating transformers, providing secondary leads, ESNA connectors. Suitable arrangements shall be made for water tightness and locking arrangement, sign boards shall be uniformly internally illuminated with required number of LED lights to achieve required illumination level, operated on input source of 2.5 A to 6.6 A constant current without any flickering, including its supporting legs, breakable coupling and base frame etc. complete as required as per ICAO. | 25.00 | Sqmtr |  | 35000.00 | 875000.00 | 39000.00 | 975000.00 | 875000.00 | Manish Electricals
29.00 | SH-VII:Civil Works Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including form work etc. as required as per the site condition. | 20.00 | Cum |  | 6500.00 | 130000.00 | 6000.00 | 120000.00 | 120000.00 | vardhman Airport solutions pvt. Ltd.
30.00 | Making of Masanory Chambers for Existing Earth pit of Size 1ftx1ft Including providing cover plate of 5mm thick MS Checkered plate. | 25.00 | Each |  | 700.00 | 17500.00 | 8000.00 | 200000.00 | 17500.00 | Manish Electricals
31.00 | Cutting & threading of Existing GI Pipe as per site requirement in order to meet with the slope of Existing CAT-1. | 40.00 | Job |  | 1500.00 | 60000.00 | 100.00 | 4000.00 | 4000.00 | vardhman Airport solutions pvt. Ltd.
32.00 | Core Cutting of Concrete wall of thickness 25cm(Approx.) and dia of 75/100 mm using core cutting machine including labour and materials etc. for crossing the OFC/RC/AFL Cables through storm water drain etc as per site condition. | 10.00 | Job |  | 1500.00 | 15000.00 | 1000.00 | 10000.00 | 10000.00 | vardhman Airport solutions pvt. Ltd.
33.00 | Taking GPS based co-ordinates by using total station and identifying the locations of light fixtures, route of cable etc based on GPS co-ordinates and marking, submission of reports / drawings etc. as required and as per directions of the Engineer In charge. Carry out Survey of CAT-1 Approach area for marking the center line. | 1.00 | Job |  | 250000.00 | 250000.00 | 100000.00 | 100000.00 | 100000.00 | vardhman Airport solutions pvt. Ltd.
34.00 | SH-VIII:Dismantling of Fixtures Dismantling of existing old elevated type Runway / Taxiway/Approach light fitting and handing over to AAI store complete as required. | 120.00 | Job |  | 200.00 | 24000.00 | 50.00 | 6000.00 | 6000.00 | vardhman Airport solutions pvt. Ltd.
35.00 | SH-IX: Photometric field test for Existing GLF fittings Carrying out and Making in-field measurement of intensity, beam spread, orientation, chromaticity, luminous factor, one time field alignment setting for inset,elevated type approach, elevated type runway edge, elevated type threshold, PAPI airfields ground lights by using vehicle mounted mobile testing equipment system, frame reader and submission of phtometric test reports etc as per requirement of ICAO / DGCA requirement etc. complete as required as per technical specifications for GLF installations of Hubballi Airport. | 1.00 | Job |  | 350000.00 | 350000.00 | 200000.00 | 200000.00 | 200000.00 | vardhman Airport solutions pvt. Ltd.
| Total in Figures |  |  |  |  | 5921050.00 |  | 6126715.00
Lowest Amount Quoted BY: Manish Electricals(5921050.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of GLF Facilities at Hubballi Airport Tender ID: 2024_AAI_212372_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals (BID ID -779679) | 5921050.00 | L1
| 2 | vardhman Airport solutions pvt. Ltd. (BID ID -778608) | 6126715.00 | L2