## BoQ1
Government eProcurement System Created By: Arun Raj N Created Date/Time: 15-Jan-2025 05:02 PM Tender Title: Provision of Airfield Lighting control and monitoring system ALCMS at new ATC cum Technical building at Tuticorin Airport Tender ID: 2024_AAI_213734_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
NAME OF WORK: Development of Tuticorin Airport: Extension of Runway with blast pad, RESA, taxiway, Apron, GSE Area, Isolation Bay, New Domestic Terminal Building and Miscellaneous work. SH: Providing Airfield Lighting Control and Monitoring System (ALCMS) at new ATC cum Technical Building at Tuticorin Airport.
Tender ID - 2024_AAI_213734_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NASU SYSTEMS (GSTN-27ABAPS2566G1ZK) BID ID -774318 |  | vardhman Airport solutions pvt. Ltd. (GSTN-NA) BID ID -778079
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I SITC of ALCMS Design, supply, installation, testing & commissioning of Airfield Lighting Control & Monitoring System(ALCMS),HMI, Type 'L 890 BB' to the requirements of FAA Advisory Circular No. AC 150/5345 - 56B(Current edition) and additional circuits/mechanisms/interfaces for control & monitoring of constant current regulators (CCRs) & fixed circuits such as Landing - H, Wind cone, and control of flood light towers & isolation bay flood light & beacon from tower to make them compatible with ALCMS, data & power cabling, earthing etc., including spare PLC and I/O modules, all hardware and software, licenses & other items as required for successful operation of the system in line with the scope of work, details of equipments, equipments specification, performance criteria etc., complete as required. Two Vault processors shall be provided both running in parallel for redundancy in operation,earthing and cable termination provision of SPD, Media converter etc., complete as required. | 1.00 | Job |  | 2000000.00 | 2000000.00 | 2700000.00 | 2700000.00 | 2000000.00 | NASU SYSTEMS
2.00 | SH II Supply and Laying of OFC cable Supply of Single mode 6 core, armoured Optic Fibre Cable (OFC) conforming to ITU-T G.652 and IEC- 60794 with up to date amendments, etc., complete as required. | 1600.00 | Mtr |  | 75.00 | 120000.00 | 40.00 | 64000.00 | 64000.00 | vardhman Airport solutions pvt. Ltd.
3.00 | Laying of Single mode 6 core, armoured Optic Fibre Cable (OFC) conforming to ITU-T G.652 and IEC- 60794 with up to date amendments, etc., complete as required in existing pipe. | 1350.00 | Mtr |  | 20.00 | 27000.00 | 15.00 | 20250.00 | 20250.00 | vardhman Airport solutions pvt. Ltd.
4.00 | Laying of Single mode 6 core, armoured Optic Fibre Cable (OFC) conforming to ITU-T G.652 and IEC- 60794 with up to date amendments, etc., inside the trenches/ duct/ surface including providing and laying of medium class PVC conduit with mounting clamps etc., complete as required. | 250.00 | Mtr |  | 80.00 | 20000.00 | 15.00 | 3750.00 | 3750.00 | vardhman Airport solutions pvt. Ltd.
5.00 | Supplying and laying of 40 mm size PN 6, PE 63 HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 complete with fitting and cutting, jointing etc.in the direct in ground (75 cm below ground level ) including excavation and refilling the trench complete as required. | 300.00 | Mtr |  | 280.00 | 84000.00 | 175.00 | 52500.00 | 52500.00 | vardhman Airport solutions pvt. Ltd.
6.00 | Supplying and laying of 40mm size PN6,PE 63 HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 complete with fitting and cutting, jointing etc. in the existing trench/hume pipe, complete as required. | 1350.00 | Mtr |  | 110.00 | 148500.00 | 140.00 | 189000.00 | 148500.00 | NASU SYSTEMS
7.00 | Supply of multi-core armoured cable with solid copper conductor cable, XLPE insulated, PVC inner sheathed, armoured of GI steel strip of 1.1 kV grade confirming to IS: 7098 (Pt-1) 24 core x 1.5 sq.mm | 700.00 | Mtr |  | 520.00 | 364000.00 | 550.00 | 385000.00 | 364000.00 | NASU SYSTEMS
8.00 | Supply of multi-core armoured cable with solid copper conductor cable, XLPE insulated, PVC inner sheathed, armoured of GI steel strip of 1.1 kV grade confirming to IS: 7098 (Pt-1) 10core x 1.5 sq.mm | 500.00 | Mtr |  | 208.00 | 104000.00 | 270.00 | 135000.00 | 104000.00 | NASU SYSTEMS
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE control cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. Up to 35 sq.mm | 550.00 | Mtr |  | 50.00 | 27500.00 | 20.00 | 11000.00 | 11000.00 | vardhman Airport solutions pvt. Ltd.
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size in the existing masonry open duct as required. Up to 35 sq.mm | 500.00 | Mtr |  | 40.00 | 20000.00 | 15.00 | 7500.00 | 7500.00 | vardhman Airport solutions pvt. Ltd.
11.00 | Providing and laying of 150mm dia B class G.I pipe below 0.75 mtr, across road including cutting bituminous road and excavation of soil ,refilling with concrete to the original finish etc. complete as required. | 24.00 | Mtr |  | 2400.00 | 57600.00 | 2700.00 | 64800.00 | 57600.00 | NASU SYSTEMS
12.00 | Supplying and making end termination with brass compression gland copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required. 24core x 1.5 sq.mm (28mm) | 5.00 | Job |  | 500.00 | 2500.00 | 900.00 | 4500.00 | 2500.00 | NASU SYSTEMS
13.00 | Supplying and making end termination with brass compression gland copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required. 10core x 1.5 sq.mm (25mm) | 50.00 | Job |  | 150.00 | 7500.00 | 430.00 | 21500.00 | 7500.00 | NASU SYSTEMS
14.00 | Termination of Single mode 6 core, armoured optic fibre cable (OFC) with suitable accessories pigtail and other accessories complete as required. | 4.00 | Job |  | 3000.00 | 12000.00 | 2200.00 | 8800.00 | 8800.00 | vardhman Airport solutions pvt. Ltd.
15.00 | SH III SPARES Suppy of essential spares for the ALCMS Terminal base of PLC for I/O module. | 1.00 | Each |  | 50.00 | 50.00 | 5500.00 | 5500.00 | 50.00 | NASU SYSTEMS
16.00 | Expansion unit for connecting I/O module. | 1.00 | Each |  | 50.00 | 50.00 | 50000.00 | 50000.00 | 50.00 | NASU SYSTEMS
17.00 | Supply of network adopter power supply | 1.00 | Each |  | 1500.00 | 1500.00 | 5000.00 | 5000.00 | 1500.00 | NASU SYSTEMS
18.00 | Supply of UPS battery, 65Ah, 12VDC | 1.00 | Each |  | 6000.00 | 6000.00 | 12000.00 | 12000.00 | 6000.00 | NASU SYSTEMS
19.00 | Supply of ALCMS Interface Module for CCR | 1.00 | Each |  | 50.00 | 50.00 | 12000.00 | 12000.00 | 50.00 | NASU SYSTEMS
20.00 | Supply of ALCMS Interface Module for fixed circuit. | 1.00 | Each |  | 3000.00 | 3000.00 | 12000.00 | 12000.00 | 3000.00 | NASU SYSTEMS
21.00 | Supply of Power Supply for vault processor | 1.00 | Each |  | 1500.00 | 1500.00 | 8500.00 | 8500.00 | 1500.00 | NASU SYSTEMS
22.00 | SH IV CMC ALL INCLUSIVE COMPREHENSIVE MAINTENANCE CONTRACT for complete ALCMS CMC (Comprehensive Maintenance Contract) for 5 years after ONE year DLP (Defect Liability Period) with year wise breakup for the entire installation. Year 1 - (5 % of SITC cost including freight, insurance and transportation of SH-I) | 1.00 | Job |  | 100000.00 | 100000.00 | 135000.00 | 135000.00 | 100000.00 | NASU SYSTEMS
23.00 | Year 2 - ( Yearly 6 % cumulative enhancement on first year cost shall be applicable for the second year.) | 1.00 | Job |  | 106000.00 | 106000.00 | 143100.00 | 143100.00 | 106000.00 | NASU SYSTEMS
24.00 | Year 3 - ( Yearly 6% cumulative enhancement on second year cost shall be applicable for the third year.) | 1.00 | Job |  | 112360.00 | 112360.00 | 151686.00 | 151686.00 | 112360.00 | NASU SYSTEMS
25.00 | Year 4 - ( Yearly 6 % cumulative enhancement on third year cost shall be applicable for the fourth year.) | 1.00 | Job |  | 119101.60 | 119101.60 | 160787.16 | 160787.16 | 119101.60 | NASU SYSTEMS
26.00 | Year 5 - ( Yearly 6 % cumulative enhancement on fourth year cost shall be applicable for the fifth year.) | 1.00 | Job |  | 126247.70 | 126247.70 | 170434.39 | 170434.39 | 126247.70 | NASU SYSTEMS
| Total in Figures |  |  |  |  | 3570459.30 |  | 4533607.55
Lowest Amount Quoted BY: NASU SYSTEMS(3570459.30)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Airfield Lighting control and monitoring system ALCMS at new ATC cum Technical building at Tuticorin Airport Tender ID: 2024_AAI_213734_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NASU SYSTEMS (BID ID -774318) | 3570459.30 | L1
| 2 | vardhman Airport solutions pvt. Ltd. (BID ID -778079) | 4533607.55 | L2