## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 27-Dec-2024 06:26 PM Tender Title: Provision of VRF/VRV type AC system in Arrival Area in Bagdogra Airport along with AICMC for 05 Years.(After 02 years of DLP). Tender ID: 2024_AAI_214505_1
Tender Inviting Authority: AGM (E-E)
Name of Work: Provision of VRF/VRV type AC system in Arrival Area in Bagdogra Airport along with AICMC for 05 Years.(After 02 years of DLP).
Contract No: 2024_AAI_214505_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CAC ENGINEERS PVT LTD (GSTN-33AAECC2301D2ZK) BID ID -778154 |  | Utility Services (GSTN-06AABFU8051C1ZG) BID ID -780497
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of variable Refrigerant Flow modular type air conditioning system complete with indoor & outdoor units with individual cordless controller as per the following capacities of the IDU and ODU.
1.10 | Supply, Installation,Testing & Commissioning of modular type Variable Refrigerant Flow air cooled Outdoor units suitable for cooling, having all hermetically sealed inverter type Scroll Compressor(s), microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators, with suitable concreate foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 53°C ambient temperature without tripping. The unit shall be suitable to work on 415V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.8 The capacity of VRF/VRV unit is minimum 300 HP (ODU to be supplied in multiple of VRF/ VRV units, maximum upto 3 type unit sizes). | 1.00 | Job | 5090000.00 | 4467600.00 | 4467600.00 | 3788843.00 | 3788843.00 | 3788843.00 | Utility Services
1.20 | Supply, installation, testing and commissioning of minimum 4 TR capacity 4-way flow VRF Cassette Type Indoor ceiling mounted Indoor unit equipped with fan section with low noise fan / dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cord less remote control, drain pan, necessary accessories etc., suitable for operation on 230 V ± 10%, 50 Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | 47.00 | Each | 47565.00 | 31907.40 | 1499647.80 | 31910.00 | 1499770.00 | 1499647.80 | CAC ENGINEERS PVT LTD
1.30 | Supply,installation, testing and comminssioning of High Static Ductable Indoor units of minimum 8.0 TR capacity and external static pressure VRF/VRV celing mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve,corded remote control,outer cabinet,vibration isolators,drain pipe,other necessary supports etc. suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shutdown provision in case of fire on receiving signal from BMS system. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | 9.00 | Each | 62790.00 | 69371.50 | 624343.50 | 70311.00 | 632799.00 | 624343.50 | CAC ENGINEERS PVT LTD
2.00 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing among following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with Nitrile Rubber Class-O tubular insulation/with Class-O closed cell elastomeric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc.as applicable for the system :
2.01 | 9-11 mm dia (OD) (Soft drawn) with 19 mm thick insulation | 250.00 | Metre | 560.00 | 376.95 | 94237.50 | 609.00 | 152250.00 | 94237.50 | CAC ENGINEERS PVT LTD
2.02 | 12-13 mm dia (OD) (Soft drawn) mm with 19 mm thick insulation | 80.00 | Metre | 670.00 | 770.70 | 61656.00 | 786.00 | 62880.00 | 61656.00 | CAC ENGINEERS PVT LTD
2.03 | 14-16 mm dia (OD) (Soft drawn) with 19 mm thick insulation | 300.00 | Metre | 850.00 | 641.55 | 192465.00 | 965.00 | 289500.00 | 192465.00 | CAC ENGINEERS PVT LTD
2.04 | 17-20 mm dia (OD) (Hard drawn)mm with 19 mm thick insulation | 350.00 | Metre | 1050.00 | 770.70 | 269745.00 | 1204.00 | 421400.00 | 269745.00 | CAC ENGINEERS PVT LTD
2.05 | 21-23 mm dia (OD) (Hard drawn) with 19 mm thick insulation | 120.00 | Metre | 1080.00 | 900.90 | 108108.00 | 1389.00 | 166680.00 | 108108.00 | CAC ENGINEERS PVT LTD
2.06 | 24-26 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 150.00 | Metre | 1120.00 | 945.00 | 141750.00 | 1570.00 | 235500.00 | 141750.00 | CAC ENGINEERS PVT LTD
2.07 | 27-29 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 250.00 | Metre | 1250.00 | 1177.05 | 294262.50 | 1769.00 | 442250.00 | 294262.50 | CAC ENGINEERS PVT LTD
2.08 | 30-32 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 70.00 | Metre | 1450.00 | 1279.95 | 89596.50 | 2446.00 | 171220.00 | 89596.50 | CAC ENGINEERS PVT LTD
2.09 | 33-35 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 30.00 | Metre | 1750.00 | 1873.20 | 56196.00 | 2693.00 | 80790.00 | 56196.00 | CAC ENGINEERS PVT LTD
2.10 | 36-39 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 100.00 | Metre | 1932.00 | 1950.00 | 195000.00 | 2950.00 | 295000.00 | 195000.00 | CAC ENGINEERS PVT LTD
2.11 | 40-42 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 90.00 | Metre | 2105.00 | 2211.30 | 199017.00 | 3204.00 | 288360.00 | 199017.00 | CAC ENGINEERS PVT LTD
2.12 | 43-45 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 90.00 | Metre | 2266.00 | 2225.00 | 200250.00 | 3459.00 | 311310.00 | 200250.00 | CAC ENGINEERS PVT LTD
2.13 | 46-55 mm dia (OD) (Hard drawn) with tube thickness 1.6 mm with 19 mm thick insulation | 150.00 | Metre | 2392.00 | 1976.25 | 296437.50 | 4111.00 | 616650.00 | 296437.50 | CAC ENGINEERS PVT LTD
3.00 | Supply, Installation, Testing and Commissioning of Refnet Joints & Branch Distributors for Indoor & Outdoor units as applicable to the system design as per OEM recommendation. | 56.00 | Each | 6500.00 | 3500.00 | 196000.00 | 2843.00 | 159208.00 | 159208.00 | Utility Services
4.00 | Providing & fixing rigid UPVC piping complete with fittings, supports as per specifications and pre insulated with 6mm thick closed cell elastomeric nitrile rubber tubular thermal insulation.
4.10 | 25 MM Dia | 350.00 | Metre | 210.00 | 250.00 | 87500.00 | 207.00 | 72450.00 | 72450.00 | Utility Services
4.20 | 32 MM Dia | 250.00 | Metre | 240.00 | 350.00 | 87500.00 | 259.00 | 64750.00 | 64750.00 | Utility Services
4.30 | Ducting
5.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per OEM standards as per approved drawings and specifications of following sheet thickness complete as required.
5.10 | 24 G (Thickness 0.63 mm sheet) | 120.00 | Sq. mtr | 1035.00 | 800.00 | 96000.00 | 1031.00 | 123720.00 | 96000.00 | CAC ENGINEERS PVT LTD
5.20 | Grillers/Diffuser
6.00 | Supply,installation, testing and comminssioning of grilles/diffuser as per specification and drawing.
6.10 | Aluminium supply air jet diffuser | 27.00 | Nos | 3890.00 | 3000.00 | 81000.00 | 2998.00 | 80946.00 | 80946.00 | Utility Services
7.00 | Supplying and drawing 3C x 0.75 Sqmm FRLS PVC shielded copper in the existing surface/ recessed steel/ PVC conduit as required. | 2000.00 | Mtr. | 165.00 | 110.00 | 220000.00 | 106.00 | 212000.00 | 212000.00 | Utility Services
8.00 | Supplying and drawing 3C x 1.5 sqmm of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | 2000.00 | Mtr. | 88.00 | 86.25 | 172500.00 | 144.00 | 288000.00 | 172500.00 | CAC ENGINEERS PVT LTD
9.00 | Supplying and fixing of 25 mm size of Steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. | 2000.00 | Mtr. | 334.00 | 92.00 | 184000.00 | 208.00 | 416000.00 | 184000.00 | CAC ENGINEERS PVT LTD
10.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cable as required. | 500.00 | Mtr. | 36.00 | 38.50 | 19250.00 | 43.00 | 21500.00 | 19250.00 | CAC ENGINEERS PVT LTD
11.00 | Supply of 4 CORE 35 sq.mm. XLPE insulated and PVC sheathed FRLS aluminium conductor armoured Power Cable of 1.1KV grade, confirming to IS 7098, Part-I 1988 with up to date amendments and confirming to technical specifications. | 200.00 | Mtr. | 507.00 | 402.50 | 80500.00 | 552.00 | 110400.00 | 80500.00 | CAC ENGINEERS PVT LTD
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 200.00 | Mtr. | 49.00 | 38.50 | 7700.00 | 189.00 | 37800.00 | 7700.00 | CAC ENGINEERS PVT LTD
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
13.10 | a) 4 X 35 sq. mm (32mm) | 4.00 | Set | 445.00 | 450.00 | 1800.00 | 291.00 | 1164.00 | 1164.00 | Utility Services
14.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
14.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 350.00 | Meter | 780.00 | 858.00 | 300300.00 | 591.00 | 206850.00 | 206850.00 | Utility Services
14.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 500.00 | Meter | 1300.00 | 1210.00 | 605000.00 | 808.00 | 404000.00 | 404000.00 | Utility Services
15.00 | Refrigerant-410a Supply , charging & Leakage testing of refrigerant - 410a in additional copper piping circuit. | 150.00 | Kg | 900.00 | 900.00 | 135000.00 | 935.00 | 140250.00 | 135000.00 | CAC ENGINEERS PVT LTD
16.00 | Lifting/lowering & shifting of ODUs & IDUs as per site requirement. | 1.00 | Job | 120000.00 | 25000.00 | 25000.00 | 114450.00 | 114450.00 | 25000.00 | CAC ENGINEERS PVT LTD
17.00 | Supplying and fixing 12 way double door, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB / RCCB / Isolator) | 3.00 | Job | 2202.00 | 2750.00 | 8250.00 | 1780.00 | 5340.00 | 5340.00 | Utility Services
18.00 | Supplying and fixing of following ways surface/ recess mounting, Horizontal type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’/MCCB ) as required .
18.10 | 8 way (4 + 24), Double door, suitable for MCCB Incoming | 1.00 | Job | 6134.00 | 2625.00 | 2625.00 | 6773.00 | 6773.00 | 2625.00 | CAC ENGINEERS PVT LTD
19.00 | Supplying and fixing of follwoing rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
19.10 | Single pole (5 amps to 32 amps) | 48.00 | Each | 267.00 | 165.00 | 7920.00 | 225.00 | 10800.00 | 7920.00 | CAC ENGINEERS PVT LTD
19.20 | Double Pole, 63 Amp | 3.00 | Each | 1158.00 | 3850.00 | 11550.00 | 941.00 | 2823.00 | 2823.00 | Utility Services
19.30 | Triple pole (5 amps to 32 amps) | 2.00 | Each | 1089.00 | 192.50 | 385.00 | 1800.00 | 3600.00 | 385.00 | CAC ENGINEERS PVT LTD
19.40 | Triple pole and neutral (63 Amps) | 2.00 | Each | 2052.00 | 3850.00 | 7700.00 | 2743.00 | 5486.00 | 5486.00 | Utility Services
20.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. a) Blanking plate | 2.00 | Job | 25.00 | 100.00 | 200.00 | 745.00 | 1490.00 | 200.00 | CAC ENGINEERS PVT LTD
21.00 | Supply and fixing of 1 Mtr Air curtain along with sensor at Bagdogra Airport as per technical specification. | 10.00 | Job | 15719.00 | 19500.00 | 195000.00 | 32436.00 | 324360.00 | 195000.00 | CAC ENGINEERS PVT LTD
22.00 | Supply and fixing of 1.2 Mtr Air curtain at Bagdogra Airport as per technical specification. | 9.00 | Job | 17165.00 | 21500.00 | 193500.00 | 35711.00 | 321399.00 | 193500.00 | CAC ENGINEERS PVT LTD
23.00 | SITC of outdoor PTTA type LT Panel, made out of 14 SWG CRCA sheet steel double door, totally enclosed, IP-55, protection free standing, floor mounting, dust and vermin proof, compartmentalized, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with bus bars extensible on both sides, entire panel shall have a common Copper earth bus bar of size 25 mm x 6 mm at the rear with 2 Nos. earth stud, interconnections with suitable size of copper leads/ solid aluminium strips. (Panel shall conform to IEC 60439 & of Form-4b construction).
23.01 | Incomer:
23.02 | 02 No. MCCB LISG type, 400 Amps, 4 pole, 35 kA (Ics=100% Icu) with adjustable setting, microprocessor release with O/C & S/C protection with simultaneous double break mechanism & total break time less than equal to 10ms with Spreader terminal of both side
23.03 | Bus Coupler:
23.04 | 01 No. MCCB LISG type, 400 Amps, 4 pole, 35 kA (Ics=100% Icu) with adjustable setting, microprocessor release with O/C & S/C protection with simultaneous double break mechanism & total break time less than equal to 10ms with Spreader terminal of both side as Bus Coupler
23.05 | Busbars:
23.06 | 4P aluminum bus bars of minimum 600 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec.
23.07 | Instruments & accessories:
23.08 | 2 No. 96 mm x 96 mm digital type Voltmeter suitable range for 3phase,4 wire operation with LED display and selector switch backup by 3 nos of 2Amp MCB.
23.09 | 2 No.96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch and CT's
23.10 | 2 Set of LED type phase indicating lamps (RYB) and 3 set LED type Indicating lamps for ON-OFF controlled by 2Amp MCBs .
23.11 | 4 Pole SPD's of type 2 class C with both the Incomer.
23.12 | 3 Set Rotary operating mechanism and terminal extension spreaders with door interlock for all the MCCB's.
23.13 | Mechanical & Electrical Interlocking system for Incomer & Bus Coupler.
23.14 | Outgoing:
23.15 | 06 Nos MCCB(Ics=100% Icu), 100 Amps, 4 Pole, min 25 kA with adjustable setting , Thermal Magnetic release shall have Variable Thermal (O/L) & Variable Magnetic (S/C) protection,including connections etc as required with LED type ON-OFF Indicating lamp controlled by 2Amp MCBs . | 1.00 | Job | 212100.00 | 575000.00 | 575000.00 | 431182.00 | 431182.00 | 431182.00 | Utility Services
24.00 | SITC of Indoor TTA type LT Panel, made out of 14 SWG CRCA sheet steel double door, totally enclosed, IP-55, protection free standing, floor mounting, dust and vermin proof, compartmentalized, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with bus bars extensible on both sides, entire panel shall have a common Copper earth bus bar of size 25 mm x 6 mm at the rear with 2 Nos. earth stud, interconnections with suitable size of copper leads/ solid aluminium strips. (Panel shall conform to IEC 61439 -1&2 & of Form-4b construction).
24.01 | Incomer:
24.02 | 02 No. MCCB LISG type, 630 Amps, 4 pole, 50 kA (Ics=100% Icu) with adjustable setting, microprocessor release with O/C & S/C protection with simultaneous double break mechanism & total break time less than equal to 10ms with Spreader terminal of both side .
24.03 | Bus Coupler:
24.04 | 01 No. MCCB, LISG type, 630 Amps, 4 pole, 50 kA (Ics=100% Icu) with adjustable setting, microprocessor release with O/C & S/C protection with simultaneous double break mechanism & total break time less than equal to 10ms with Spreader terminal of both side as Bus Coupler
24.05 | Busbars:
24.06 | 4P aluminum bus bars of minimum 1000 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 36 KA for 1 sec.
24.07 | Instruments & accessories:
24.08 | 2 No. 96 mm x 96 mm digital type Voltmeter suitable range for 3phase,4 wire operation with LED display and selector switch backup by 3 nos of 2Amp MCB.
24.09 | 2 No.96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch and CT's
24.10 | 2 Set of LED type phase indicating lamps (RYB) and 3 set LED type Indicating lamps for ON-OFF controlled by 2Amp MCBs .
24.11 | 4 Pole SPD's of type 2 class C with both the Incomer.
24.12 | 3 Set Rotary operating mechanism and terminal extension spreaders with door interlock for all the MCCB's.
24.13 | Mechanical & Electrical Interlocking system for Incomer & Bus Coupler.
24.14 | Outgoing:
24.15 | (i) 02 Nos MCCB(Ics=100% Icu) each for 500 Amps,400Amps,250 Amps & 125 Amps each having 4 Pole, min 36 kA,(Total 08 nos of MCCB) with adjustable setting , Thermal Magnetic release shall have Variable Thermal (O/L) & Variable Magnetic (S/C) protection, including connections etc as required with LED type ON-OFF Indicating lamp controlled by 2Amp MCBs. | 1.00 | Job | 606000.00 | 475000.00 | 475000.00 | 837388.00 | 837388.00 | 475000.00 | CAC ENGINEERS PVT LTD
25.00 | SITC of outdoor type totally enclosed double door junction box having IP-55 protection, made out of 14 SWG CRCA sheet steel ,free standing, floor mounting with angle supports, dust and vermin proof, powder coated painting includes 4P aluminum bus bars of minimum 200 A capacity with heat shrinkable coloured sleeves i/c SMC/DMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. Provision of 04 nos. 4P, 63 amp MCB should there as outgoing, interconnected with bus bar with 10 sq.mm size copper leads suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with 2 Nos. earth stud, etc complete as required. | 4.00 | Job | 15150.00 | 55000.00 | 220000.00 | 21324.00 | 85296.00 | 85296.00 | Utility Services
26.00 | To execute the work opening and closing of desired number of existing 2X2 mettalic false celing and cutting of false celing to fix cassete IDUs. All the false celing need to be fixed with professional civil man power as required suitable as per site requirement. | 1.00 | Job | 150000.00 | 25000.00 | 25000.00 | 134479.00 | 134479.00 | 25000.00 | CAC ENGINEERS PVT LTD
27.00 | Supply of 3.5 core x 300 sqmm XLPE insulated and PVC sheathed aluminium conductor armoured Power Cable of 1.1KV grade, confirming to IS 7098, Part-I 1988 with up to date amendments and confirming to technical specifications.(The outer sheath shall be FRLS.) | 450.00 | Meter | 3191.00 | 990.00 | 445500.00 | 2667.00 | 1200150.00 | 445500.00 | CAC ENGINEERS PVT LTD
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) on wall surface as required. | 400.00 | Meter | 198.00 | 150.00 | 60000.00 | 309.00 | 123600.00 | 60000.00 | CAC ENGINEERS PVT LTD
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 185 sq. mm and upto 400 sq. mm in the existing RCC/ HUME/DUCT/ METAL pipe as required | 50.00 | Meter | 16.00 | 150.00 | 7500.00 | 298.00 | 14900.00 | 7500.00 | CAC ENGINEERS PVT LTD
30.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 core x 300 sqmm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Set | 1818.00 | 1500.00 | 6000.00 | 1195.00 | 4780.00 | 4780.00 | Utility Services
31.00 | Supplying and drawing of 3 x 10 sq.mm size FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | 100.00 | Meter | 1828.00 | 345.00 | 34500.00 | 834.00 | 83400.00 | 34500.00 | CAC ENGINEERS PVT LTD
32.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3.5C x 300 sq.mm. size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 1.00 | Set | 2816.00 | 3675.00 | 3675.00 | 3937.00 | 3937.00 | 3675.00 | CAC ENGINEERS PVT LTD
33.00 | Providing and fixing of 4Pole, 630A, 36 KA MCCB with adjustable setting, microprocessor release with O/C & S/C protection along with rotary handle in the existing cubicle panel boards (i/c. neessary modification) including suitable size bus bar arrangements, drilling holes in cubicle panel with providing digital KWH Meter with maximum demand load and current display RS485 module of class-0.5 accuracy with suitable range of cast resin CT including making connections etc as required. 3 Nos of LED type phase indicating lamps (RYB) controlled by 2Amp MCB should be provided in panel board compartment. | 2.00 | Set | 60600.00 | 140000.00 | 280000.00 | 96405.00 | 192810.00 | 192810.00 | Utility Services
34.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Meter | 197.00 | 150.00 | 7500.00 | 124.00 | 6200.00 | 6200.00 | Utility Services
35.00 | Providing & fixing in position 3mm thick Aluminum composite panels in external face, column / wall cladding and canopy ceiling of approved make comprising virgin polyethylene core sandwiched between two skins of 0.25mm thick. Fixing of surface cladding to masonry / concrete faces / steel structure as called for (straight/slope and curvilinear profile and shapes),including all required aluminium frame and supporting items fixed on appropriate and adequate frame work of aluminium tubular sections/round/hinges etc including all accessories and all incidental work. The cladding shall be done in accordance with the drawings, fixed to sides and faces of columns/ piers, to sills and soffits of window opening, returned over coping, to RCC / structureal steel system, etc, to line and level. The joints shall be properly sealed with approved silicon sealant to make the joints wateright and weather proof includding, fixing over aluminum frame using mechaical fasteners such as Aluminum cleats and stainless steel fasteners all complete as approved by the Engineer-in-charge. The colour of ACP will be approved by EIC. The work shall be completed as per specification and directions of Engineer-in-charge. | 250.00 | Sq Mtr | 3103.00 | 1200.00 | 300000.00 | 2771.00 | 692750.00 | 300000.00 | CAC ENGINEERS PVT LTD
36.00 | All Inclusive Comprehensive Maintenance Conrtract (AICMC) of above VRF/VRV AC System for 5 years (after defect liability period of 2 years) as per the direction of EIC complete as required.
36.10 | Year -1 (5.37 % of SITC cost) | 1.00 | Job | 969600.00 | 749446.18 | 749446.18 | 880767.69 | 880767.69 | 749446.18 | CAC ENGINEERS PVT LTD
36.20 | Year -2 (5.00% cumulative enhancement on Year - 1 AICMC cost) | 1.00 | Job | 1018080.00 | 786918.49 | 786918.49 | 924806.08 | 924806.08 | 786918.49 | CAC ENGINEERS PVT LTD
36.30 | Year- 3 (5.00% cumulative enhancement on Year - 2 AICMC cost) | 1.00 | Job | 1068984.00 | 826264.42 | 826264.42 | 971046.38 | 971046.38 | 826264.42 | CAC ENGINEERS PVT LTD
36.40 | Year -4 (5.00% cumulative enhancement on Year - 3 AICMC cost) | 1.00 | Job | 1122433.00 | 867577.64 | 867577.64 | 1019598.70 | 1019598.70 | 867577.64 | CAC ENGINEERS PVT LTD
36.50 | Year -5 (5.00% cumulative enhancement on Year - 4 AICMC cost) | 1.00 | Job | 1178555.00 | 910956.52 | 910956.52 | 1070578.63 | 1070578.63 | 910956.52 | CAC ENGINEERS PVT LTD
| Total in Figures |  |  |  |  | 18097330.55 |  | 21268430.48
Lowest Amount Quoted BY: CAC ENGINEERS PVT LTD(18097330.55)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of VRF/VRV type AC system in Arrival Area in Bagdogra Airport along with AICMC for 05 Years.(After 02 years of DLP). Tender ID: 2024_AAI_214505_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CAC ENGINEERS PVT LTD (BID ID -778154) | 18097330.55 | L1
| 2 | Utility Services (BID ID -780497) | 21268430.48 | L2