## BoQ1
Government eProcurement System Created By: Shridhar Gupta Created Date/Time: 26-Dec-2024 03:43 PM Tender Title: Provision of UPS power supply system for IT equipments and miscellaneous electrical works Tender ID: 2024_AAI_217164_1
Tender Inviting Authority: AGM (Engg-Elect), AAI, Patna Airport, Patna.
Name of Work: Construction of New Domestic Terminal Building and Other Structures (Phase I & II) at Patna Airport. Sub-Head : Provision of UPS Power supply system for IT equipments and miscellenous electrical works.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -793025 |  | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -793642 |  | EVERCREST PROJECTS PVT LTD (GSTN-24AADCE7826L1ZE) BID ID -793930 |  | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -794436 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -793482
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Supply of following sizes of Aluminium / copper Power Cables, multi stranded conductor, XLPE Insulated, cores laid up, PVC tape/ Extruded Inner sheathed, Un Armour or Armour, FRLS at outer sheathed, 1100 V grade as per IS 7098 (Part 1) 1988. 4 CORE 16 sq.mm. CU Armoured XLPE cable | 7600.00 | Mtr | 2719420.00 | 689.00 | 5236400.00 | 748.00 | 5684800.00 | 897.00 | 6817200.00 | 810.00 | 6156000.00 | 675.00 | 5130000.00 | 5130000.00 | SAURABH ENTERPRISES
1.20 | 4 CORE 10 sq.mm. CU Armoured XLPE cable | 10300.00 | Mtr | 3074740.00 | 444.00 | 4573200.00 | 485.00 | 4995500.00 | 588.00 | 6056400.00 | 520.00 | 5356000.00 | 470.00 | 4841000.00 | 4573200.00 | DOSHI ELECTRIC ENGG. CO.
1.30 | 3 CORE 2.5 sq.mm. CU Armoured XLPE cable | 18500.00 | Mtr | 3074740.00 | 114.00 | 2109000.00 | 150.00 | 2775000.00 | 143.00 | 2645500.00 | 150.00 | 2775000.00 | 247.00 | 4569500.00 | 2109000.00 | DOSHI ELECTRIC ENGG. CO.
1.40 | 1 CORE 300 sq.mm. CU Armoured XLPE cable | 1200.00 | Mtr | 3074740.00 | 3190.00 | 3828000.00 | 4000.00 | 4800000.00 | 4564.00 | 5476800.00 | 3700.00 | 4440000.00 | 2900.00 | 3480000.00 | 3480000.00 | SAURABH ENTERPRISES
1.50 | 1 CORE 300 sq.mm. CU Unarmoured XLPE cable | 360.00 | Mtr | 3074740.00 | 2920.00 | 1051200.00 | 4000.00 | 1440000.00 | 4278.00 | 1540080.00 | 4700.00 | 1692000.00 | 3080.00 | 1108800.00 | 1051200.00 | DOSHI ELECTRIC ENGG. CO.
2.10 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 36400.00 | Mtr | 516.00 | 15.00 | 546000.00 | 30.00 | 1092000.00 | 28.00 | 1019200.00 | 59.00 | 2147600.00 | 10.00 | 364000.00 | 364000.00 | SAURABH ENTERPRISES
2.20 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 1560.00 | Mtr | 273.00 | 60.00 | 93600.00 | 150.00 | 234000.00 | 125.00 | 195000.00 | 50.00 | 78000.00 | 20.00 | 31200.00 | 31200.00 | SAURABH ENTERPRISES
3.10 | Earthing Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each | 980.00 | 18000.00 | 72000.00 | 17000.00 | 68000.00 | 22722.00 | 90888.00 | 20000.00 | 80000.00 | 16000.00 | 64000.00 | 64000.00 | SAURABH ENTERPRISES
3.20 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Mtr | 220.00 | 1750.00 | 175000.00 | 1500.00 | 150000.00 | 1922.00 | 192200.00 | 1000.00 | 100000.00 | 1400.00 | 140000.00 | 100000.00 | Balaji Engineering
3.30 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 300.00 | Mtr | 220.00 | 1200.00 | 360000.00 | 1500.00 | 450000.00 | 1415.00 | 424500.00 | 1250.00 | 375000.00 | 1200.00 | 360000.00 | 360000.00 | DOSHI ELECTRIC ENGG. CO., SAURABH ENTERPRISES
3.40 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 36400.00 | Mtr | 220.00 | 20.00 | 728000.00 | 20.00 | 728000.00 | 24.00 | 873600.00 | 30.00 | 1092000.00 | 15.00 | 546000.00 | 546000.00 | SAURABH ENTERPRISES
4.10 | DISTRIBUTION BOARDS Supplying and fixing following way, horizontal type three pole and neulral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/ lsolator) 4 way (8 + 12), Double door | 10.00 | No. | 413679.00 | 2750.00 | 27500.00 | 2123.00 | 21230.00 | 3425.00 | 34250.00 | 10000.00 | 100000.00 | 2100.00 | 21000.00 | 21000.00 | SAURABH ENTERPRISES
4.20 | 6 way (8 + 18), Double door | 4.00 | No. | 17.00 | 3250.00 | 13000.00 | 2642.00 | 10568.00 | 4207.00 | 16828.00 | 10000.00 | 40000.00 | 2600.00 | 10400.00 | 10400.00 | SAURABH ENTERPRISES
4.30 | 8 way (8 + 24), Double door | 39.00 | No. | 17.00 | 3750.00 | 146250.00 | 3401.00 | 132639.00 | 5045.00 | 196755.00 | 12000.00 | 468000.00 | 3250.00 | 126750.00 | 126750.00 | SAURABH ENTERPRISES
4.40 | 12 way (8 + 36), Double door | 3.00 | No. | 17.00 | 5350.00 | 16050.00 | 5021.00 | 15063.00 | 7320.00 | 21960.00 | 15000.00 | 45000.00 | 4800.00 | 14400.00 | 14400.00 | SAURABH ENTERPRISES
5.10 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBS (but without MCBS and incomer) as required. (Note:Verlical type MCB TPDB is normally used where 3 phase outlets are required.) 6 way (8 + 18), Double door | 10.00 | No. | 27.00 | 6500.00 | 65000.00 | 7415.00 | 74150.00 | 8516.00 | 85160.00 | 15000.00 | 150000.00 | 6300.00 | 63000.00 | 63000.00 | SAURABH ENTERPRISES
5.20 | 8 way (8 + 24), Double door | 10.00 | No. | 26.00 | 7500.00 | 75000.00 | 7415.00 | 74150.00 | 9905.00 | 99050.00 | 15000.00 | 150000.00 | 7000.00 | 70000.00 | 70000.00 | SAURABH ENTERPRISES
6.10 | Supplying and fixing Cable End Box (Loose wire boxxlP 43) suitable for foltowing triple pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with testing and commissioning etc. as required. For 4 way, Double door TPN MCB DB | 10.00 | No. | 57.00 | 700.00 | 7000.00 | 1818.00 | 18180.00 | 2184.00 | 21840.00 | 1000.00 | 10000.00 | 550.00 | 5500.00 | 5500.00 | SAURABH ENTERPRISES
6.20 | For 6 way, Double door TPN MCB DB | 4.00 | No. | 26.00 | 900.00 | 3600.00 | 2261.00 | 9044.00 | 2184.00 | 8736.00 | 1000.00 | 4000.00 | 760.00 | 3040.00 | 3040.00 | SAURABH ENTERPRISES
6.30 | For 8 way, Double door TPN MCB DB | 39.00 | No. | 26.00 | 1100.00 | 42900.00 | 1300.00 | 50700.00 | 2272.00 | 88608.00 | 1000.00 | 39000.00 | 1000.00 | 39000.00 | 39000.00 | SAURABH ENTERPRISES, Balaji Engineering
6.40 | For 12 way, Double door TPN MCB DB | 3.00 | No. | 26.00 | 1700.00 | 5100.00 | 2000.00 | 6000.00 | 4591.00 | 13773.00 | 1000.00 | 3000.00 | 1500.00 | 4500.00 | 3000.00 | Balaji Engineering
7.10 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 250 A, tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBS (but without MCBS and incomer) as required. (Note:Verlical type MCB TPDB is normally used where 3 phase outlets are required.) 12 way, with 250 A MCCB as incomer and SP/ TP MCBs as outgoing | 6.00 | No. | 456.00 | 14000.00 | 84000.00 | 15000.00 | 90000.00 | 16194.00 | 97164.00 | 25000.00 | 150000.00 | 12850.00 | 77100.00 | 77100.00 | SAURABH ENTERPRISES
8.00 | Supplying and fixing Cable End Box (Loose wire box) suitable for triple pole and neutral, sheet steel, Vertical MCB distribution board, 415 V, on surface/ recess, complete with testing and commissioning etc. as required. | 20.00 | No. | 356.00 | 600.00 | 12000.00 | 2000.00 | 40000.00 | 5185.00 | 103700.00 | 1000.00 | 20000.00 | 565.00 | 11300.00 | 11300.00 | SAURABH ENTERPRISES
9.00 | Supplying and fixing Single pole 5 amps to 32 amps rating, 240 volts 1O KA, "C" curve, miniature circuit breaker suitable for inductive load in the existing MCB DB complete. with connections, testing and commissioning etc. as required. | 1200.00 | No. | 356.00 | 150.00 | 180000.00 | 200.00 | 240000.00 | 208.00 | 249600.00 | 175.00 | 210000.00 | 120.00 | 144000.00 | 144000.00 | SAURABH ENTERPRISES
10.00 | Supplying and fixing Triple pole 6 amps to 32 amps rating, 415 volts 1O KA, "C" curve, miniature circuit breaker suitable for inductive load in the existing MCB DB complete. with connections, testing and commissioning etc. as required. | 60.00 | No. | 356.00 | 750.00 | 45000.00 | 725.00 | 43500.00 | 1015.00 | 60900.00 | 750.00 | 45000.00 | 500.00 | 30000.00 | 30000.00 | SAURABH ENTERPRISES
11.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 100.00 | No. | 356.00 | 10.00 | 1000.00 | 21.00 | 2100.00 | 13.00 | 1300.00 | 750.00 | 75000.00 | 12.00 | 1200.00 | 1000.00 | DOSHI ELECTRIC ENGG. CO.
12.10 | Supplying and fixing following rating, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A | 60.00 | No. | 356.00 | 600.00 | 36000.00 | 659.00 | 39540.00 | 872.00 | 52320.00 | 500.00 | 30000.00 | 500.00 | 30000.00 | 30000.00 | SAURABH ENTERPRISES, Balaji Engineering
12.20 | 63 A | 20.00 | No. | 599.00 | 700.00 | 14000.00 | 667.00 | 13340.00 | 952.00 | 19040.00 | 500.00 | 10000.00 | 500.00 | 10000.00 | 10000.00 | SAURABH ENTERPRISES, Balaji Engineering
13.10 | Supplying and fixing following rating, double pole / four pole, 240 / 415 volts, RCBO having a sensitivity current upto 300 milliamperes in the existing [,lCB DB complete with connections, testing and commissioning etc. as required. 40 amps FP 4 module | 60.00 | No. | 356.00 | 3000.00 | 180000.00 | 3297.00 | 197820.00 | 2871.00 | 172260.00 | 1000.00 | 60000.00 | 2600.00 | 156000.00 | 60000.00 | Balaji Engineering
13.20 | 63 amps FP 4 module | 20.00 | No. | 599.00 | 3200.00 | 64000.00 | 3476.00 | 69520.00 | 3266.00 | 65320.00 | 1000.00 | 20000.00 | 3000.00 | 60000.00 | 20000.00 | Balaji Engineering
14.00 | ELECTRICAL PANELS Supply, Installation, Testing and Commissioning of cubicle type LT panel/ Outdoor feeder pillar, IP42 protection in case of indoor panel and IP-54 in case of outdoor feeder pillar, 35 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 35 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor S/C cable, cable alleys, cable gland plates in two half, i/c providing following switch gears :- Also, refer to General Notes and Specifications for Panels/ Feeder Pillers/Boards. All live accessible parts shall be shrouded and all equipment shall be finger touch proof. SMC shrouds busbar supports shall be used. Padlocking facility shall be provided on all MCCB feeder doors and switch handles shall be locakble in OFF position. Sealing Arrangement:- PE Foam Rubber Gasket Bus Bars Supports - Non-Hygroscopic, Non Carbonising, Corrosion Resistant, SMC Supports 1Set of connector (Phase+Neutral) shall be provided in cable alley for all outgoing with interconnection wires between MCB and Connector. Minimum Air Clearances between bus bars; P-P=32mm, P-N=32mm,P-E=26mm and N-E=26mm Panel Power and control Wiring shall be with FRLS PVC insulated cable AC voltage circuit-1.5 sqmm Red,Yellow,Blue &Black Current circuit-1.5 sqmm Red,Yellow,Blue &Black AC Control circuit-1.5 sqmm White for Phase & Black for Neutral DC Control circuit-2.5 sqmm Grey Power circuit- Red,Yellow,Blue for Phase &Black for Neutral Labelling- Computerised Laminated Aluminium Name Plate with White letters on Blue/Black Background For Each Feeder and Panel Itself. All indicating lamps shall be LED type with 2 amp protection MCB All ammeter/ volt meter/MFM shall be digital type of size 96 mm x 96 mm. Note: If mentioned fault rating is unavailable consider nearby upside rating All outgoing MCCB shall be with adjustable O/L protection. All outgoing MCCB shall have 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. All incomers and Buscoupler breakers shall be electrical and mechanical interlocked with suitable accessories. 1 Set Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. Suitable size insulation mat conforming to IS: 15652: 2006 shall be provided in front of the panels. MDB (Emergency smoke spill fan upper arrival Panel) Incomer-I & II: 2 Nos. 630A, 4P MCCB, 35KA, Microprocessor based release (Ics = Icu = 100%) with inbuilt O/L , S/C & E/F protection as per specification and with following accessories. Each Incomer shall have one set of the following items: 1 No. Digital MFM meter and 3 nos. CTs of ratio 630/5A , Class 0.5 accuracy and 10 VA burden. digital multifunction meter suitable to measure voltage, Ampere, Frequency, Power Factor with RS-485 Port 1 Set of ON/ OFF/TRIP Indicating LED Lamps with 2 Amp MCB. 1 Set of phase indicating LED lamps with 2 amp back up MCB. Buscoupler: 1 No. 630A, 4P MCCB, 35KA, Microprocessor based release (Ics = Icu = 100%) with inbuilt O/L , S/C & E/F protection with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. Busbars: 4P aluminium bus bars of 800A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. Outgoing: 08 Nos. 63A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =35 KA) 17 Nos. 32A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =35 KA) 2 Nos. Type-2 SPD 65kA 4P (Similar to HAGER (SPN465R) or Equivalent ) with 1No. Red Indicator Light for SPD with 1Set. SPD Back up fuse 1P 50A 20kA including all necessary accessories. | 2.00 | Each | 599.00 | 1275000.00 | 2550000.00 | 1000000.00 | 2000000.00 | 1149140.00 | 2298280.00 | 150000.00 | 300000.00 | 108154.50 | 216309.00 | 216309.00 | SAURABH ENTERPRISES
15.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class A, 2mm thick suitable for all voltages not exceeding 3.3 KV AC and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ±20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 300.00 | Mtr | 599.00 | 600.00 | 180000.00 | 600.00 | 180000.00 | 1321.00 | 396300.00 | 1850.00 | 555000.00 | 500.00 | 150000.00 | 150000.00 | SAURABH ENTERPRISES
16.00 | Supply and laying of 110 mm dia size of HDPE pipe PE-100, PN-10 at a depth of 0.8 mtr below the ground as per site condition incl. excavation and re-filing etc. complete as required. | 1000.00 | Mtr | 599.00 | 130.00 | 130000.00 | 500.00 | 500000.00 | 465.00 | 465000.00 | 500.00 | 500000.00 | 500.00 | 500000.00 | 130000.00 | DOSHI ELECTRIC ENGG. CO.
17.00 | Supply and fixing Chandeliers light of Diameter: 1050 mm & Height: 560 mm with weight of 20 kg ,No of head :18 and made of brass with Gold Plating with wattage :18*4 W led including, Warrenty : 7years on Plating, 2 years on Crystal & 1 years on Electrical. all the necessary accessories as per the design ,specifiaction. Jaquar :AS110212, Havels Monarc Chandelier 12LS E14 Hony GLD Item Code LHFHAZCNTB 1D005, Philips cat ref. 581857 Monarch Chandelier Crystal Ag Al Rod E14 6*MAX 60W or equevalent as approved. | 16.00 | Each | 599.00 | 30000.00 | 480000.00 | 20900.00 | 334400.00 | 40580.00 | 649280.00 | 55500.00 | 888000.00 | 23500.00 | 376000.00 | 334400.00 | M/S AMAR ENTERPRISES
18.00 | Supply and fixing Light fabric shade with chrome finish table lamp of Dia :380 mm and Height: 680 mm with weight of 2.65 kg and lamp :E27 LED 7 W x 1 including all the necessary accessories as per the design ,specifiaction Jaquar : DTL-CHR-MT160275451A, HavelsTable Lamp Harriet Table Lamp Flax Shade ABR Item Code :LHFEAAG1TN 1T040, Philips cat ref. 581873 Floret 6W LED Table Lamp or equevalent as approved. | 24.00 | Each | 599.00 | 8000.00 | 192000.00 | 3000.00 | 72000.00 | 9567.00 | 229608.00 | 3000.00 | 72000.00 | 6150.00 | 147600.00 | 72000.00 | M/S AMAR ENTERPRISES, Balaji Engineering
19.00 | Supply and fixing Light aluminium shade with white/Black paint finish Floor lamp of Dia :500 mm and Height: 1765 mm with weight of 12.5 kg and lamp :E27 LED 7 W x 1 including all the necessary accessories as per the design ,specifiaction Jaquar : DFL-WHT-FL306F, Havels Floor Lamp Fair Tailes FL WHT A60 Fabric Shade Item Code : LHFHAODBT N1W007, Philips cat ref. 582084 Ornate Wood Floor Lamp E27 or equevalent as approved. | 16.00 | Each | 385.00 | 7500.00 | 120000.00 | 7900.00 | 126400.00 | 7363.00 | 117808.00 | 6000.00 | 96000.00 | 6150.00 | 98400.00 | 96000.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 23441800.00 |  | 26777644.00 |  | 30896208.00 |  | 28331600.00 |  | 22999999.00
Lowest Amount Quoted BY: SAURABH ENTERPRISES(22999999.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS power supply system for IT equipments and miscellaneous electrical works Tender ID: 2024_AAI_217164_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES (BID ID -793482) | 22999999.00 | L1
| 2 | DOSHI ELECTRIC ENGG. CO. (BID ID -793025) | 23441800.00 | L2
| 3 | M/S AMAR ENTERPRISES (BID ID -793642) | 26777644.00 | L3
| 4 | Balaji Engineering (BID ID -794436) | 28331600.00 | L4
| 5 | EVERCREST PROJECTS PVT LTD (BID ID -793930) | 30896208.00 | L5