## BoQ1
Government eProcurement System Created By: Semreichui Duidang Created Date/Time: 13-Jan-2025 01:24 PM Tender Title: Replacement of Old AC with Star Rated-Inv AC or VRV System and Provision of Water Dispenser for Ops Infrastructure at Imphal International Airport. Tender ID: 2024_AAI_217677_1
Tender Inviting Authority: Sr. Manager (Engg.-Elect.), AAI, Imphal International Airport.
Name of Work:
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RS COOLING APPLIANCES (GSTN-18AALFR2502H3Z8) BID ID -796018 |  | thangtech global infra pvt ltd (GSTN-NA) BID ID -802668
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Item No. 1: DEPARTURE HALL
1.01 | Item No. 1.1: Outdoor Unit
1.02 | Supply, installation, testing and commisioning of Variable refrigerant volume / flow modular type air-conditioning system suitable to operate from 415 ±10% volt, 50 Hz, 3 phase AC power supply for Cooling by using inverter driven capacity control compressors (Hermetically sealed scroll / DC Twin Rotary) complete with individual controller and fittings with necessary wiring, connection, including suitable isolator for each selected module, termination etc., as per quantity given below including full charging of R-410A refrigerant gas complete as per the schematic draw & technical specifications i/c suitable size 1:2:4 c/c foundation, cable tray with MS support on ground / wall / above false ceiling. The COP of the Unit shall not be less than 5.3 at 50% load.
1.03 | Hi Side - Outdoor Units
1.04 | Supply, installation, testing and commisioning of variable refrigerant flow / variable refrigerant volume modular type outdoor unit complete with hermetically sealed DC inverter scroll type compressor with BLDC motor Heat exchanger / condenser coil, microproccessor controller, low noise condenser fan, auto check function for connection error, auto address setting and minimum capacity as mentioned below incuding foundation as per OEM complete with all accessories etc. All outdoor unit should have cooling COP not less than 3.80 & 6.0 at 100% & 50% load condition respectively for colling as per AHRI standards and conditions capable of operation upto 50 Degree ambient. The outdoor aluminium fins should be with corrosive resistance coating apart from hydrophobic coating. The configuration of outdoor unit may be higher capacity or equal capacity as per site condition.
1.05 | a) 10 HP (cooling only) | 3.00 | No | 0.00 | 240000.00 | 720000.00 | 213395.00 | 640185.00 | 640185.00 | thangtech global infra pvt ltd
1.06 | Item No. 1.2: Low Side - Indoor Units - (High wall Units)
1.07 | Supply of Indoor Units for variable refrigerant flow airconditioning system suitable for 220 ± 10% volt, 50 Hz, 1 phase AC supply equipped with washable filter, BLDC motor including corded remote and y - branches, drain pan, drain water lift-up mechanism, insulation, pipe connections, fresh air intake etc. complete with PVC insulated FRLS copper conductor electric wire upto 1.5 metre length for electrically connecting the IDU with minimum capacity as given below.
1.08 | a) 10 HP cooling capacity with 3200 CFM airflow | 3.00 | No | 0.00 | 60000.00 | 180000.00 | 92625.00 | 277875.00 | 180000.00 | RS COOLING APPLIANCES
1.09 | Item No. 1.3: Supply, Installation, testing and commissioning of necessary fittings, Y-joints and headers etc. | 4.00 | Set | 0.00 | 5300.00 | 21200.00 | 8000.00 | 32000.00 | 21200.00 | RS COOLING APPLIANCES
1.10 | Item No. 1.4: Supply, installation, testing and commissioning of wired remote controls. | 3.00 | No | 0.00 | 2000.00 | 6000.00 | 1500.00 | 4500.00 | 4500.00 | thangtech global infra pvt ltd
2.00 | Item No. 2: COPPER PIPING
2.01 | Item No. 2.1: Refrigerant Piping
2.02 | Supply & Installation of interconnecting following sizes of one end expanded refrigerant copper pipe work of following outer diameter, insulated with 19/13 mm thick closed cell electrometric EPDM/nitrile rubber tubular insulation between each set of indoor & outdoor units with outer mechanical protection of alluminum cladding for all exposed pipes as per specification. All piping inside the room shall be properly fixed/supported with suitable size of clamp / M.S. hanger and all external piping shall run in M.S. painted cable tray (Price Extra) etc. as reqd.
2.03 | Item No. 2.1.2: 34.9 mm dia with 19 mm thick EPDM/nitrile rubber insulation. | 70.00 | Mtr | 0.00 | 1750.00 | 122500.00 | 1627.40 | 113918.00 | 113918.00 | thangtech global infra pvt ltd
2.04 | Item No. 2.1.3: 28.6 mm dia with 19mm thick EPDM/nitrile rubber insulation. | 12.00 | Mtr | 0.00 | 1100.00 | 13200.00 | 1236.00 | 14832.00 | 13200.00 | RS COOLING APPLIANCES
2.05 | Item No. 2.1.4: 22.2 mm dia with 19mm thick EPDM/nitrile rubber insulation. | 40.00 | Mtr | 0.00 | 790.00 | 31600.00 | 1001.16 | 40046.40 | 31600.00 | RS COOLING APPLIANCES
2.06 | Item No. 2.1.5: 19.1 mm dia with 13 mm thick EPDM/ nitrile rubber insulation. | 70.00 | Mtr | 0.00 | 675.00 | 47250.00 | 971.29 | 67990.30 | 47250.00 | RS COOLING APPLIANCES
2.07 | Item No. 2.1.6: 12.7 mm dia with 13 mm thick EPDM/ nitrile rubber insulation. | 12.00 | Mtr | 0.00 | 500.00 | 6000.00 | 539.72 | 6476.64 | 6000.00 | RS COOLING APPLIANCES
2.08 | Item No. 2.1.7: 9.5 mm dia with 13mm thick EPDM/nitrile rubber insulation. | 40.00 | Mtr | 0.00 | 400.00 | 16000.00 | 616.97 | 24678.80 | 16000.00 | RS COOLING APPLIANCES
3.00 | Item No. 3: Drain Piping
3.01 | Item No. 3.1: Providing & fixing of PVC Pipe complete with fittings of following sizes.
3.02 | a) 25 mm dia with 6 mm thick insulation | 70.00 | Mtr | 0.00 | 220.00 | 15400.00 | 47.00 | 3290.00 | 3290.00 | thangtech global infra pvt ltd
3.03 | b) 32 mm dia with 6 mm thick insulation | 70.00 | Mtr | 0.00 | 240.00 | 16800.00 | 60.00 | 4200.00 | 4200.00 | thangtech global infra pvt ltd
3.04 | c) 40 mm dia with 6 mm thick insulation | 60.00 | Mtr | 0.00 | 270.00 | 16200.00 | 80.00 | 4800.00 | 4800.00 | thangtech global infra pvt ltd
3.05 | Item No. 3.2: Gas filling of R410 | 30.00 | Kg | 0.00 | 1400.00 | 42000.00 | 1900.00 | 57000.00 | 42000.00 | RS COOLING APPLIANCES
4.00 | Item No. 4: Control & Transmission Wiring
4.01 | Item No. 4.1: Providing & fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor/controller. | 100.00 | Mtr | 0.00 | 210.00 | 21000.00 | 120.00 | 12000.00 | 12000.00 | thangtech global infra pvt ltd
5.00 | Item No. 5: Cables
5.01 | Item No. 5.1: Supplying, laying, testing and commissioning of XLPE insulated Copper conductor armored cables, 4C x 10 Sq.mm of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps, With / Without End terminations with Double Compression type glands on both ends, double earthing with GI strip/wire of suitable size and hardware as per specifications including termination of cables to feeders complete in all respect. | 200.00 | Mtr | 0.00 | 900.00 | 180000.00 | 947.00 | 189400.00 | 180000.00 | RS COOLING APPLIANCES
5.02 | Item No. 5.2: Supply and laying of 3C x 2.5 Sq.mm PVC insulated and PVC sheathed Flexible copper conducotr of 1.1 KV grade for indoor Units in MS conduit. | 80.00 | Mtr | 0.00 | 200.00 | 16000.00 | 515.00 | 41200.00 | 16000.00 | RS COOLING APPLIANCES
6.00 | Item No. 6: Supply, installation, testing and balancing of square/circular return air diffusers of powder coated extruded aluminium construction without volume control dampers. | 5.00 | Sqm | 0.00 | 7000.00 | 35000.00 | 6000.00 | 30000.00 | 30000.00 | thangtech global infra pvt ltd
7.00 | Item No. 7: Removal and modification of existing false ceiling and ducts made of 2' x 2' for aestheticaly covering as per site conditions. | 25.00 | Sqm | 0.00 | 300.00 | 7500.00 | 140.00 | 3500.00 | 3500.00 | thangtech global infra pvt ltd
8.00 | Item No. 8: Supply of 25 mm thick double skin plenum Box made of 36 Kg/M3 density puff sandwiched in 0.5 mm PCGI suitable for indoor unit CFM. | 3.00 | Each | 0.00 | 30000.00 | 90000.00 | 25000.00 | 75000.00 | 75000.00 | thangtech global infra pvt ltd
9.00 | Item No. 9: Supply and installation of flexible canvass connection for indoor unit. | 3.00 | Each | 0.00 | 2000.00 | 6000.00 | 680.00 | 2040.00 | 2040.00 | thangtech global infra pvt ltd
10.00 | Item No. 10: Supply, installation, testing and commissioning of Jet Nozzles suitable for indoor unit CFM inclusive of GI butterfly damper 18 SWG frame with 20 SWG blade, 150 mm depth. | 9.00 | Each | 0.00 | 7000.00 | 63000.00 | 2500.00 | 22500.00 | 22500.00 | thangtech global infra pvt ltd
11.00 | Item No. 11: Providing, fabrication and fixing of 50 mm x 50 mm x 5 mm MS angle support for positioning ODU and support for copper pipping i/c grouting, welding, fixing clamps, bolts, nuts, and washers and painting with primer and finish paint etc. complete as required. | 100.00 | Kg | 0.00 | 200.00 | 20000.00 | 300.00 | 30000.00 | 20000.00 | RS COOLING APPLIANCES
12.00 | Item No. 12: DISMANTLING
12.01 | Item No. 12.1: Dismantling of existing 22 TR IDU & ODU ductable AC including Cable, Copper pipe, Iron frame, other accessories and handing over to AAI store along with material list. The agency must submit the work plan for dismalting of the AC duct. The work shall be carried out in phase Manner as per the available length i/c temporary covering with green shade net during the dismantling work and also the false ceiling as per area where work is not completed. | 1.00 | Job | 0.00 | 15000.00 | 15000.00 | 10000.00 | 10000.00 | 10000.00 | thangtech global infra pvt ltd
12.02 | Item No. 12.2: Dismantling of existing AC Duct after removing and refixing the same to the orignial design and finishing including handing over dismantled duct to AAI store. | 3.00 | Sqm | 0.00 | 700.00 | 2100.00 | 600.00 | 1800.00 | 1800.00 | thangtech global infra pvt ltd
13.00 | Item No. 13: Supply and installation of 300 mm x 62.5 mm x 2 mm perforated Hot dip Galvanished Cable trays with perforation not more than 17.5% in covenient sections, joined with connectors fixed on wall/Floor/Surface/Ceiling with necessary fixing accessories for running refrigerant piping and cable along with control wiring etc., complete as required. | 100.00 | Mtr | 0.00 | 800.00 | 80000.00 | 900.00 | 90000.00 | 80000.00 | RS COOLING APPLIANCES
14.00 | Item No. 14: Supply and installation of top loaded Normal, Hot and Cold water dispenser suitable for use with 20 litre AR for opeerating on 1-Phase, 50 Hz, 230 VAC power. | 5.00 | Each | 0.00 | 12000.00 | 60000.00 | 16000.00 | 80000.00 | 60000.00 | RS COOLING APPLIANCES
| Total in Figures |  |  |  |  | 1849750.00 |  | 1879232.14
Lowest Amount Quoted BY: RS COOLING APPLIANCES(1849750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Old AC with Star Rated-Inv AC or VRV System and Provision of Water Dispenser for Ops Infrastructure at Imphal International Airport. Tender ID: 2024_AAI_217677_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RS COOLING APPLIANCES (BID ID -796018) | 1849750.00 | L1
| 2 | thangtech global infra pvt ltd (BID ID -802668) | 1879232.14 | L2