## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 28-Jan-2025 05:52 PM Tender Title: Construction of New MSSR Building at R.B. Airport, Bhopal. SH Provision of Fire Fighting Systems. Tender ID: 2024_AAI_219145_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Construction of New MSSR Building at R.B. Airport, Bhopal. SH: Provision of Fire Fighting Systems.
Contract No: AAI/BPL/ENGG(E)/NIT-13/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SUPER INDIA BUILDPRO PRIVATE LIMITED (GSTN-22AASCS8674F1ZU) BID ID -803967 |  | DIZA ENTERPRISES PRIVATE LIMITED (GSTN-NA) BID ID -797900 |  | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -804655 |  | ILLUMECH ENGINEERING (GSTN-NA) BID ID -804225 |  | NEW ERA SYSTEM & TECHNOLOGY (GSTN-NA) BID ID -804792
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of electric driven main fire Hydrant & Sprinkler pumps suitable for automatic operation complete in all respect as required & as per enclosed specification and consisting of the following: Horizontal type multistage, centrifugal, split casing pump of cast iron body and bronze impeller with stainless steel shaft, to ensure minimum pressure of 3.5 kg/cm2 at highest and farthest outlet at specified flow of 2280 LPM & 75 Meter head conforming to IS- 1520 complete with mechanical seals, safety relief valve, pressure gauges on delivery side, Suitable rating IE-3 ,TEFC type Squirrel cage Induction motor suitable for operation on 415V, 3 phase, 50Hz, AC confirming to IS-325 with IP:55 protection for enclosure, horizontal foot mounted with class F insulation, spacer type love-joy / flexible coupling & coupling guard with the pump complete. Common bed plate fabricated from MS channel / ISMB with spring type vibration isolators. The pump set base shall be held by bolts grouted in the suitable cement concrete foundation duly as per recommendation of OEM, plastered and painted including foundation bolts, washers complete etc. as required. Cement concrete / RCC foundation in the scope of Agency. | 2.00 | Each |  | 440000.00 | 880000.00 | 494445.00 | 988890.00 | 308500.00 | 617000.00 | 458900.00 | 917800.00 | 550000.00 | 1100000.00 | 617000.00 | VOID FIRE CONSULTANTS
2.00 | Supply, installation, testing and commissioning of Diesel driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required as per specifications. a. Horizontal type, multistage, centrifugal, pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm.at highest and farthest outlet at specified flow of 2280 lpm at minimum 75 m. head conforming to IS 1520. b. Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant BS & IS standard complete with auto starting mechanism, 12 volts/24 Volts electric starting equipment, Diesel Tank , exhaust pipe extended up to 6 m. outside pump house duly insulated with 75 mm. thick glass wool (density 48kg/cum) with 24 SWG aluminium sheet clading, residential silencer, instruments and protection as per specification, stop solenoid for auto stop in the event of fault with audio indications, painted with posts office red colour including battery, battery stand, AVM pads, etc. as required. c. M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. duly painted as required. d. Suitable cement concrete foundation duly plastered with anti vibration pads. | 1.00 | Each |  | 690600.00 | 690600.00 | 635715.00 | 635715.00 | 535000.00 | 535000.00 | 656666.00 | 656666.00 | 1050000.00 | 1050000.00 | 535000.00 | VOID FIRE CONSULTANTS
3.00 | Supply, installation, testing and commissioning of Electric driven Pressurization / Jockey Pump suitable for suitable for automatic operation and consisting of following, complete in all respect as required as per specifications. a. Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at minimum 75 m head conforming toIS : 1520. b. Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant BS & IS standard complete with auto starting mechanism, 12 volts/24 Volts electric starting equipment, Diesel Tank , exhaust pipe extended up to 6 m. outside pump house duly insulated with 75 mm. thick glass wool (density 48kg/cum) with 24 SWG aluminium sheet clading, residential silencer, instruments and protection as per specification, stop solenoid for auto stop in the event of fault with audio indications, painted with posts office red colour including battery, battery stand, AVM pads, etc. as required. c. M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. duly painted as required. d. Suitable cement concrete foundation duly plastered with anti vibration pads. | 2.00 | Each |  | 155000.00 | 310000.00 | 135970.08 | 271940.16 | 192500.00 | 385000.00 | 142890.00 | 285780.00 | 371250.00 | 742500.00 | 271940.16 | DIZA ENTERPRISES PRIVATE LIMITED
4.00 | Supply, Installation, Testing & Commissioning of electrical control panel of cubicle type body made out of 2mm thick CRCA sheet,totally enclosed, IP 42, floor with channel base frame, dust and vermin proof, indoor, compartmentalised, segregated hinged lockeble door, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, making interlocking arrangement between incomers & buscoupler breakers, including copper control wiring with 2.5 sq mm size wires/cable, interconnection, duly powder coated after 7 tank treatment process painting etc. including supply & installation of following switchgears, metering instruments and accessories as per specifications.
4.01 | (i) Incomer a. 2 No. 400 Amp 4P MCCB (Ics=Icu= 50 KA) with built in thermal magnetic release, adjustable setting. b. 2 No. digital Voltmeter (0-500V) with selector switch for 3 phase, 4 wire operation, each with 3 nos of 2 amp MCB. c. 2 No. digital Ammeter (0-250A) for 3 phase, 4 wire operation with selector switch & CTs. d. 2 Sets of RYB phase indicating lamp each controlled by 2 amp MCB.
4.02 | (ii) Busbars 500Amp FP busbars of high conductivity electrolytic quality aluminium alloy.
4.03 | (iii) Buscoupler 1 No. 400 Amp 4P MCCB (Icu=Ics value 50KA) . 1 Set of ON LED type indication lamp controlled by 2 Amp SP MCB. Including all features of mechnical interlocking with incomers.
4.04 | (iv) Outgoing Main Fire Pump: Hydrant & Sprinkler Pump Set - 2 Nos. a. 200 Amps TPN MCCB(Ics=Icu=35KA) having thermal magnetic release with adjustable setting, with suitable HP fully automatic star/delta starter with over load protection, current sensing type single phase accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/off operation. (0-150A) Ammeter with 3CTs, selector switch.
4.05 | Jockey Pump: 2 Nos. b. 63 Amp TP MCCB (Ics=Icu=10KA) having thermal magnetic release with adjustable setting, with suitable HP fully automatic star/delta starter with overload protection, current sensing type single phase preventer complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/off operation. (0-50A) Ammeter with 3CTs, selector switch.
4.06 | c. Diesel Engine Control: Control for Diesel Engine comprising:- i. Auto/ Manual selector switch & 3 attempt strating device, timers and relays as required, push buttons, strat/stop in manual mode. ii. Indication lamp for High/ Low Lub. Oil pressure, High Water Temp. and Engine ON Indication. iii. Battery charger suitable for 12 V/ 24 V DC with boost and tickle selector switch, 0-30 V DC volt meter, 0-20A DC Ammeter, with boost and trickle selector switch. It will have electronic module to check and indicate the health of batteries regularly. iv. All standard relays and accessories for automatic operation of diesel engine.
4.07 | (v) System Controller Designing, supplying, installation, testing and commissioning of System controller to control operation of main electric fire pump, diesel pump, pressurisation pump in sequence as per specification consisting of relays, timers, sensors, annunciation window for fault indication, complete as per specification.
4.08 | Note: All incomer & buscoupler MCCB shall be mechanical interlocked with suitable accessories. Separate neutral link shall be provided in all 4 Pole feeders.
4.09 | All breakers breaking capacity shall be Icu=Ics | 1.00 | Each |  | 350000.00 | 350000.00 | 540855.00 | 540855.00 | 400000.00 | 400000.00 | 492000.00 | 492000.00 | 450000.00 | 450000.00 | 350000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
5.00 | Supply, Installation, testing and commissioning of pressure switches in MS pipe for Hydrant / Diesel Engine Driven Pump / Jockey Pumps, diaphragm type, adjustable range from 0-10 kg/sq.cm and a regulation range of 0.1 - 1.5 kg/sq.cm direct mounted SNAP acting type made from die cast aluminium with epoxy powder coated finish and SS316 diaphragm and other wetted parts, including necessary wiring upto control panel & other materials as required as per specifications. | 5.00 | Each |  | 2000.00 | 10000.00 | 7551.06 | 37755.30 | 1325.00 | 6625.00 | 1845.00 | 9225.00 | 4500.00 | 22500.00 | 6625.00 | VOID FIRE CONSULTANTS
6.00 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI, short pieces, nipples, elbows, stainless steel 'U' tube & ball valve, etc as required as per specifications. | 13.00 | Each |  | 2000.00 | 26000.00 | 1441.56 | 18740.28 | 816.00 | 10608.00 | 1845.00 | 23985.00 | 7500.00 | 97500.00 | 10608.00 | VOID FIRE CONSULTANTS
7.00 | Providing, laying, testing and comissioning of 'C' Class heavy duty MS Pipe conforming to IS:1239 along with fittings like tees, elbows, flanges, tapers, compressed asbestos gaskets, nuts and bolts, etc. in ground including excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphatt tape as per IS:10221, refilling the trench etc. of following sizes complete as required.
7.01 | 100 mm dia, IS:1239 | 50.00 | Meter |  | 1850.00 | 92500.00 | 1990.73 | 99536.50 | 2027.00 | 101350.00 | 1490.00 | 74500.00 | 2150.00 | 107500.00 | 74500.00 | ILLUMECH ENGINEERING
7.02 | 150 mm dia, IS:1239 | 250.00 | Meter |  | 2850.00 | 712500.00 | 2539.90 | 634975.00 | 3375.00 | 843750.00 | 2290.00 | 572500.00 | 2550.00 | 637500.00 | 572500.00 | ILLUMECH ENGINEERING
8.00 | Providing, laying, testing and comissioning of 'C' Class heavy duty MS Pipe conforming to IS:1239 / 3589 along with fittings like tees, elbows, flanges, tapers, compressed asbestos gaskets, nuts and bolts, etc., on surface and providing cement concrete blocks as supports and painting with two or more coats of synthetic enamel paint of required shade complete as required.
8.01 | 80 mm dia, IS:1239 | 10.00 | Meter |  | 1050.00 | 10500.00 | 837.48 | 8374.80 | 1150.00 | 11500.00 | 953.00 | 9530.00 | 1850.00 | 18500.00 | 8374.80 | DIZA ENTERPRISES PRIVATE LIMITED
8.02 | 150 mm dia, IS:1239 | 20.00 | Meter |  | 2850.00 | 57000.00 | 1776.55 | 35531.00 | 2150.00 | 43000.00 | 1991.99 | 39839.80 | 2550.00 | 51000.00 | 35531.00 | DIZA ENTERPRISES PRIVATE LIMITED
8.03 | 200 mm dia, IS:3589 (wall thickness 6mm) | 50.00 | Meter |  | 3000.00 | 150000.00 | 3013.55 | 150677.50 | 4150.00 | 207500.00 | 2914.00 | 145700.00 | 2850.00 | 142500.00 | 142500.00 | NEW ERA SYSTEM & TECHNOLOGY
9.00 | Providing, laying, testing and comissioning of 'C' Class heavy duty MS Pipe conforming to IS:1239 along with fittings like tees, elbows, flanges, tapers, compressed asbestos gaskets, nuts and bolts, etc. Fixing the pipe on wall / ceiling with suitable clamps and painting with two or more coats of synthetic enamel paint of required shade complete as required.
9.01 | 25 mm dia, IS:1239 | 500.00 | Meter |  | 350.00 | 175000.00 | 251.24 | 125620.00 | 356.00 | 178000.00 | 390.00 | 195000.00 | 425.00 | 212500.00 | 125620.00 | DIZA ENTERPRISES PRIVATE LIMITED
9.02 | 32 mm dia, IS:1239 | 250.00 | Meter |  | 500.00 | 125000.00 | 313.02 | 78255.00 | 472.00 | 118000.00 | 450.00 | 112500.00 | 450.00 | 112500.00 | 78255.00 | DIZA ENTERPRISES PRIVATE LIMITED
9.03 | 50 mm dia, IS:1239 | 150.00 | Meter |  | 800.00 | 120000.00 | 513.47 | 77020.50 | 730.00 | 109500.00 | 650.00 | 97500.00 | 750.00 | 112500.00 | 77020.50 | DIZA ENTERPRISES PRIVATE LIMITED
9.04 | 65 mm dia, IS:1239 | 100.00 | Meter |  | 1000.00 | 100000.00 | 659.00 | 65900.00 | 950.00 | 95000.00 | 761.00 | 76100.00 | 850.00 | 85000.00 | 65900.00 | DIZA ENTERPRISES PRIVATE LIMITED
9.05 | 80 mm dia, IS:1239 | 40.00 | Meter |  | 1050.00 | 42000.00 | 837.48 | 33499.20 | 1190.00 | 47600.00 | 956.00 | 38240.00 | 1850.00 | 74000.00 | 33499.20 | DIZA ENTERPRISES PRIVATE LIMITED
9.06 | 100 mm dia, IS:1239 | 40.00 | Meter |  | 1850.00 | 74000.00 | 1210.91 | 48436.40 | 1632.00 | 65280.00 | 1334.00 | 53360.00 | 2150.00 | 86000.00 | 48436.40 | DIZA ENTERPRISES PRIVATE LIMITED
9.07 | 150 mm dia, IS:1239 | 70.00 | Meter |  | 2850.00 | 199500.00 | 1776.55 | 124358.50 | 2400.00 | 168000.00 | 1991.00 | 139370.00 | 2550.00 | 178500.00 | 124358.50 | DIZA ENTERPRISES PRIVATE LIMITED
10.00 | Providing, installation, testing & commissioning of (PN16) stainless steel strainer fabricated out of 1.6 mm thick stainless sheet steel with 3 mm dia holes with stainless steel flange.
10.01 | 150 mm dia | 3.00 | Each |  | 8000.00 | 24000.00 | 49027.52 | 147082.56 | 33470.00 | 100410.00 | 14434.00 | 43302.00 | 15000.00 | 45000.00 | 24000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
10.02 | 80 mm dia | 2.00 | Each |  | 6000.00 | 12000.00 | 17024.20 | 34048.40 | 11614.00 | 23228.00 | 10028.00 | 20056.00 | 9000.00 | 18000.00 | 12000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
11.00 | Supply, fixing, testing and commissioning of butterfly valve, gunmetal sheet (upto 150mm dia with hand lever operation & above with gear box operation) PN 16 duly ISI marked complete with rubber gasket, flanges, nuts, bolts, washers conforming to IS 13095, of following sizes as required as per specifications.
11.01 | 65 mm dia | 3.00 | Each |  | 2000.00 | 6000.00 | 4755.79 | 14267.37 | 3345.00 | 10035.00 | 2767.00 | 8301.00 | 2500.00 | 7500.00 | 6000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
11.02 | 80 mm dia | 10.00 | Each |  | 2500.00 | 25000.00 | 3134.10 | 31341.00 | 4115.00 | 41150.00 | 2916.00 | 29160.00 | 3500.00 | 35000.00 | 25000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
11.03 | 100 mm dia | 8.00 | Each |  | 3500.00 | 28000.00 | 4324.69 | 34597.52 | 8179.00 | 65432.00 | 3574.00 | 28592.00 | 6500.00 | 52000.00 | 28000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
11.04 | 150 mm dia | 8.00 | Each |  | 4000.00 | 32000.00 | 5826.80 | 46614.40 | 7510.00 | 60080.00 | 4985.00 | 39880.00 | 10500.00 | 84000.00 | 32000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
11.05 | 200 mm dia | 3.00 | Each |  | 5000.00 | 15000.00 | 11593.07 | 34779.21 | 15072.00 | 45216.00 | 9863.00 | 29589.00 | 15500.00 | 46500.00 | 15000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
12.00 | Providing, installation, testing and commissioning of dual plate non return valve, PN16, of following sizes confirming to IS:5312 complete with rubber gasket, GI bolt, nuts, washers etc. as required.
12.01 | 150 mm dia | 3.00 | Each |  | 5000.00 | 15000.00 | 14749.69 | 44249.07 | 17418.00 | 52254.00 | 14293.00 | 42879.00 | 5500.00 | 16500.00 | 15000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
13.00 | Supplying & fixing, testing & commissioning of double flanged Sluice valve PN 16 rating with non rising spindle, bronze/gun metal seat, ISI marked complete with Nut, bolts & washers, gaskets, confirming to IS:780 of following sizes as required.
13.01 | 150 mm dia | 3.00 | Each |  | 15000.00 | 45000.00 | 21276.27 | 63828.81 | 24640.00 | 73920.00 | 21158.00 | 63474.00 | 9500.00 | 28500.00 | 28500.00 | NEW ERA SYSTEM & TECHNOLOGY
13.02 | 80 mm dia | 2.00 | Each |  | 8000.00 | 16000.00 | 10640.13 | 21280.26 | 12580.00 | 25160.00 | 10269.00 | 20538.00 | 7500.00 | 15000.00 | 15000.00 | NEW ERA SYSTEM & TECHNOLOGY
14.00 | Providing and fixing gunmetal gate valve with PN 16 rating with nut, bolts & washers, painting etc complete as required as per specifications.
14.01 | 25 mm dia | 15.00 | Each |  | 2000.00 | 30000.00 | 3089.07 | 46336.05 | 1940.00 | 29100.00 | 2970.00 | 44550.00 | 1600.00 | 24000.00 | 24000.00 | NEW ERA SYSTEM & TECHNOLOGY
15.00 | Supplying & fixing gun metal single headed fire hydrant landing valve with instantaneous Gun metal coupling of 63mm dia with cast iron wheel ISI marked conforming to IS:5290 (Type-A) with blank gunmetal cap and chain as required. | 12.00 | Each |  | 8500.00 | 102000.00 | 8923.98 | 107087.76 | 12166.00 | 145992.00 | 10701.00 | 128412.00 | 8500.00 | 102000.00 | 102000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED, NEW ERA SYSTEM & TECHNOLOGY
16.00 | Supplying and fixing 63mm dia, 15 mtr. Long RRL (Reinforced Rubber Lined) hose pipe with 63mm dia Male and Female gun metal couplings duly binded with copper wire, rivets etc conforming to IS 636 (type-A) as required. | 24.00 | Each |  | 8000.00 | 192000.00 | 6864.60 | 164750.40 | 5620.00 | 134880.00 | 5719.00 | 137256.00 | 7500.00 | 180000.00 | 134880.00 | VOID FIRE CONSULTANTS
17.00 | Supplying and fixing orifice plate made of 6 mm thick stainless steel with orifice of required size in between flange and landing valve of external and internal hydrant to reduce pressure to working pressure of 3.5 kg /sq.cm complete as per specifications as required. | 12.00 | Each |  | 2200.00 | 26400.00 | 2059.38 | 24712.56 | 924.00 | 11088.00 | 1783.00 | 21396.00 | 3500.00 | 42000.00 | 11088.00 | VOID FIRE CONSULTANTS
18.00 | Providing and Fixing 63 mm dia instantaneous pattern gunmetal branch pipe, 20 mm dia nozzle conforming to IS 903, suitable for instantaneous connection to hose pipe coupling complete as required as per specifications. | 12.00 | Each |  | 2500.00 | 30000.00 | 3432.30 | 41187.60 | 3388.00 | 40656.00 | 3013.00 | 36156.00 | 4500.00 | 54000.00 | 30000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
19.00 | Providing and fixing first aid hose reel with MS construction spray painted in post office Red, confirming to IS:884 with upto date amendments, complete with the following as required. a. 30 m length x 20 mm (nominal internal) dia water hose Thermoplastic (Textile reinforced ) type-2 as per IS: 12585. b. 20 mm (nominal internal) dia gun metal ball valve & nozzle. c. Drum and brackets for fixing the equipments on wall. d. Connection from riser to hose reel 40 mm dia stop valve(gun metal) & M.S. pipe including sockets, nipples, elbows etc. | 5.00 | Each |  | 90000.00 | 450000.00 | 9610.44 | 48052.20 | 9856.00 | 49280.00 | 7290.00 | 36450.00 | 9500.00 | 47500.00 | 36450.00 | ILLUMECH ENGINEERING
20.00 | Supplying and fixing of hose cabinet of size 0.9 mtr x 0.6 mtr x 0.5 mtr made out of MS sheet 2mm thick with 6 mm thick glazed glass doors i/c necessary locking arrangement suitable to accommodate external hydrant with butterfly valve, 2 nos 15mtr. long hose pipe, 1 no. branch pipe, mounted on wall OR raised brick platform & duly painted with post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant, as required. | 7.00 | Each |  | 5000.00 | 35000.00 | 4805.22 | 33636.54 | 7700.00 | 53900.00 | 7690.00 | 53830.00 | 8500.00 | 59500.00 | 33636.54 | DIZA ENTERPRISES PRIVATE LIMITED
21.00 | Providing and fixing angle iron (40mmx40mmx5mm) door frame and S.S. sheet (2mm thick) cum glass shutter of size 2.1 mtr x 0.9 mtr x 0.75 mtr (N.S.) with 25mmx25mmx3mm angle frame all around and stiffened in between i/c hinges, handle, locking arrangement, painting with approved synthetic enamel paint i/c sign writing on glass at internal hydrant including providing & fixing S.S. sheet 2mm thick on remaining portion above door to close opening i/c painting etc. as required. | 5.00 | Each |  | 10000.00 | 50000.00 | 41187.60 | 205938.00 | 26950.00 | 134750.00 | 18790.00 | 93950.00 | 8000.00 | 40000.00 | 40000.00 | NEW ERA SYSTEM & TECHNOLOGY
22.00 | Providing & fixing double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per specs including rubber gaskets, flanges, nuts, bolts and washers complete as required as per specifications.
22.01 | 100 mm dia | 5.00 | Each |  | 6500.00 | 32500.00 | 16019.23 | 80096.15 | 12630.00 | 63150.00 | 3013.00 | 15065.00 | 5000.00 | 25000.00 | 15065.00 | ILLUMECH ENGINEERING
22.02 | 150 mm dia | 4.00 | Each |  | 8000.00 | 32000.00 | 21074.73 | 84298.92 | 15840.00 | 63360.00 | 3653.00 | 14612.00 | 9000.00 | 36000.00 | 14612.00 | ILLUMECH ENGINEERING
23.00 | Supplying and fixing 4 way fire brigade connection of cast iron body with 4 nos. Gun metal male instantaneous inlet couplings complete with cap and chain as required for 150mm diam MS pipe connection, conforming to IS 904 as required as per specifications. | 2.00 | Each |  | 10000.00 | 20000.00 | 8751.60 | 17503.20 | 10625.00 | 21250.00 | 8610.00 | 17220.00 | 10500.00 | 21000.00 | 17220.00 | ILLUMECH ENGINEERING
24.00 | Providing & fixing MS cabinet to enclose fire brigade connection and draw out connection fabricated from MS sheet 2mm thick with 2mm thick MS sheet frame with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry platform as required as per specifications. (Approx 0.6m x 0.6m x 0.45m) | 2.00 | Each |  | 5000.00 | 10000.00 | 4712.40 | 9424.80 | 4158.00 | 8316.00 | 5354.00 | 10708.00 | 3500.00 | 7000.00 | 7000.00 | NEW ERA SYSTEM & TECHNOLOGY
25.00 | Providing & fixing gun-metal fire brigade suction hose coupling with cap and chain as required (draw-out connection) with nut for female coupling as per IS: 902-1974 complete with 100 mm dia GI suction pipe and 100 mm dia foot valve (to be connected to static tank). Provision of GI drop pipe and foot valve shall be made in all the fire water static storage tanks as required as per specifications. | 1.00 | Each |  | 10000.00 | 10000.00 | 8751.60 | 8751.60 | 6314.00 | 6314.00 | 10086.00 | 10086.00 | 5000.00 | 5000.00 | 5000.00 | NEW ERA SYSTEM & TECHNOLOGY
26.00 | Constructing masonry chamber 0.9m x 0.9m x 1.0m inside with hollow concrete blocks work in cement mortar 1:5 (1 cement : 5 fine sand) for sluice valve with C.I medium duty circular cover with frame of 560 mm internal dia for valve chamber. The weight of the cover not to be less than 20 Kg and frame not less than 38 Kg as per standard design and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), necessary excavation, foundation concrete 1:5:10 mix (1 cement : 5 fine sand:10 grades stone aggregate 40mm nominal size), and inside plastering with cement mortar 1:3 (1cement : 3 coarse sand), 12mm thick finished with a floating coat of neat cement complete as per standard design. | 5.00 | Each |  | 8000.00 | 40000.00 | 20394.90 | 101974.50 | 16940.00 | 84700.00 | 8700.00 | 43500.00 | 10000.00 | 50000.00 | 40000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
27.00 | Supply and fixing air vessel made of 250mm dia, 8mm thick MS sheet, 1200mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required as per specifications. | 2.00 | Each |  | 24000.00 | 48000.00 | 21754.56 | 43509.12 | 21560.00 | 43120.00 | 29890.00 | 59780.00 | 15000.00 | 30000.00 | 30000.00 | NEW ERA SYSTEM & TECHNOLOGY
28.00 | Fabricating, Supplying, Installation, Testing and Commissioning of 450 mm dia, 2 Metre high Air Vessel of continuous welded construction with flanged discharge header in pump house fabricated out of 10 mm thick dished ends and 8 mm thick MS sheet, Air Release Valve, complete with drain arrangement with 25 mm dia gun metal wheel valve complete with all accessories etc. | 1.00 | Each |  | 29000.00 | 29000.00 | 44460.88 | 44460.88 | 40810.00 | 40810.00 | 34900.00 | 34900.00 | 25000.00 | 25000.00 | 25000.00 | NEW ERA SYSTEM & TECHNOLOGY
29.00 | Providing, fixing, testing and commissioning of Control valve of cast iron body and brass/bronze working parts comprising of water motor alarm, bronze seat clapper, and clapper arm, hydraulically driven mechanical gong bell to sound continuous alarm when the wet riser/sprinkler system activates, pressure gauges, emergency releases, strainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, MS pipe of required size, flanges, orifice plate, gasket etc. of size 150mm dia as required. | 2.00 | Each |  | 100000.00 | 200000.00 | 48131.96 | 96263.92 | 56980.00 | 113960.00 | 54890.00 | 109780.00 | 10000.00 | 20000.00 | 20000.00 | NEW ERA SYSTEM & TECHNOLOGY
30.00 | Providing & fixing brass quartzoid sprinklers (UL, FM approved) of 15 mm dia size, suitable for sustaining the seat & water hammer effect. The type & temperature rating shall be as follows :
30.01 | Pendant & rosette adjustable type with quartzoid bulb operating temperature at 68 deg. C as per specification. | 90.00 | Each |  | 200.00 | 18000.00 | 299.12 | 26920.80 | 442.00 | 39780.00 | 514.00 | 46260.00 | 500.00 | 45000.00 | 18000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
30.02 | Upright type with quartzoid bulb operating temperature at 68°C as per specification. | 40.00 | Each |  | 200.00 | 8000.00 | 297.08 | 11883.20 | 388.00 | 15520.00 | 490.00 | 19600.00 | 500.00 | 20000.00 | 8000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
31.00 | Providing & fixing 25mm dia stainless steel(SS) flexible sprinkler hose fitting as required as per specifications.
31.01 | 1500 mm long | 90.00 | Each |  | 1200.00 | 108000.00 | 1359.66 | 122369.40 | 1039.00 | 93510.00 | 1780.00 | 160200.00 | 1500.00 | 135000.00 | 93510.00 | VOID FIRE CONSULTANTS
32.00 | Providing and Fixing electrically operated water flow switches (Vane type) including tamper switch and accessories, complete with tap off socket arrangement as required, with with 2 Nos. NO/ NC potential free contact as required as per specifications.
32.01 | 80 mm dia | 2.00 | Each |  | 8000.00 | 16000.00 | 3399.15 | 6798.30 | 6314.00 | 12628.00 | 9870.00 | 19740.00 | 3500.00 | 7000.00 | 6798.30 | DIZA ENTERPRISES PRIVATE LIMITED
32.02 | 150 mm dia | 2.00 | Each |  | 12000.00 | 24000.00 | 3399.15 | 6798.30 | 7238.00 | 14476.00 | 9870.00 | 19740.00 | 5500.00 | 11000.00 | 6798.30 | DIZA ENTERPRISES PRIVATE LIMITED
33.00 | Providing and fixing inspectors test assembly complete with test valve, sight glass sectional drain valve, union with corrosion resistant orifice all complete as per drawing and as per specifications.
33.01 | 50 mm dia | 5.00 | Each |  | 4000.00 | 20000.00 | 6798.30 | 33991.50 | 8505.00 | 42525.00 | 16590.00 | 82950.00 | 5000.00 | 25000.00 | 20000.00 | SUPER INDIA BUILDPRO PRIVATE LIMITED
34.00 | Supply, installation, testing and commissioning ISI marked (IS:940) portable fire extinguisher, water (gas pressure) type capacity 9 kg with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets as required as per specifications. | 10.00 | Each |  | 2900.00 | 29000.00 | 2855.28 | 28552.80 | 3149.50 | 31495.00 | 1659.00 | 16590.00 | 3500.00 | 35000.00 | 16590.00 | ILLUMECH ENGINEERING
35.00 | Supply, installation, testing and commissioning ISI marked (IS:2878) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and walll suspension braket as required as per specifications. | 10.00 | Each |  | 5000.00 | 50000.00 | 7994.80 | 79948.00 | 6600.00 | 66000.00 | 4190.00 | 41900.00 | 5500.00 | 55000.00 | 41900.00 | ILLUMECH ENGINEERING
36.00 | Supply, installation, testing and commissioning of 6 kg ABC (Powder Type) Fire Extinguisher. Mild Steel Cylinders ISI marked TAC approved fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and conforming to IS:13849-1993 as required as per specifications. | 10.00 | Each |  | 3300.00 | 33000.00 | 3235.99 | 32359.90 | 2289.00 | 22890.00 | 1650.00 | 16500.00 | 2500.00 | 25000.00 | 16500.00 | ILLUMECH ENGINEERING
37.00 | Supply, installation, testing and commissioning Mechanical Foam type Fire Extinguisher (AFFF) of 9 Kg, plastic coated as required for electrical rooms and substation as required as per specifications. | 5.00 | Each |  | 2900.00 | 14500.00 | 2447.38 | 12236.90 | 3375.00 | 16875.00 | 1980.00 | 9900.00 | 5500.00 | 27500.00 | 9900.00 | ILLUMECH ENGINEERING
| Total in Figures |  |  |  |  | 6000000.00 |  | 5968012.04 |  | 5839923.00 |  | 5566397.80 |  | 6782000.00
Lowest Amount Quoted BY: ILLUMECH ENGINEERING(5566397.80)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New MSSR Building at R.B. Airport, Bhopal. SH Provision of Fire Fighting Systems. Tender ID: 2024_AAI_219145_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ILLUMECH ENGINEERING (BID ID -804225) | 5566397.80 | L1
| 2 | VOID FIRE CONSULTANTS (BID ID -804655) | 5839923.00 | L2
| 3 | DIZA ENTERPRISES PRIVATE LIMITED (BID ID -797900) | 5968012.04 | L3
| 4 | SUPER INDIA BUILDPRO PRIVATE LIMITED (BID ID -803967) | 6000000.00 | L4
| 5 | NEW ERA SYSTEM & TECHNOLOGY (BID ID -804792) | 6782000.00 | L5