## BoQ1
Government eProcurement System Created By: Rudra Prasad Acharya Created Date/Time: 05-Feb-2025 06:03 PM Tender Title: Provision of Fire Detection, Alarm and Suppression System for balance NAVAIDS installations at Bhubaneswar Airport. (SH SITC of Lift well and Stair case pressurization system work at New ATC Tower cum Technical Building at B.P.I Airport Bhubaneswar. Tender ID: 2024_AAI_219291_1
Tender Inviting Authority: Asst. General Manager (Engg.-Elect.)-II, Airports Authority of India, B.P.I Airport, Bhubaneswar.
Name of Work: Provision of Fire Detection, Alarm & Suppression System for balance NAVAIDS installations at Bhubaneswar Airport. (SH: SITC of Lift well & Stair case pressurization system work at New ATC Tower cum Technical Building at B.P.I Airport Bhubaneswar).
Contract No: 2024_AAI_219291_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHREE ADIYOGI FIRE & ENGINEERING (GSTN-NA) BID ID -798369
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing & Commissioning of following direct driven axial flow pressurization fan complete with Long casing AMCA Certified and Motor should completely accommodated inside the fan casing. Fan should be G.S.S. sheet(Steel sheet should be JFE Galvazinc), JIS G3302, SGCC with Z22 (minimum coating weight on both sides @ 220 g/m2) zinc coating & Zero Spangle, skinpassed, chromated and dry. Fan motor shall be suitable for operation on 415 ± 10% volts, 50 cycles, 3 phase power supply with class 'F' insulation. The fan shall be equipped with mounting bracket & spring isolators for the installation of the fans including fire proof flexible connection at inlet and outlet with facility to operate in Emergency condition during fire fault signal generated from fire alarm system.All tube/vane axial fans motors shall be of minimum IE2 efficiency not be less than 65 % and noise level should not be more than 75 dbA @ 3 m distance for normal operation and 80 dbA @ 3 m distance for emergency operation of fans when measured in hemisperical reverberant room conditions. Sound attenutors of appropriate length shall be included in the cost to achieve the desired result having outlet velocity of fans not more than 15m/s
1.01 | 21000 CFM Lift Well Pressurization of 35 ESP(MM)(External static Pressure) | 1.00 | No | 100.00 | 182546.00 | 182546.00 | 182546.00 | SHREE ADIYOGI FIRE & ENGINEERING
1.02 | 10000 CFM Lift Well Pressurization of 30 ESP(MM)(External static Pressure) | 1.00 | No | 100.00 | 108206.00 | 108206.00 | 108206.00 | SHREE ADIYOGI FIRE & ENGINEERING
1.03 | 22000 CFM Stair Well Pressurization of 30 ESP(MM)(External static Pressure) | 1.00 | No | 10.00 | 182546.00 | 182546.00 | 182546.00 | SHREE ADIYOGI FIRE & ENGINEERING
1.04 | 15000 CFM Stair Well Pressurization of 35 ESP(MM)(External static Pressure) | 1.00 | No | 10.00 | 166970.00 | 166970.00 | 166970.00 | SHREE ADIYOGI FIRE & ENGINEERING
2.00 | Providing and fixing Rot proof Flexible Connection at the blower outlet of item No-1 as per requirement suitable to Fan size. | 4.00 | Each | 10.00 | 4560.00 | 18240.00 | 18240.00 | SHREE ADIYOGI FIRE & ENGINEERING
3.00 | Supplying, fabricating, installing and testing of site fabricated G.I. sheet metal ducts of following thicknesses including necessary supports, flexible hangers with isolators, nut, bolts, gaskets, splitter, damper ,vanes, all in GI, complete in all respect as per specifications and as required in accordance with the approved drawings.
3.01 | 22 Gauge(1.0mm thick) | 250.00 | Sqm | 100.00 | 1512.00 | 378000.00 | 378000.00 | SHREE ADIYOGI FIRE & ENGINEERING
4.00 | Supply & fixing of bird screen as per site requirement for Air pressurization work and as per instruction of Engineer-in-charge. | 4.00 | Nos | 10.00 | 3840.00 | 15360.00 | 15360.00 | SHREE ADIYOGI FIRE & ENGINEERING
5.00 | Supply & fixing of vibration pad to control fan vibration as per site requirement for Air pressurization work and as per instruction of Engineer-in-charge. | 4.00 | Set | 10.00 | 1200.00 | 4800.00 | 4800.00 | SHREE ADIYOGI FIRE & ENGINEERING
6.00 | Supply, Fabrication and Installation of M.S. angle supports for installation of all axial fan including necessary required hardware for fixing of supports etc. and other works like chisseling ,Glass cutting work,civil work etc for sucessful completion of pressurization/ ducting work as required and as per instruction of E-I-C. | 1.00 | Job | 10.00 | 144000.00 | 144000.00 | 144000.00 | SHREE ADIYOGI FIRE & ENGINEERING
7.00 | Supply, Installation, testing & commisioning of 7.5KW 3 phase DOL starer in 2mm CRCA steel sheet duly painted having 1 no 32A 4P MCB, 1 no 3P power contactor, 1 no OLR, 1 no 32A ameter, 3 nos. phase indication lamp, 3 nos. ON,OFF,TRIP indicator, 2 nos. ON/OFF push button, 1 no Auto/Manual Selector switch, 1 no. emergency stop button with provision for remote operation of 1 no PRESSURIZATION fan.having provision of automatic switched on operation in case of receipt of fault FIRE SIGNAL. | 2.00 | Set | 10.00 | 31800.00 | 63600.00 | 63600.00 | SHREE ADIYOGI FIRE & ENGINEERING
8.00 | Supply, Installation, testing & commisioning of 5.5KW 3 phase DOL starer in 2mm CRCA steel sheet duly painted having 1 no 32A 4P MCB, 1 no 3P power contactor, 1 no OLR, 1 no 32A ameter, 3 nos. phase indication lamp, 3 nos. ON,OFF,TRIP indicator, 2 nos. ON/OFF push button, 1 no Auto/Manual Selector switch, 1 no. emergency stop button with provision for remote operation of 1 no PRESSURIZATION fan.having provision of automatic switched on operation in case of receipt of fault FIRE SIGNAL. | 2.00 | Set | 10.00 | 31800.00 | 63600.00 | 63600.00 | SHREE ADIYOGI FIRE & ENGINEERING
9.00 | Supply and Installation of suitable relay module with fire alarm panel during fire fault alarm signal for sucessful integration with pressurization system. | 4.00 | Nos | 10.00 | 3900.00 | 15600.00 | 15600.00 | SHREE ADIYOGI FIRE & ENGINEERING
10.00 | Supply and laying of following XLPE insualted and PVC sheathed 1.1 KV Grade copper conductor armoured power cable confirming to IS 7098 Part-I/1988 upto date amendment.
10.01 | 3Cx 2.5 Sq mm | 80.00 | Mtr | 10.00 | 372.00 | 29760.00 | 29760.00 | SHREE ADIYOGI FIRE & ENGINEERING
10.02 | 4Cx4 Sq mm | 250.00 | Mtr | 10.00 | 624.00 | 156000.00 | 156000.00 | SHREE ADIYOGI FIRE & ENGINEERING
10.03 | 2Cx1.5 Sq mm | 550.00 | Mtr | 10.00 | 144.00 | 79200.00 | 79200.00 | SHREE ADIYOGI FIRE & ENGINEERING
11.00 | Supply and laying of 8 SWG dia G.I Earthing Wire on surface or in recess for connection with existing earthing. | 80.00 | Mtr | 10.00 | 112.50 | 9000.00 | 9000.00 | SHREE ADIYOGI FIRE & ENGINEERING
| Total in Figures |  |  |  |  | 1617428.00
Lowest Amount Quoted BY: SHREE ADIYOGI FIRE & ENGINEERING(1617428.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Fire Detection, Alarm and Suppression System for balance NAVAIDS installations at Bhubaneswar Airport. (SH SITC of Lift well and Stair case pressurization system work at New ATC Tower cum Technical Building at B.P.I Airport Bhubaneswar. Tender ID: 2024_AAI_219291_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHREE ADIYOGI FIRE & ENGINEERING (BID ID -798369) | 1617428.00 | L1