## BoQ1
Government eProcurement System Created By: JAGAN MOHAN BONTADA Created Date/Time: 27-Jan-2025 04:07 PM Tender Title: Upgradation of Fire Alarm System at T1, T4 and Utility Building at Chennai Airport Tender ID: 2024_AAI_220171_1
Tender Inviting Authority: Sr.Manager (Engg-Elect), Airports Authority of India, Operational Offices, Chennai Airport, Chennai – 600 016.
Name of Work: Upgradation of Fire Alarm System at T1, T4 & Utility Building at Chennai Airport.
Contract No: AAM/ENGG(E)/FAS/2024-2025/1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Globe Detective Agency Pvt. Ltd. (GSTN-19AAACG1108N1ZN) BID ID -802766 |  | Sagtaur Systems Private Limited (GSTN-NA) BID ID -796764 |  | Honeywell Automation India Limited (GSTN-NA) BID ID -791909 |  | Sterling and wilson pvt ltd (GSTN-NA) BID ID -804112 |  | A R BUILDING SOLUTIONS (GSTN-NA) BID ID -804961 |  | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED (GSTN-NA) BID ID -804467
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Modular Microprocessor based expandable intelligent Addressable Type Fire Alarm Control Panel with minimum 10 loops, 240 intelligent addressable detectors/ devices (In any combination ) in one loop, minimum 320 character graphics / LCD display with keypad and minimum 4000 events history log in the non-volatile memory (EPROM), capable of taking Protocol Devices, LCD Display, panel shall work in degrade mode incase of CPU failure, suitable for operation on 230 volts, 50 Hz AC power supply, inbuilt/external automatic battery charger with the charging capacity of 200AH, 24 volts, sealed maintenance free batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency/fault conditions. The panel shall be equipped with Digital voice control system for 2 ways communication Fire Fighters System capable of supervising all the speaker circuits with adequate zone control and accessories. Failure of Fire panel CPU shall not result in failure of FFT operation. The panel shall have facility for seamless integration with PA system (For giving trigger signal to Start Pre-recorded Digital Voice Evacuation from PA system in case of fire). The panel shall be inter connected with the existing Building Management System (Honeywell) with open protocol BACNET/MODBUS etc. or advanced software as per specification the programme software license & graphic card, CD, Dongle should be handed over to AAI, inclusion of devices and deletion of devices should be carried out till the life of Fire Alarm Panel i.e., is 5 years, antivirus software original version should be installed and updated till the life time of the panel, battery stand may be provided for above batteries etc., Supply, Installation, Testing & Commissioning of Network Control Annunciator Card for Integration to view all panels of other Area etc. complete as required. List of Preferred makes for use in AAI works.
1.01 | Ground Floor (All Above as Sl.No.1) | 2.00 | Each |  | 771000.00 | 1542000.00 | 700357.00 | 1400714.00 | 530000.00 | 1060000.00 | 409365.19 | 818730.38 | 720000.00 | 1440000.00 | 563186.00 | 1126372.00 | 818730.38 | Sterling and wilson pvt ltd
2.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Modular Microprocessor based expandable intelligent Addressable Type Fire Alarm Control Panel with min 10 loops , 240 intelligent addressable detectors/ devices (In any combination ) in one loop, with minimum 320 character graphics / LCD display with keypad and minimum 4000 events history log in the non-volatile memory (EPROM) , capable of taking Protocol Devices, LCD Display, panel shall work in degrade mode incase of CPU failure, suitable for operation on 230 volts, 50 Hz AC power supply, inbuilt/external automatic battery charger with the charging capacity of 200AH, 24 volts, sealed maintenance free batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency/fault conditions along with battery stand. as per relevant standard/specifications complete as required. Supply, Installation, Testing & Commissioning of Network Control Annunciator Card for Integration to view all panels of other Area etc. complete as required. List of Preferred makes for use in AAI works.
2.01 | Basement & Mezzanine Floor (All Above as Sl.No.2) | 4.00 | Each |  | 525000.00 | 2100000.00 | 488735.00 | 1954940.00 | 486000.00 | 1944000.00 | 362092.08 | 1448368.32 | 410000.00 | 1640000.00 | 328491.00 | 1313964.00 | 1313964.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
3.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Modular Microprocessor based expandable intelligent Addressable Type Fire Alarm Control Panel with min 4 loops , 240 intelligent addressable detectors/ devices (In any combination ) in one loop, with minimum 320 character graphics / LCD display with keypad and minimum 4000 events history log in the non-volatile memory (EPROM) , capable of taking Protocol Devices, LCD Display, panel shall work in degrade mode incase of CPU failure, suitable for operation on 230 volts, 50 Hz AC power supply, inbuilt/external automatic battery charger with the charging capacity of 200 AH, 24 volts, sealed maintenance free batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency/fault conditions along with battery stand. as per relevant standard/specifications complete as required.Supply, Installation, Testing & Commissioning of Network Control Annunciator Card for Integration to view all panels of other Area etc. complete as required. List of Preferred makes for use in AAI works.
3.01 | Utility Building (All Above as Sl.No.3) | 1.00 | Each |  | 333000.00 | 333000.00 | 309370.00 | 309370.00 | 395000.00 | 395000.00 | 168250.76 | 168250.76 | 265000.00 | 265000.00 | 304938.00 | 304938.00 | 168250.76 | Sterling and wilson pvt ltd
4.00 | SITC of Open Protocol Modbus Interface Module for Graphics Integration etc. complete as required. | 2.00 | Each |  | 237000.00 | 474000.00 | 125573.00 | 251146.00 | 165000.00 | 330000.00 | 372612.25 | 745224.50 | 95000.00 | 190000.00 | 0.00 | 0.00 | 0.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
5.00 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) Repeater Panel shall provide pin point location of the fault or fire event and should Provide complete control (shall not be dependent on the Fire Panel CPU operation) of system at remote location. The panel shall have a 320 character (graphics) / LCD display with touch screen or other keypad. Supply, Installation, Testing & Commissioning of Network Card for above panels & Annunciator Card etc. complete as required. List of Preferred makes for use in AAI works. | 6.00 | Each |  | 205500.00 | 1233000.00 | 170718.00 | 1024308.00 | 189000.00 | 1134000.00 | 64084.90 | 384509.40 | 52000.00 | 312000.00 | 196519.00 | 1179114.00 | 312000.00 | A R BUILDING SOLUTIONS
6.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable Smoke detector with base and unique optical sensing chamber, visible LED etc. complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate ) or equivalent complete with connections etc. as required and to be installed below/above false ceiling roof and concreate space and as per enclosed specifications complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) List of Preferred makes for use in AAI works. | 5000.00 | Each |  | 1995.00 | 9975000.00 | 1876.00 | 9380000.00 | 2222.00 | 11110000.00 | 1646.77 | 8233850.00 | 1820.00 | 9100000.00 | 1680.00 | 8400000.00 | 8233850.00 | Sterling and wilson pvt ltd
7.00 | Supply, Installation, Testing and Commissioning of UL / EN listed (latest version) intelligent Addressable Type Heat Detector/Laser Dedector (Fixed cum-rate of rise type) with max. triggering temperature programmable as per UL/EN settings complete with all fixing accessories like base, base box, self-adhesive sticker indicating loop number and address etc. to be installed below / above false ceiling, roof and concealed space, etc. interconnecting to loop cable, etc. as per specification complete as required. List of Preferred makes for use in AAI works. | 403.00 | Each |  | 1994.00 | 803582.00 | 1816.00 | 731848.00 | 2083.00 | 839449.00 | 1829.25 | 737187.75 | 1820.00 | 733460.00 | 1670.00 | 673010.00 | 673010.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
8.00 | Supply, Installation, Testing and Commissioning of UL / EN listed (latest version) Response Indicators for getting fire indications of detectors above false ceiling area interconnecting to loop cable etc. as per specification complete as required. List of Preferred makes for use in AAI works. | 254.00 | Each |  | 128.00 | 32512.00 | 169.00 | 42926.00 | 179.00 | 45466.00 | 178.11 | 45239.94 | 300.00 | 76200.00 | 202.00 | 51308.00 | 32512.00 | Globe Detective Agency Pvt. Ltd.
9.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Intelligent Addressable fault isolator module complete etc. required and as per specification. List of Preferred makes for use in AAI works. | 253.00 | Each |  | 1450.00 | 366850.00 | 2082.00 | 526746.00 | 2679.00 | 677787.00 | 1809.18 | 457722.54 | 10.00 | 2530.00 | 0.00 | 0.00 | 0.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
10.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Intelligent Addressable Manual Call Station (Push & pull dual action type) with connection etc. complete as required and as per Specifications. List of Preferred makes for use in AAI works. | 218.00 | Each |  | 4694.00 | 1023292.00 | 5325.00 | 1160850.00 | 3530.00 | 769540.00 | 3646.21 | 794873.78 | 4000.00 | 872000.00 | 3851.00 | 839518.00 | 769540.00 | Honeywell Automation India Limited
11.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) Addressable Hooter-cum strobe with adjustable sound level in the range as per UL/EN described db with termination etc. complete as required and as per Specification. List of Preferred makes for use in AAI works. | 197.00 | Each |  | 2550.00 | 502350.00 | 3112.00 | 613064.00 | 3320.00 | 654040.00 | 2993.94 | 589806.18 | 2150.00 | 423550.00 | 2343.00 | 461571.00 | 423550.00 | A R BUILDING SOLUTIONS
12.00 | Supply, Installation, Testing and commissioning of UL/EN listed (latest version) Intelligent Addressable Control Module for Sounders/Strobes/Sounder cum strobes/Telephone with termination etc. complete as required and as per Specifications. List of Preferred makes for use in AAI works. | 356.00 | Each |  | 3920.00 | 1395520.00 | 2484.00 | 884304.00 | 2758.00 | 981848.00 | 2476.75 | 881723.00 | 3250.00 | 1157000.00 | 3214.00 | 1144184.00 | 881723.00 | Sterling and wilson pvt ltd
13.00 | Supply, Installation, Testing and Commissioning of UL/EN listed (latest version) Intelligent Addressable Relay Module (output module) for tripping of AHU & Ventilation /pressurisation fans/hooter with termination etc. complete as required and as per Specifications. List of Preferred makes for use in AAI works. | 368.00 | Each |  | 3920.00 | 1442560.00 | 2484.00 | 914112.00 | 2572.00 | 946496.00 | 2476.75 | 911444.00 | 3250.00 | 1196000.00 | 3214.00 | 1182752.00 | 911444.00 | Sterling and wilson pvt ltd
14.00 | Supply, Installation, Testing and Commissioning of UL/EN listed (latest version) of Fireman telephone jack with suitable module for two-way communication, complete etc. as required and as per Specifications. | 105.00 | Each |  | 3072.00 | 322560.00 | 1450.00 | 152250.00 | 1399.00 | 146895.00 | 2288.03 | 240243.15 | 1500.00 | 157500.00 | 2520.00 | 264600.00 | 146895.00 | Honeywell Automation India Limited
15.00 | Supply, Erection, Testing and Commissioning of Fire Fighters Telephone Headset with enclosure for two-way communication between Remote Fire Fighter & Fire Command Centre Complete etc. as required. | 12.00 | Each |  | 7420.00 | 89040.00 | 10932.00 | 131184.00 | 9873.00 | 118476.00 | 3956.38 | 47476.56 | 7500.00 | 90000.00 | 6119.00 | 73428.00 | 47476.56 | Sterling and wilson pvt ltd
16.00 | Providing, Installation, Testing & Commissioning of UL/EN listed (latest version) Monitor Module /input module etc. complete as per Specifications. List of Preferred makes for use in AAI works. | 287.00 | Each |  | 3100.00 | 889700.00 | 2163.00 | 620781.00 | 1895.00 | 543865.00 | 2430.29 | 697493.23 | 2580.00 | 740460.00 | 2569.00 | 737303.00 | 543865.00 | Honeywell Automation India Limited
17.00 | Supplying & laying of 2 X 1.5 Sq.mm FRLS armoured cable, copper conductor in surface /false ceiling etc. as per applicable IS standard complete as required. (Shall be executed as per site requirement) List of Preferred makes for use in AAI works. | 5800.00 | Mtrs |  | 127.00 | 736600.00 | 129.00 | 748200.00 | 101.00 | 585800.00 | 124.29 | 720882.00 | 145.00 | 841000.00 | 104.00 | 603200.00 | 585800.00 | Honeywell Automation India Limited
18.00 | Supply, Installation, Testing & Commissioning of UL/EN listed (latest version) 12V/24V 4.5 amps suitable SMPS etc. complete as required. | 197.00 | Each |  | 2350.00 | 462950.00 | 4200.00 | 827400.00 | 1708.00 | 336476.00 | 2451.27 | 482900.19 | 2200.00 | 433400.00 | 647.00 | 127459.00 | 127459.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
19.00 | Supply, Installation, Testing and Commissioning of UL/EN listed (latest version) of approved make Addressable Duct Smoke detector, the high sensitivity Duct Smoke Detectors, sensitivity with Smoke Probe/Tubes and Addressable detectors including the cost of mounting accessories complete as per Specification and as required. List of Preferred makes for use in AAI works. | 67.00 | Each |  | 8900.00 | 596300.00 | 18408.00 | 1233336.00 | 9326.00 | 624842.00 | 10806.06 | 724006.02 | 4100.00 | 274700.00 | 7830.00 | 524610.00 | 274700.00 | A R BUILDING SOLUTIONS
20.00 | Supply, Installation, Testing & Commissioning of Graphic User Interface (GUI) / Operator work station with PC having Intel Pentium I7 Processor or latest version including serial ports (RS232) and USB ports and following accessories etc. complete with software all as specified: a. 4 Gigabytes of RAM memory b. 2 TB of hard disk space c. DVD ROM d. 21” LED colour monitor e. Mouse with Mouse Pad f. Standard Key Board g. Latest Windows Operating System h. Compatible Fire Alarm System Control Software i. Laser Printer colour A4- 1 No j. Software for Automatic Fire Detection and Alarm System k. Software for Aspiration Based Smoke Detection System l. UPS 800 VA or better | 2.00 | Job |  | 925000.00 | 1850000.00 | 351500.00 | 703000.00 | 178000.00 | 356000.00 | 649516.93 | 1299033.86 | 450000.00 | 900000.00 | 545670.00 | 1091340.00 | 356000.00 | Honeywell Automation India Limited
21.00 | Dismantling of existing Fire alarm control panels & associated components like Smoke, Heat detectors, MCP, Hooters etc. from ceiling/low ceiling areas and shifting to AAI stores etc. complete as required. | 2.00 | Job |  | 214000.00 | 428000.00 | 122761.00 | 245522.00 | 45000.00 | 90000.00 | 135517.22 | 271034.44 | 350000.00 | 700000.00 | 24875.00 | 49750.00 | 49750.00 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 26598816.00 |  | 23856001.00 |  | 23689980.00 |  | 20700000.00 |  | 21544800.00 |  | 20148421.00
Lowest Amount Quoted BY: TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED(20148421.00)

## BOQ Summary
BOQ Summary Details Tender Title: Upgradation of Fire Alarm System at T1, T4 and Utility Building at Chennai Airport Tender ID: 2024_AAI_220171_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | TRISIM GLOBAL SOLUTIONS PRIVATE LIMITED (BID ID -804467) | 20148421.00 | L1
| 2 | Sterling and wilson pvt ltd (BID ID -804112) | 20700000.00 | L2
| 3 | A R BUILDING SOLUTIONS (BID ID -804961) | 21544800.00 | L3
| 4 | Honeywell Automation India Limited (BID ID -791909) | 23689980.00 | L4
| 5 | Sagtaur Systems Private Limited (BID ID -796764) | 23856001.00 | L5
| 6 | Globe Detective Agency Pvt. Ltd. (BID ID -802766) | 26598816.00 | L6