## BoQ1
Government eProcurement System Created By: DEVENDRA GOSWAMI Created Date/Time: 24-Jan-2025 05:27 PM Tender Title: Provision of Aerosol-based Fire Suppression System for Navaids System at S. V. Airport, Raipur. Tender ID: 2024_AAI_220636_1
Tender Inviting Authority: Asst. Gen. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Provision of Aerosol-based Fire Suppression System for Navaids System at S. V. Airport, Raipur.
Contract No: 2024_AAI_220636_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | KV FIRE CHEMICALS INDIA PVT LTD (GSTN-27AAACK5054B1ZY) BID ID -796402 |  | Unex Power Point Pvt Ltd (GSTN-07AAACU1740J1ZG) BID ID -805426 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -805450 |  | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -805561 |  | Nexpo Power Solutions Pvt Ltd (GSTN-NA) BID ID -806904 |  | DSS Electric Corporation LLP (GSTN-NA) BID ID -806561
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | H1 Amount | H1 Vendor
1.00 | Design, Manufacturing, supply of UL/EN-listed, Environmentally friendly aerosol-based fire suppression system comprising an electrically operated aerosol generator with shelflife of atleast 15 years having aerosol mass based on UL/EN approved design concentration applicable for Class A, B & C class of Fire with Volumetric Design Consideration. The generator shall be electrically actuated by the existing Fire Alarm cum Release Panel. The quantity of Aerosole generators shall be decided according to volume/dimension of existing Battery room above false flooring having Volume Approx. 120 Cubic mtr.along with UL approved concentration of aerosole duly approved by OEM and shall be approved from EIC prior to starting of the works. The aerosol generated shall be potassium-based, providing effective fire suppression while being environmentally friendly with zero ozone depletion potential and zero global warming potential. The system shall be supplied with necessary accessories complete as required. Dimension of Space- (L X W X H =8 X 5 X3) Cubic Mtr =Approx. 120 Cubic Mtr | 1.00 | Job | 927871.00 | 595000.00 | 595000.00 | 682000.00 | 682000.00 | 800000.00 | 800000.00 | 495500.00 | 495500.00 | 649850.00 | 649850.00 | 645117.00 | 645117.00 | 800000.00 | CENTRE TAP ENGINEERING
2.00 | Installation, testing, and commissioning of above aerosole generators as per item no-01 in the Battery room above false flooring having Volume Approx.120 Cubic mtr. | 1.00 | Job | 53000.00 | 145000.00 | 145000.00 | 50000.00 | 50000.00 | 15000.00 | 15000.00 | 30000.00 | 30000.00 | 10000.00 | 10000.00 | 41250.00 | 41250.00 | 145000.00 | KV FIRE CHEMICALS INDIA PVT LTD
3.00 | Design, Manufacturing, supply of UL/EN-listed, Environmentally friendly aerosol-based fire suppression system comprising an electrically operated aerosol generator with shelflife of atleast 15 years having aerosol mass based on UL/EN approved design concentration applicable for Class A, B & C class of Fire with Volumetric Design Consideration. The generator shall be electrically actuated by the existing Fire Alarm cum Release Panel. The quantity of Aerosole generators shall be decided according to volume/dimension of existing Battery room above false flooring having Volume Approx.150 Cubic mtr.along with UL approved concentration of aerosole duly approved by OEM and shall be approved from EIC prior to starting of the works. The aerosol generated shall be potassium-based, providing effective fire suppression while being environmentally friendly with zero ozone depletion potential and zero global warming potential. The system shall be supplied with necessary accessories complete as required. Dimension of Space- (L X W X H =10 X 5 X 3) Cubic Mtr =Approx. 150 Cubic Mtr | 1.00 | Job | 1114590.00 | 755000.00 | 755000.00 | 875000.00 | 875000.00 | 800000.00 | 800000.00 | 633100.00 | 633100.00 | 875650.00 | 875650.00 | 858808.50 | 858808.50 | 875650.00 | Nexpo Power Solutions Pvt Ltd
4.00 | Installation, testing, and commissioning of above aerosole generators as per item no-03 in the Battery room above false flooring having Volume Approx. 150 Cubic mtr. | 1.00 | Job | 53000.00 | 145000.00 | 145000.00 | 55000.00 | 55000.00 | 15000.00 | 15000.00 | 45000.00 | 45000.00 | 10000.00 | 10000.00 | 57750.00 | 57750.00 | 145000.00 | KV FIRE CHEMICALS INDIA PVT LTD
5.00 | Design, Manufacturing, supply of UL/EN-listed, Environmentally friendly aerosol-based fire suppression system comprising an electrically operated aerosol generator with shelflife of atleast 15 years having aerosol mass based on UL/EN approved design concentration applicable for Class A, B & C class of Fire with Volumetric Design Consideration. The generator shall be electrically actuated by the existing Fire Alarm cum Release Panel. The quantity of Aerosole generators shall be decided according to volume/dimension of existing Battery room below false flooring having Volume Approx. 144.71 Cubic mtr.along with UL approved concentration of aerosole duly approved by OEM and shall be approved from EIC prior to starting of the works. The aerosol generated shall be potassium-based, providing effective fire suppression while being environmentally friendly with zero ozone depletion potential and zero global warming potential. The system shall be supplied with necessary accessories complete as required. Dimension of Space- (L X W X H =7.75 X 5.5 X 3.39) Cubic Mtr =Approx.144.71 Cubic Mtr | 1.00 | Job | 1114590.00 | 755000.00 | 755000.00 | 880000.00 | 880000.00 | 800000.00 | 800000.00 | 631000.00 | 631000.00 | 825450.00 | 825450.00 | 858808.50 | 858808.50 | 880000.00 | Unex Power Point Pvt Ltd
6.00 | Installation, testing, and commissioning of above aerosole generator as per item no-05 in the Battery room below false flooring having Volume Approx. 144.71 Cubic mtr. | 1.00 | Job | 53000.00 | 145000.00 | 145000.00 | 55000.00 | 55000.00 | 15000.00 | 15000.00 | 45000.00 | 45000.00 | 10000.00 | 10000.00 | 57750.00 | 57750.00 | 145000.00 | KV FIRE CHEMICALS INDIA PVT LTD
7.00 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | 90.00 | Meter | 302.13 | 385.00 | 34650.00 | 260.00 | 23400.00 | 250.00 | 22500.00 | 132.00 | 11880.00 | 165.00 | 14850.00 | 288.75 | 25987.50 | 34650.00 | KV FIRE CHEMICALS INDIA PVT LTD
| Total in Figures |  |  |  |  | 2574650.00 |  | 2620400.00 |  | 2467500.00 |  | 1891480.00 |  | 2395800.00 |  | 2545471.50
Highest Amount Quoted BY: Unex Power Point Pvt Ltd(2620400.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Aerosol-based Fire Suppression System for Navaids System at S. V. Airport, Raipur. Tender ID: 2024_AAI_220636_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Unex Power Point Pvt Ltd (BID ID -805426) | 2620400.00 | H1
| 2 | KV FIRE CHEMICALS INDIA PVT LTD (BID ID -796402) | 2574650.00 | H2
| 3 | DSS Electric Corporation LLP (BID ID -806561) | 2545471.50 | H3
| 4 | CENTRE TAP ENGINEERING (BID ID -805450) | 2467500.00 | H4
| 5 | Nexpo Power Solutions Pvt Ltd (BID ID -806904) | 2395800.00 | H5
| 6 | Nexus Fire And Security Systems (BID ID -805561) | 1891480.00 | H6