## BoQ1
Government eProcurement System Created By: Dinesh Patel Created Date/Time: 10-Feb-2025 01:02 PM Tender Title: Development of Fursatganj Airport at Uttar Pradesh for RCS Operation _ Construction of Apron Taxiway and Associated Works. SH_ Provision of Apron Flood Lights at Fursatganj Airport Tender ID: 2024_AAI_221456_1
Tender Inviting Authority: Asst. General Manager (Engg.-E), Airports Authority of India, Fursatganj Airport, Fursatganj
Name of Work: Development of Fursatganj Airport at Uttar Pradesh for RCS Operation- Construction of Apron Taxiway and Associated Works. SH: Provision of Apron Flood Lights at Fursatganj Airport
Contract No: 2024_AAI_221456_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -810963 |  | Dubey Trading Company (GSTN-NA) BID ID -812678 |  | SARANBIR DHINDSA (GSTN-NA) BID ID -809995
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 18 Mtr. High Mast Pole of approved make with motorised lowering rising system for light bracket/frame, hot dip galvanized inside & outside, having pole sheet thickness 3mm Top & 4mm Bottom, Top dia minimum 150mm, bottom dia minimum 410mm, base plate suitable for wind velocity as per IS 875 part 3 ...............................................and satisfaction to the engineer in-charge. Construction of suitable shallow foundation with RCC M-25 design mix for the high mast considering the safe soil bearing capacity .............................................. shall be deemed included in quoted unit rate. Assembly and erection supervision of above mentioned mast ............................................. complete as required. | 2.00 | Job | 429250.00 | 220000.00 | 440000.00 | 300000.00 | 600000.00 | 460000.00 | 920000.00 | 440000.00 | Awasthi Electric Works
2.00 | SITC of 250W LED Flood Light Fixture having die cast aluminium housing & toughened flat glass cover confirming to IP 66 ingress protection (System Lumen – 30045Lm, High Power LED with Lenses, 120LPW, PF>0.95, THD<10% st full load, CRI>70, Phase to Phase protection at 440V & >300V Auto Cut and Restart including fixing on the bracket, connections etc. complete as required. Luminaire should have minimum lifetime of 50000 burning hour and 5 years warrantee as per the technical specifications. | 20.00 | Nos. | 14645.00 | 6500.00 | 130000.00 | 7500.00 | 150000.00 | 11000.00 | 220000.00 | 130000.00 | Awasthi Electric Works
3.00 | SITC of LED type Aviation obstruction light including fixing, connections etc. complete as required. Luminaire should have minimum lifetime of 50000 burning hour and 5 years warrantee as per the technical specifications. . | 4.00 | Nos. | 4919.00 | 5500.00 | 22000.00 | 4500.00 | 18000.00 | 5500.00 | 22000.00 | 18000.00 | Dubey Trading Company
4.00 | Supply, installation, testing and commissioning of dust & vermin proof outdoor, IP-54, floor mounted feeder pillar of suitable size on cement concrete foundations generally conforming to IS 5039 and to withstand rough usage and weather. The panel shall be fabricated with 14 SWG M.S.sheet with hinged door on front side with locking arrangement, suitable angle/ channels frame in the bottom, legs for grouting in foundation, openable cable protection covers at bottom portion, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, etc.as per the drawings. Incomer: 63 Amps.4P,25 KA MCCB (Ics = lcu= 100%) with extended rotary handle-- 1 No. MCBs connecting copper strip to connect all outgoing MCBs LED type indication lamps with control fuse and bases-3 Nos. Outgoing : 6-32 Amps.SP,MCB C-series 10 KA -11 Nos. 15 Amps Socket and switch -1 set | 2.00 | Nos. | 29795.00 | 58500.00 | 117000.00 | 47500.00 | 95000.00 | 25000.00 | 50000.00 | 50000.00 | SARANBIR DHINDSA
5.00 | Supply of 4 Core x 25 Sqmm Aluminium conductor XLPE insulated armoured power cable of 1.1 KV grade, confirming to IS 7098 (Part - I) with upto date ammendment. | 250.00 | Metre | 238.00 | 220.00 | 55000.00 | 300.00 | 75000.00 | 300.00 | 75000.00 | 55000.00 | Awasthi Electric Works
6.00 | Supplying and making end termination with brass compression gland and aluminium lugs for size 4 x 25 sqmm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required : | 4.00 | Set | 259.00 | 225.00 | 900.00 | 500.00 | 2000.00 | 200.00 | 800.00 | 800.00 | SARANBIR DHINDSA
7.00 | Supply of 63 mm outer dia PN6 , PE 80 HDPE Pipe as per IS:4984 suitable to lay in underground. | 210.00 | Metre | 98.00 | 200.00 | 42000.00 | 210.00 | 44100.00 | 150.00 | 31500.00 | 31500.00 | SARANBIR DHINDSA
8.00 | Laying of 63mm dia HDPE direct in underground at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 125.00 | Metre | 191.00 | 100.00 | 12500.00 | 120.00 | 15000.00 | 40.00 | 5000.00 | 5000.00 | SARANBIR DHINDSA
9.00 | Laying of additional 63mm dia HDPE Pipe direct in underground in the same trench in one tier horizontal formation at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 60.00 | Metre | 126.00 | 90.00 | 5400.00 | 100.00 | 6000.00 | 40.00 | 2400.00 | 2400.00 | SARANBIR DHINDSA
10.00 | Laying of 63mm dia HDPE Pipe in underground for laying of cable across pavement / road at depth of upto 2 mtr through Horizontal Directional Drilling Method (manual or motorised) etc. complete as required. | 25.00 | Metre | 1818.00 | 880.00 | 22000.00 | 800.00 | 20000.00 | 750.00 | 18750.00 | 18750.00 | SARANBIR DHINDSA
11.00 | Laying of one number PVC insulated and PVC sheathed / XPLE power cable 1.1 KVgrade/5 KV grade AFL cable of size not exceeding 25 sqmm in the existing HDPE pipe/RCC / HUME / M.S pipe as reqd. | 210.00 | Metre | 24.00 | 50.00 | 10500.00 | 25.00 | 5250.00 | 20.00 | 4200.00 | 4200.00 | SARANBIR DHINDSA
12.00 | Laying of one number PVC insulated and PVC sheathed / XPLE power cable 1.1KVgrade/5 KV grade AFL cable of size not exceeding 25 sqmm in the existing masonary open duct as required. | 30.00 | Metre | 22.00 | 30.00 | 900.00 | 30.00 | 900.00 | 20.00 | 600.00 | 600.00 | SARANBIR DHINDSA
13.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Job | 6215.00 | 8500.00 | 34000.00 | 6000.00 | 24000.00 | 3000.00 | 12000.00 | 12000.00 | SARANBIR DHINDSA
14.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection, excavation and re-filling as required. | 20.00 | Metre | 260.00 | 200.00 | 4000.00 | 160.00 | 3200.00 | 100.00 | 2000.00 | 2000.00 | SARANBIR DHINDSA
15.00 | SITC of CCR by OEM of AAI approved make ( Aeronautical Ground Light Item): Supply, Installation, testing & commisioning of ICAO compliant indoor type microprocessor based, air cooled constant current regulator (CCR) of thyristor control electronic type suitable for use on 240 VAC 50/60 Hz, input AC supply with below mentioned output power at 6.6 Amps with 5 step variation of current output suitable for local and remote control operation with 24/28 VDC control supply complete with output current indicated on multifunctional digital display, over current, over voltage, earth fault protection and earth leakage meter, positive back indication equipments relay contactor etc. as required for airfield ground lighting as per specification of following rating: 7.5 KW MP CCR at 6.6 Amps, supply voltage 240VAC and Tapping at 4 KW | 1.00 | No. | 348450.00 | 295000.00 | 295000.00 | 230438.00 | 230438.00 | 300000.00 | 300000.00 | 230438.00 | Dubey Trading Company
| Total in Figures |  |  |  |  | 1191200.00 |  | 1288888.00 |  | 1664250.00
Lowest Amount Quoted BY: Awasthi Electric Works(1191200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Development of Fursatganj Airport at Uttar Pradesh for RCS Operation _ Construction of Apron Taxiway and Associated Works. SH_ Provision of Apron Flood Lights at Fursatganj Airport Tender ID: 2024_AAI_221456_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works (BID ID -810963) | 1191200.00 | L1
| 2 | Dubey Trading Company (BID ID -812678) | 1288888.00 | L2
| 3 | SARANBIR DHINDSA (BID ID -809995) | 1664250.00 | L3