## BoQ1
Government eProcurement System Created By: AKSHAYA KUMAR NAYAK Created Date/Time: 17-Jan-2025 11:51 AM Tender Title: Replacement supply installation and commissioning of LT power distribution panels in HFMD shops(Bldg No 2 and 5) inside the Factory area at OFMK Tender ID: 2024_AVNL_209916_1
Tender Inviting Authority: CHIEF GENERAL MANAGER, ORDNANCE FACTORY MEDAK HYDERABAD A UNIT OF AVNL
Name of Work: Replacement, supply, installation and commissioning of LT power distribution panels in HFMD shops(Bldg.No.2 & 5) inside the Factory area at OFMK
Contract No: 76026/ TE-09/ OFMK/EOC/ HFMD LT PANEL/ 2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | R Pandurangam and sons (GSTN-36AACFP1646F1ZG) BID ID -757654 |  | JITENDRA ELECTRICALS (GSTN-24AACFJ9752E1ZE) BID ID -759041 |  | BBN ENERGY SYSTEMS PVT LTD (GSTN-06AAECB3449D1Z0) BID ID -759162
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation & Commissioning of LT power distribution Panel: LT power distribution panel indoor type, front operated, fixed type construction, fully compartmentalized, hinged doors at front and rear with screw type knobs, separate hinged doors for incomer and each individual outgoing feeder. Indoor floor mounted with bus bars access from front and cable termination access from rear side. Cubical type uniform depth throughout the panel. As per attached Annexure-1 for technical specification and scope of work.
1.01 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without MCCBs) i)MCCB, 3 pole, 400A, 36 KA as incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 125A, 16KA-10 Nos Panel shall be designed as per Sl. No.1 of specification. | 4.00 | Each | 100.00 | 300000.00 | 1200000.00 | 265800.00 | 1063200.00 | 224229.50 | 896918.00 | 896918.00 | BBN ENERGY SYSTEMS PVT LTD
1.02 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 800 amps, 4 pole,50 KA,manual draw out type as Incomer. and the following as outgoing MCCBs ii) MCCB, 3 pole, 250 A, 36KA -2Nos iii) MCCB, 3 pole, 160A, 36KA-4 Nos. iv) MCCB, 3 pole, 125A, 16KA-4 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work. | 5.00 | Each | 100.00 | 400000.00 | 2000000.00 | 333800.00 | 1669000.00 | 240130.00 | 1200650.00 | 1200650.00 | BBN ENERGY SYSTEMS PVT LTD
1.03 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 1000 amps, 4 pole,50 KA,manual draw out type as Incomer and the following as outgoing ACB’s & MCCBs ii) ACB, 4 pole, 630A, 50KA-2 Nos. iii) MCCB, 3 pole, 400A, 36KA-2 Nos. iv) MCCB, 3 pole, 160A, 36KA-3 Nos Panel shall be designed as per Sl. No.1 of specification and scope of work. | 2.00 | Each | 10.00 | 700000.00 | 1400000.00 | 448800.00 | 897600.00 | 304251.20 | 608502.40 | 608502.40 | BBN ENERGY SYSTEMS PVT LTD
1.04 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 1000 amps, 4 pole,50 KA,manual draw out type as Incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 400A, 36KA-2 Nos. iii) MCCB, 3 pole, 250A, 36KA-3 Nos. iv.) MCCB, 3 pole, 160A, 36KA-3 Nos. v) MCCB, 3 pole, 125A, 16KA-7 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work. | 7.00 | Each | 10.00 | 575000.00 | 4025000.00 | 507800.00 | 3554600.00 | 341893.20 | 2393252.40 | 2393252.40 | BBN ENERGY SYSTEMS PVT LTD
1.05 | Indoor power panel : Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs ) i) Air circuit breaker 800 amps, 4 pole,50 KA,manual draw out type as Incomer. Panel shall be designed as per Sl. No.1 of specification and scope of work. | 2.00 | Each | 10.00 | 145000.00 | 290000.00 | 112800.00 | 225600.00 | 97350.00 | 194700.00 | 194700.00 | BBN ENERGY SYSTEMS PVT LTD
1.06 | Indoor power panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without MCCBs) i) MCCB, 3 pole,400A, 36 KA as incomer. Panel shall be designed as per Sl. No.1 of specification. | 1.00 | Each | 100.00 | 75000.00 | 75000.00 | 50800.00 | 50800.00 | 64900.00 | 64900.00 | 50800.00 | JITENDRA ELECTRICALS
1.07 | Indoor power distribution panel : Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (withoutMCCBs) i)MCCB, 3 pole , 400A ,36 KA as incomer and the following as outgoing MCCBs ii) MCCB, 3 pole,250A,36KA-01 No. Iii) MCCB, 3 pole, 160A, 36KA-02 Nos. Iv) MCCB, 3 pole, 125A, 16KA-02 Nos. Panel shall be designed as per Sl. No.1 of specification. | 3.00 | Each | 100.00 | 150000.00 | 450000.00 | 152800.00 | 458400.00 | 129800.00 | 389400.00 | 389400.00 | BBN ENERGY SYSTEMS PVT LTD
1.08 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following(without MCCBs) i)MCCB, 3 pole , 400A ,36 KA as incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 160A, 36KA-04 Nos. iii) MCCB, 3 pole, 125A, 16KA-06 Nos. Panel shall be designed as per Sl. No.1 of specification. | 10.00 | Each | 10.00 | 300000.00 | 3000000.00 | 266800.00 | 2668000.00 | 203137.00 | 2031370.00 | 2031370.00 | BBN ENERGY SYSTEMS PVT LTD
1.09 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 1000 amps, 4 pole,50 KA,manual draw out type as Incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 400A, 36KA-1 No. iii) MCCB, 3 pole, 250A, 36KA-2 Nos. iv.) MCCB, 3 pole, 125A, 16KA-7 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work | 2.00 | Each | 10.00 | 425000.00 | 850000.00 | 346800.00 | 693600.00 | 242077.00 | 484154.00 | 484154.00 | BBN ENERGY SYSTEMS PVT LTD
1.10 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 1000 amps, 4 pole,50 KA,manual draw out type as Incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 400A, 36KA-2 Nos. iii) MCCB, 3 pole, 250A, 36KA-2 Nos. iv.) MCCB, 3 pole, 160A, 36KA-3 Nos. v) MCCB, 3 pole, 125A, 16KA-3 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work | 4.00 | Each | 10.00 | 425000.00 | 1700000.00 | 349800.00 | 1399200.00 | 259600.00 | 1038400.00 | 1038400.00 | BBN ENERGY SYSTEMS PVT LTD
1.11 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 800 amps, 4 pole,50 KA,manual draw out type as Incomer and the following as outgoing MCCBs ii) MCCB, 3 pole, 400A, 36KA-1 No. iii) MCCB, 3 pole, 250A, 36KA-2 Nos. iv) MCCB, 3 pole, 160A, 36KA-3 Nos. v) MCCB, 3 pole, 125A, 16KA-4 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work | 5.00 | Each | 100.00 | 425000.00 | 2125000.00 | 338000.00 | 1690000.00 | 257004.00 | 1285020.00 | 1285020.00 | BBN ENERGY SYSTEMS PVT LTD
1.12 | Indoor power distribution panel: Supply, Installation & Commissioning of LT power distribution Panel shall have provision of the following (without ACBs and MCCBs) i) Air circuit breaker 1000 amps, 4 pole, 50 KA, manual draw out type as Incomer and the following as outgoing ACB’s & MCCBs ii) ACB, 4 pole, 630A, 50KA-1 No. iii) MCCB, 3 pole, 400A, 36KA-2 Nos. iv) MCCB, 3 pole, 250A, 36KA-2 Nos. v) MCCB, 3 pole, 160A, 36KA-3 Nos. vi) MCCB, 3 pole, 125A, 16KA-3 Nos. Panel shall be designed as per Sl. No.1 of specification and scope of work. | 5.00 | Each | 100.00 | 575000.00 | 2875000.00 | 425800.00 | 2129000.00 | 373824.00 | 1869120.00 | 1869120.00 | BBN ENERGY SYSTEMS PVT LTD
2.00 | Dismantling of Panels: Dismantling of existing Electrical panels including disconnection of cables, glands etc completely and shifting to stores as instructed by EIC. | 50.00 | Each | 10.00 | 5000.00 | 250000.00 | 5800.00 | 290000.00 | 53607.40 | 2680370.00 | 250000.00 | R Pandurangam and sons
3.00 | Air circuit Breaker (ACB): Supply and Fixing of ACB 4 Pole, 415 V, Manual Draw out type with microprocessor release of capacity 1000 Amps, 50KA breaking capacity with Earth fault, Over load, short circuit protection, shunt trip, Ics=Icu=Icw (1 sec) and auxiliary contacts, LCD Back light Display, Front ON/OFF indication, spring charge/Discharge indication, 3 distinct mechanical positions indication, Make GE /Areva T&D/Schneider/ Siemens/ L&T/ABB The incoming/ outgoing ACBs are to be installed and commissioned in the LT Distribution Panel as mentioned Sl. No.1 of specification and scope of work | 20.00 | Each | 10.00 | 127000.00 | 2540000.00 | 127000.00 | 2540000.00 | 127204.00 | 2544080.00 | 2540000.00 | R Pandurangam and sons, JITENDRA ELECTRICALS
4.00 | Air circuit Breaker (ACB): Supply and Fixing of ACB 4 Pole, 415 V, Manual Draw out type with microprocessor release of capacity 800 Amps, 50KA breaking capacity with Earth fault, Over load, short circuit protection, shunt trip, Ics=Icu=Icw (1 sec) and auxiliary contacts, LCD Back light Display, Front ON/OFF indication, spring charge/Discharge indication, 3 distinct mechanical positions indication, Make GE/Areva T&D/Schneider/Siemens/L&T/ABB The incoming/outgoing ACBs are to be installed and commissioned in the LT Distribution Panel as mentioned Sl. No.1 of specification and scope of work | 12.00 | Each | 10.00 | 120000.00 | 1440000.00 | 120000.00 | 1440000.00 | 123310.00 | 1479720.00 | 1440000.00 | R Pandurangam and sons, JITENDRA ELECTRICALS
5.00 | Air circuit Breaker (ACB): Supply and Fixing of ACB 4 Pole, 415 V, Manual Draw out type with microprocessor release of capacity 630 Amps, 50KA breaking capacity with Earth fault, Over load, short circuit protection, shunt trip, Ics=Icu=Icw (1 sec) and auxiliary contacts, LCD Back light Display, Front ON/OFF indication, spring charge/Discharge indication, 3 distinct mechanical positions indication, Make GE/Areva T&D/Schneider/ Siemens/ L&T/ABB The incoming/ outgoing ACBs are to be installed and commissioned in the LT Distribution Panel as mentioned Sl. No.1 of specification and scope of work | 9.00 | Each | 10.00 | 117000.00 | 1053000.00 | 120000.00 | 1080000.00 | 119416.00 | 1074744.00 | 1053000.00 | R Pandurangam and sons
6.00 | Moulded Case circuit Breaker (MCCB): Supply and Fixing of MCCB 3 Pole, 415 V, Adjustable type, 400 Amps with breaking capacity 36 KA. The Incoming & outgoing Moulded Case Circuit Breakers are to be installed and commissioned in the LT Distribution Panel as mentioned above, Confirms IEC 60947, IS 13947. Make: GE/Schneider /Siemens/ L&T/ ABB. | 61.00 | Each | 10.00 | 23200.00 | 1415200.00 | 23000.00 | 1403000.00 | 15316.40 | 934300.40 | 934300.40 | BBN ENERGY SYSTEMS PVT LTD
7.00 | Moulded Case circuit Breaker (MCCB): Supply and Fixing of MCCB 3 Pole, 415 V, Adjustable type, 250 Amps with breaking capacity 36 KA. The incoming & outgoing Moulded Case Circuit Breakers are to be installed and commissioned in the LT Distribution Panel as mentioned above, Confirms IEC 60947, IS 13947. Make:- GE/Schneider /Siemens/ L&T/ ABB. | 66.00 | Each | 10.00 | 16600.00 | 1095600.00 | 17000.00 | 1122000.00 | 11552.20 | 762445.20 | 762445.20 | BBN ENERGY SYSTEMS PVT LTD
8.00 | Moulded Case circuit Breaker (MCCB): Supply and Fixing of MCCB 3 Pole, 415 V, Fixed type, 160 Amps with breaking capacity 36 KA. The Incoming & outgoing Moulded Case Circuit Breakers are to be installed and commissioned in the LT Distribution Panel as mentioned above, Confirms IEC 60947, IS 13947. Make:- GE/Schneider /Siemens/ L&T/ ABB. | 135.00 | Each | 10.00 | 8900.00 | 1201500.00 | 9600.00 | 1296000.00 | 10643.60 | 1436886.00 | 1201500.00 | R Pandurangam and sons
9.00 | Moulded Case circuit Breaker (MCCB): Supply and Fixing of MCCB 3 Pole, 415 V, Fixed type, 125 Amps with breaking capacity 16 KA. The Incoming & outgoing Moulded Case Circuit Breakers are to be installed and commissioned in the LT Distribution Panel as mentioned above, Confirms IEC 60947, IS 13947. Make:- GE/Schneider /Siemens/ L&T/ ABB. | 236.00 | Each | 10.00 | 5100.00 | 1203600.00 | 5650.00 | 1333400.00 | 3894.00 | 918984.00 | 918984.00 | BBN ENERGY SYSTEMS PVT LTD
10.00 | Earthing: Earthing complete with Galvanised steel earth plate electrode 60x60 cm X 6 mm thick, buries directly in ground (Earth pit not less than 2.25 meters deep below ground level) with top edge of the plate not less than 1.5 meters below normal ground level, connected to galvanised iron or steel strip 25x4 mm as earthing lead by means of bolts, nuts, check nuts and watchers of GI or steel all as shown in Electrical plate no 3 connected to earth test point as specified or indicated including testing on completion. | 15.00 | each | 100.00 | 9000.00 | 135000.00 | 11800.00 | 177000.00 | 8437.00 | 126555.00 | 126555.00 | BBN ENERGY SYSTEMS PVT LTD
11.00 | Earth continuity conductor: M&L Earth continuity conductor for or main earthing lead fixed to wall on batten or recess chase or buried in ground or drawn in conduit/pipe or fixed to pole or any other indicated situation for loop earthing etc, as required 25x4 mm GI strip | 600.00 | RM | 10.00 | 100.00 | 60000.00 | 250.00 | 150000.00 | 220.66 | 132396.00 | 60000.00 | R Pandurangam and sons
12.00 | GI PIPE: Supply and fixing of GI pipe to protect earthing strip 40 mm dia. medium grade complete all as specified and directed | 15.00 | RM | 10.00 | 400.00 | 6000.00 | 485.00 | 7275.00 | 375.12 | 5626.80 | 5626.80 | BBN ENERGY SYSTEMS PVT LTD
13.00 | GI PIPE: Supply and fixing of GI pipe to protect earthing strip 20 mm dia. medium grade complete all as specified and directed | 15.00 | RM | 10.00 | 250.00 | 3750.00 | 250.00 | 3750.00 | 142.78 | 2141.70 | 2141.70 | BBN ENERGY SYSTEMS PVT LTD
14.00 | Excavation: Excavating in trenches in hard/dense soil not exceeding 1.5 metre wide and not exceeding 1.5 metre depth over areas in Hard/Dense soil getting out complete all as specified and directed. | 38.00 | cu.m | 100.00 | 800.00 | 30400.00 | 945.00 | 35910.00 | 908.60 | 34526.80 | 30400.00 | R Pandurangam and sons
15.00 | cement concrete: providing cement concrete cast in situ for each pit chamber slightly rounded or chamfer angles including finishing by using type B1 1:2:4 (20mm graded aggregate complete all as specified by the EIC | 3.00 | cu.m | 100.00 | 6500.00 | 19500.00 | 9400.00 | 28200.00 | 15576.00 | 46728.00 | 19500.00 | R Pandurangam and sons
16.00 | precast cement concrete: B1 1:2:4 (20mm graded aggregate) in covers slabs for earth pits with faces complete all as specified and diriected | 1.00 | cu.m | 10.00 | 7000.00 | 7000.00 | 9400.00 | 9400.00 | 15576.00 | 15576.00 | 7000.00 | R Pandurangam and sons
17.00 | mild steel bar 8 mm dia. over cut to length, bend to shape for hooking quality conforming to GD 1, IS 432(pt.1) complete all as specified by the EIC | 100.00 | kg | 10.00 | 120.00 | 12000.00 | 175.00 | 17500.00 | 97.75 | 9775.00 | 9775.00 | BBN ENERGY SYSTEMS PVT LTD
18.00 | Synthetic painting to plastered surfaces: Surfaces of any description over 10 cm girth or width. Synthetic enamel single coat. | 15.00 | sq.m. | 10.00 | 200.00 | 3000.00 | 600.00 | 9000.00 | 51.92 | 778.80 | 778.80 | BBN ENERGY SYSTEMS PVT LTD
19.00 | Writing letters or figures (Block, Roman, italic or Indian) n exc 30cm high | 100.00 | per 10Nos (per cm of height) | 100.00 | 500.00 | 50000.00 | 115.00 | 11500.00 | 64.90 | 6490.00 | 6490.00 | BBN ENERGY SYSTEMS PVT LTD
| Total in Figures |  |  |  |  | 30515550.00 |  | 27452935.00 |  | 24668510.50
Lowest Amount Quoted BY: BBN ENERGY SYSTEMS PVT LTD(24668510.50)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement supply installation and commissioning of LT power distribution panels in HFMD shops(Bldg No 2 and 5) inside the Factory area at OFMK Tender ID: 2024_AVNL_209916_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BBN ENERGY SYSTEMS PVT LTD (BID ID -759162) | 24668510.50 | L1
| 2 | JITENDRA ELECTRICALS (BID ID -759041) | 27452935.00 | L2
| 3 | R Pandurangam and sons (BID ID -757654) | 30515550.00 | L3