## BoQ1
Government eProcurement System Created By: ANKIT SHARMA Created Date/Time: 05-Jun-2024 11:25 AM Tender Title: INTERIOR, MEP AND RELATED WORKS FOR OFFICE BUILDING AT RANCHI, JHARKHAND Tender ID: 2024_GAIL_188833_1
Tender Inviting Authority: GAIL India Ltd
Name of Work: Project : INTERIOR, MEP AND RELATED WORKS FOR OFFICE BUILDING AT RANCHI, JHARKHAND
Contract No: GAIL/NOIDA/C&P/PROJ/INT. WORKS-OFC RANCHI/23-58
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | MANNU LAL AND SONS (GSTN-07AAAFM7256N1ZV) BID ID -693978 |  | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED (GSTN-06AACCR6279F1Z8) BID ID -694439 |  | Innovations Workspace Solutions Pvt. Ltd.(GSTN-NA)--690936
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | CIVIL AND INTERIOR RELATED WORKS
2.00 | SECTION-A: EARTHWORK
3.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, for all leads and all lifts, disposed earth to be levelled and neatly dressed. All kinds of soil | 50.00 | M3 |  | 200.00 | 10000.00 | 350.00 | 17500.00 | 275.00 | 13750.00 | 10000.00 | MANNU LAL AND SONS
4.00 | Disposal of excavated excess earth/ rock away from the site including conveyance of materials upto an average lead of 5 KM away from the site, and corresponding required lift, loading, unloading etc. complete as directed by the Engineer-in-charge. (The quantity considered shall be net quantity of capacity of truck after deduction of 20% for looseness) (Considering the maximum disposal location at 5 KM distance and is to be done at designated area as per prevailing local norms at Contractor's own responsibility including any royalties, etc. all) By mechanical transport including loading, unloading and stacking. (Lead upto 5 KM away from the site) | 40.00 | M3 |  | 300.00 | 12000.00 | 250.00 | 10000.00 | 375.00 | 15000.00 | 10000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
5.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, for all leads and for all lift. | 10.00 | M3 |  | 250.00 | 2500.00 | 196.00 | 1960.00 | 175.00 | 1750.00 | 1750.00 | Innovations Workspace Solutions Pvt. Ltd.
6.00 | Surface dressing of the ground including removing vegetation and inequalities and disposal of rubbish, for all leads and all lifts. All kinds of soil | 75.00 | M2 |  | 75.00 | 5625.00 | 34.15 | 2561.25 | 35.00 | 2625.00 | 2561.25 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
7.00 | Excavating, supplying stacking, filling and compaction of Locally available Good earth/ Moorum (including royalty) by mechanical transport for all leads also including ramming and watering of the earth in layers not exceeding 20 cm and compacted complete. | 5.00 | M3 |  | 750.00 | 3750.00 | 700.50 | 3502.50 | 750.00 | 3750.00 | 3502.50 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
8.00 | Extra for Disposal against item No. A.2 and J.61 beyond 5 KM per additional KM per Cubic metre away from the site, of excavated excess earth/ rock/ complete unserviceable material/ debris/ steel/ moorum/ building rubbish/ malba/ similar unserviceable, dismantled or waste material including conveyance of materials as directed by the Engineer-in-charge. (At designated area as per prevailing local norms at Contractor's own responsibility including any royalties, etc. all) By mechanical transport including loading, unloading and stacking. (PER means per additional KM per Cubic metre) | 50.00 | PER |  | 25.00 | 1250.00 | 380.00 | 19000.00 | 125.00 | 6250.00 | 1250.00 | MANNU LAL AND SONS
9.00 | SECTION-B: CONCRETE WORKS
10.00 | Providing and laying in position cement concrete of specified grade INCLUDING the cost of centering and shuttering - All work at all level: 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | 5.00 | M3 |  | 7500.00 | 37500.00 | 7294.00 | 36470.00 | 10750.00 | 53750.00 | 36470.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
11.00 | SCREED CONCRETE Providing and laying in position cement concrete of specified grade INCLUDING the cost of centering and shuttering - All work : Concrete 1:3:6 (1 cement:3 Coarse Sand:6 graded stone aggregate 20 mm nominal size) of 70-75 mm average thickness. | 7000.00 | M2 |  | 400.00 | 2800000.00 | 215.00 | 1505000.00 | 695.00 | 4865000.00 | 1505000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
12.00 | Providing and injecting approved grout in proportion recommended by the manufacturer into cracks/honey-comb area of concrete/ masonry by suitable gun/pump at required pressure including Providing and inserting 12mm dia galvanised steel injection nipple in honey comb area and along crack line including drilling of holes of required diameter (20mm to 30mm) up to depth from 30mm to 80mm at required spacing and making the hole & crack dust free by blowing compressed air, sealing the distance between injection nipple with adhesive chemical of approved make and allow it to cure complete as per direction of Engineer-In-Charge and cutting of nipples after curing etc. complete as per directions of Engineer-in-Charge. (The payment shall be made on the basis of actual weight of approved grout injected.) Epoxy injection grout in concrete/ RCC work of approved make | 200.00 | KG |  | 650.00 | 130000.00 | 119.00 | 23800.00 | 75.00 | 15000.00 | 15000.00 | Innovations Workspace Solutions Pvt. Ltd.
13.00 | Providing and laying cement concrete/ RCC in parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor and all similar places of retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses etc., at all levels, INCLUDING the cost of centering, shuttering and finishing but EXCLUDING the cost of reinforcement: 1:1½:3 (1 cement : 1½ coarse sand : 3 graded stone aggregate 20 mm nominal size) | 5.00 | M3 |  | 9500.00 | 47500.00 | 10357.00 | 51785.00 | 11750.00 | 58750.00 | 47500.00 | MANNU LAL AND SONS
14.00 | SECTION-C: REINFORCED CEMENT CONCRETE WORKS
15.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement,, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads and heights ; INCLUDING the cost of centering, shuttering (for all elements and shuttering for slab upto 6.0 mtr. height (in single length)), finishing but EXCLUDING the cost of reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works (Suspended floors, roofs, landing, beams, coloumn, slab and balconies, Retaining wall, Foundations, footings, bases of columns, Walls (any thickness) including attached pilasters, buttresses, plinth and string courses, Lintels, beams, plinth beams, girders, bressumers and cantilevers, Columns, Pillars, Piers, Abutments, Posts and Struts, stairs, etc.) at all level: Concrete of M25 grade with minimum cement content of 330 kg /cum | 2.00 | M3 |  | 10000.00 | 20000.00 | 9439.00 | 18878.00 | 11750.00 | 23500.00 | 18878.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
16.00 | Add for using extra cement in the items of design mix over and above the specified cement content therein up to 10% of the minimum specified cement content in design mix (QT means Quintal here) | 2.00 | QT |  | 650.00 | 1300.00 | 1134.00 | 2268.00 | 1550.00 | 3100.00 | 1300.00 | MANNU LAL AND SONS
17.00 | Steel Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level: Thermo-Mechanically Treated bars of grade Fe-500D or more | 300.00 | KG |  | 120.00 | 36000.00 | 107.00 | 32100.00 | 98.00 | 29400.00 | 29400.00 | Innovations Workspace Solutions Pvt. Ltd.
18.00 | Add for plaster drip course/ groove in plastered surface or moulding to R.C.C. projections. | 5.00 | M |  | 110.00 | 550.00 | 78.00 | 390.00 | 250.00 | 1250.00 | 390.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
19.00 | SECTION-D MASONRY WORK
20.00 | Brick work with non modular fly ash bricks conforming to IS:12894, class designation 7.5 average compressive strength all works at all level in: Cement mortar 1:6 (1 cement : 6 Coarse sand) | 50.00 | M3 |  | 8500.00 | 425000.00 | 8962.00 | 448100.00 | 6500.00 | 325000.00 | 325000.00 | Innovations Workspace Solutions Pvt. Ltd.
21.00 | Half brick masonry with non modular fly ash bricks of class designation 7.5, conforming to IS :12894 INLCUDING providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brick masonry, all works at all level in: Cement mortar 1:4 (1 cement : 4 coarse sand) | 50.00 | M2 |  | 995.00 | 49750.00 | 1132.00 | 56600.00 | 950.00 | 47500.00 | 47500.00 | Innovations Workspace Solutions Pvt. Ltd.
22.00 | SECTION-E:FINISHING WORK
23.00 | 12/ 15 mm cement plaster of mix : 1:6 (1 cement: 6 coarse sand) INCLUDING Scaffolding at all levels. | 200.00 | M2 |  | 450.00 | 90000.00 | 662.00 | 132400.00 | 415.00 | 83000.00 | 83000.00 | Innovations Workspace Solutions Pvt. Ltd.
24.00 | 6 mm cement plaster for all heights including scaffolding etc. complete of mix : 1:3 (1 cement : 3 fine sand) | 50.00 | M2 |  | 425.00 | 21250.00 | 300.00 | 15000.00 | 375.00 | 18750.00 | 15000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
25.00 | Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. (PER means per bag of 50KG Cement Used in Mix here) | 40.00 | PER |  | 25.00 | 1000.00 | 22.00 | 880.00 | 125.00 | 5000.00 | 880.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
26.00 | Providing and applying Plaster of Paris putty of 2 to 4 mm thickness over plastered surface to prepare the surface even and smooth complete. | 50.00 | M2 |  | 330.00 | 16500.00 | 262.00 | 13100.00 | 345.00 | 17250.00 | 13100.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
27.00 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade : Two or more coats on new work INCLUDING primer complete | 4500.00 | M2 |  | 150.00 | 675000.00 | 92.00 | 414000.00 | 185.00 | 832500.00 | 414000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
28.00 | Neat cement punning | 250.00 | M2 |  | 100.00 | 25000.00 | 155.00 | 38750.00 | 345.00 | 86250.00 | 25000.00 | MANNU LAL AND SONS
29.00 | Providing and applying white cement based putty of average thickness 2-3 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete | 4500.00 | M2 |  | 132.00 | 594000.00 | 156.00 | 702000.00 | 110.00 | 495000.00 | 495000.00 | Innovations Workspace Solutions Pvt. Ltd.
30.00 | Distempering with 1st quality acrylic distemper, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre, of approved brand and manufacture, INCLUDING one coat of water thinnable cement primer of approved brand and manufacture and applying additional coats wherever required, to achieve even shade and colour. Two coats | 50.00 | M2 |  | 200.00 | 10000.00 | 186.00 | 9300.00 | 315.00 | 15750.00 | 9300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
31.00 | Finishing walls with textured exterior paint of required shade : New work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/10 sqm | 50.00 | M2 |  | 280.00 | 14000.00 | 223.00 | 11150.00 | 1950.00 | 97500.00 | 11150.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
32.00 | Finishing with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications : Painting wood work with Deluxe Multi Surface Paint of required shade. Two or more coat applied @0.90 ltr/10 sqm over an under coat of primer applied @0.75 ltr/ 10 sqm of approved brand or manufacture | 100.00 | M2 |  | 350.00 | 35000.00 | 193.00 | 19300.00 | 645.00 | 64500.00 | 19300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
33.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 50.00 | M2 |  | 197.00 | 9850.00 | 155.00 | 7750.00 | 255.00 | 12750.00 | 7750.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
34.00 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand) - at all level including scaffolding etc. complete | 50.00 | M2 |  | 600.00 | 30000.00 | 518.00 | 25900.00 | 775.00 | 38750.00 | 25900.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
35.00 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 50.00 | M2 |  | 250.00 | 12500.00 | 160.00 | 8000.00 | 675.00 | 33750.00 | 8000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
36.00 | White washing with lime to give an even shade : New work (three or more coats) | 5000.00 | M2 |  | 50.00 | 250000.00 | 39.00 | 195000.00 | 110.00 | 550000.00 | 195000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
37.00 | SECTION-F: FLOORING AND CLADDING WORK
38.00 | Polished Kota stone slab in flooring over 20 mm (average) thick base laid over with base of cement mortar 1 : 4 (1 cement : 4 coarse sand), and in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) INCLUDING pre finished nosing to treads of steps, and risers using single length up to 2.00 metre, rubbing, rounding and polishing complete and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing, rounding and polishing complete, 20 mm thick Polished Kota stone | 880.00 | M2 |  | 1750.00 | 1540000.00 | 2354.00 | 2071520.00 | 1975.00 | 1738000.00 | 1540000.00 | MANNU LAL AND SONS
39.00 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm (thickness to be specified by the manufacturer), of 1st quality conforming to IS : 15622, of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, laid on 20 mm thick bed of cement mortar 1:4 (1 Cement : 4 Coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including pointing the joints with white cement and matching pigments etc., complete. | 20.00 | M2 |  | 1000.00 | 20000.00 | 1315.00 | 26300.00 | 1650.00 | 33000.00 | 20000.00 | MANNU LAL AND SONS
40.00 | Providing and fixing Ist quality Ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 220.00 | M2 |  | 1100.00 | 242000.00 | 1267.00 | 278740.00 | 1550.00 | 341000.00 | 242000.00 | MANNU LAL AND SONS
41.00 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement including cement slurry, including the cost of nosing of steps etc. complete. 40mm thick with 20mm nominal size stone aggregate. | 50.00 | M2 |  | 750.00 | 37500.00 | 614.00 | 30700.00 | 775.00 | 38750.00 | 30700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
42.00 | Providing and fixing 18 mm thick Polished Granite stone flooring\ cladding in required design and patterns, in linear as well as curvilinear portions of the building all complete/ gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations, for wall lining (veneer work) including dado, skirting, risers of steps etc., of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including fixing in facia and drops of width upto 150 mm with epoxy resin based adhesive, including cleaning etc. complete and providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete and rubbing, curing, edge moulding (including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge) and polishing of edges to give high gloss finish etc. complete at all levels. Granite stone slab of any colour and texture as approved for all granite works with minimum base rate of Approx Rs. 2000/ sqm. | 1400.00 | M2 |  | 4145.00 | 5803000.00 | 4481.00 | 6273400.00 | 3965.00 | 5551000.00 | 5551000.00 | Innovations Workspace Solutions Pvt. Ltd.
43.00 | Providing and fixing 18 mm thick stone slab with table rubbed, edges rounded and polished, fixed in urinal partitions by cutting a chase of appropriate width with chase cutter and embedding the stone in the chase with epoxy grout or with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 6 mm nominal size) as per direction of Engineer-in-charge and finished smooth. Granite Stone of approved shade with minimum base rate of Approx Rs. 2000/ sqm. | 20.00 | M2 |  | 3800.00 | 76000.00 | 4051.00 | 81020.00 | 4850.00 | 97000.00 | 76000.00 | MANNU LAL AND SONS
44.00 | Providing and laying vitrified tiles for flooring laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) and for wall lining (veneer work) including dado, skirting, risers of steps etc., over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand) in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS: 15622, of approved make, in all colours and shades, jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joints with white cement and matching pigments etc., complete.
45.00 | Size of Tile 600x600 mm | 1200.00 | M2 |  | 1244.00 | 1492800.00 | 1553.00 | 1863600.00 | 1325.00 | 1590000.00 | 1492800.00 | MANNU LAL AND SONS
46.00 | Size of Tile 1000x1000 mm | 2000.00 | M2 |  | 1600.00 | 3200000.00 | 2089.00 | 4178000.00 | 1675.00 | 3350000.00 | 3200000.00 | MANNU LAL AND SONS
47.00 | Providing and laying Vitrified tiles for flooring laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) and for wall lining (veneer work) including dado, skirting, risers of steps etc., over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand) in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only. Laying of tiles will be done with the notch trowel, plier, wedge, clips of required thickness, levelling system and rubber mallet for placing the tiles gently and easily.
48.00 | Double charge vitrified tile polished finish of - Size of Tile 1000 x 1000 mm | 1000.00 | M2 |  | 1425.00 | 1425000.00 | 1801.00 | 1801000.00 | 1675.00 | 1675000.00 | 1425000.00 | MANNU LAL AND SONS
49.00 | Glazed vitrified tiles polished finish of size
50.00 | Size of Tile 600 x 600 mm | 400.00 | M2 |  | 1300.00 | 520000.00 | 1502.00 | 600800.00 | 1325.00 | 530000.00 | 520000.00 | MANNU LAL AND SONS
51.00 | Size of Tile 600 x 1200 mm | 500.00 | M2 |  | 1600.00 | 800000.00 | 1798.00 | 899000.00 | 1325.00 | 662500.00 | 662500.00 | Innovations Workspace Solutions Pvt. Ltd.
52.00 | Glazed Vitrified tiles Matt/Antiskid finish of size
53.00 | Size of Tile 600 x 600 mm | 200.00 | M2 |  | 1300.00 | 260000.00 | 1464.00 | 292800.00 | 1275.00 | 255000.00 | 255000.00 | Innovations Workspace Solutions Pvt. Ltd.
54.00 | Size of Tile 600 x 1200 mm | 550.00 | M2 |  | 1500.00 | 825000.00 | 1797.00 | 988350.00 | 1325.00 | 728750.00 | 728750.00 | Innovations Workspace Solutions Pvt. Ltd.
55.00 | Providing and laying machine cut, mirror polished 18 mm thick Italian Marble stone in flooring, in required design (Simple geometrical, abstract etc.) and in patterns in combination with Italian marble stones of different colours, shades and finished surface texture etc., in linear portions of the building, all complete as per the architectural drawings, laid over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with white cement slurry @ 4.4 kg/sqm, and for wall lining (veneer work) including dado, skirting, risers of steps etc., in required design and pattern (if required with marble stone slab pieces of different shapes, sizes & texture but of even thickness) on 12 mm (average) thick cement mortar 1:3 (1 cement : 3 coarse sand) laid and jointed with white cement slurry @ 3.3 kg/sqm including pointing with white cement slurry admixed with pigment to match the marble shade, including rubbing, curing and polishing etc. all complete as specified and as directed by the Engineer-in-Charge. 18 mm thick Italian Marble stone slab, Perlato, Rosso verona, Fire Red or Dark Emperadore etc. The stone to be fixed after putting dabs of neat cement on walls & resting stone on them. The Stone to be anchored at bottom and at top with "L" Shaped MS Cleats as per details. Back of stone to be filled with white cement slurry complete. Size of the stone to be atleast 2100mm height /length x 600mm wide. Joints to be minimal and filled with white cement mixed with colour pigment to match colour of stone. The item include polishing the laid stone to give a plain, level and smooth finish complete.
56.00 | For Lift Lobby,Corridor & Reception Flooring with (Botticino Classic ,Grey William, Royal Diana, Statuario Marble, Rosso Verona Perlato, Fire Red or Dark Emperadore etc. with minimum base rate of Approx Rs. 465/Sqft.) | 430.00 | M2 |  | 8231.00 | 3539330.00 | 6603.00 | 2839290.00 | 9750.00 | 4192500.00 | 2839290.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
57.00 | For Lift Lobby,Corridor & Reception Wall dado Marble slabs (Botticino Classic ,Grey William, Royal Diana, Statuario Marble, Rosso Verona Perlato, Fire Red or Dark Emperadore etc. with minimum base rate of Approx Rs. 465/Sqft.) | 230.00 | M2 |  | 8831.00 | 2031130.00 | 6927.00 | 1593210.00 | 9750.00 | 2242500.00 | 1593210.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
58.00 | Crystallization treatment for Italian Marble flooring - Honing, polishing and crystallization of marble/Italian by using single disc machine by filling the gaps with Tenax to match the colour, applying liquid crystallizer (Taski Jontec Terranova or equivalent) on floor, buffing thereafter to give an mirror like glossy shine on the floor surface and providing anti-slip properties. | 660.00 | M2 |  | 600.00 | 396000.00 | 5850.00 | 3861000.00 | 25.00 | 16500.00 | 16500.00 | Innovations Workspace Solutions Pvt. Ltd.
59.00 | Providing and fixing Glass mossaic tiles with minimum base rate of Approx Rs. 2049/ sqm. on finished plain wall surface of size 20 mm x 20 mm x 4 mm in all colour, design , fixing in customize design as per direction of Engineer-in- Charge. The glass mosaic tiles to be fixed on the wall surface with the help of approved adhesive applied at the rate of 2.5 kg per sqm and grouting of the same. The rate is inclusive of all operation, material and required pattern approved by Engineer-in-Charge | 100.00 | M2 |  | 3500.00 | 350000.00 | 3891.00 | 389100.00 | 150.00 | 15000.00 | 15000.00 | Innovations Workspace Solutions Pvt. Ltd.
60.00 | Providing and laying Pre-Laminated Engineered wooden flooring with minimum base rate of Approx Rs. 160/ sqft. (Grade AC4 or AC4+ laminates) 8mm thick, having a good backing layer made up of plastic laminate or melamine, core made up of medium-density fibreboard (MDF),which is less resistant to impact damage and less resistant to being dented by heavy furniture, having a décor layer to give each floor its appearance and consisting of one or more sheets of paper impregnated with melamine resin and top wear layer having clear aluminium oxide finish that protects the decorative layer & imparts the desired level of sheen, from full gloss to low gloss, duly fixed to the base floor using adhesive as approved by the manufacturer. | 500.00 | M2 |  | 2600.00 | 1300000.00 | 5900.00 | 2950000.00 | 2090.00 | 1045000.00 | 1045000.00 | Innovations Workspace Solutions Pvt. Ltd.
61.00 | Providing and fixing removable raised/ false access flooring with system and its components of approved make for different plenum height with possible height adjustment upto 50 mm, comprising of modular load bearing floor panels supported on G.I. rectangular stinger frame work and G.I. Pedestal etc. all complete, as per the architectural drawings, as specified and as directed by Engineer-in-charge consisting of: (a) Providing at required spacing to form modular framework, pedestals made out of GI tube of thickness minimum 2 mm and 25 mm outer diameter, fully welded on to the G.I. Base plate of size 100mm x 100mm x 3mm at the bottom of the pedestal tube, G.I. pedestal head of size 75mmx75mmx3.5 mm welded with GI fully threaded stud 16mm outer diameter with two GI Check nuts screwed on the stud for level adjustment upto 50mm, locking and stabilizing the pedestal head in position at the required level. The pedestals shall be fixed to the subfloor (base) through base plate using epoxy based adhesive of approved make or the machine screw with rawl plug. (b) Stringers system in all steel construction hot dipped galvanized of rectangular size 570x20x30x0.80mm thick having holes at both ends for securing the stringers on to the pedestal head using fully threaded screws ensuring maximum lateral stability in all directions, | 70.00 | M2 |  | 5200.00 | 364000.00 | 5970.00 | 417900.00 | 4550.00 | 318500.00 | 318500.00 | Innovations Workspace Solutions Pvt. Ltd.
62.00 | the grid formed by the pedestal and stringer assembly shall receive the floor panel, this system shall provide adequate solid, rigid support for access floor panel, the system shall provide a minimum clear uninterrupted clearance between the bottom of the floor for electrical conduits and wiring etc. all complete as per the architectural drawings, as specified and as directed by the Engineer-in-charge. (c) Providing and fixing Access Floor panel of 600x600x32 mm medium grade Filled Steel anti static high pressure Lamination of 800H grade (FS800H). Access Floor panel shall be steel welded construction with an enclosed bottom pan with uniform pattern of 64 hemispherical cones. The top and bottom plates of Steel Gauges: top 0.6 mm and bottom 0.7 mm fused spot welded together (minimum 64 welds in each dome and 20 welds along each flange). The panel should be Corroresist epoxy coated for lifetime rust protection and cavity formed by the top and bottom plate is filled with Pyrogrip noncombustible Portland cementitious core mixed with lightweight foaming compound. The access floor shall be factory finished with Anti-static High Pressure laminate with Non Warp technology upto 1mm thickness for superior adhesion and Surface flatness within 0.75mm.The panel is to withstand a Concentrated Load of 363 kgs applied on area 25mm x 25mm without collapse in the centre of the panel which is placed on four steel blocks. The panel will withstand and Uniformly Distributed Load (UDL) minimum 1250 kg/sqm and an impact load of 50kg all complete as per the approved manufacturers specification and as per the direction of Engineer-in-charge. All specification must be printed on the side of the panel to ensure the quality of the product. 300 mm Finished Floor Height (FFH)
63.00 | Providing and laying 18 mm thick flamed finish Granite stone flooring/ Cladding in required design and patterns, in linear as well as curvilinear portions of the building all complete as per the architectural drawings over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry and pointing with white cement slurry admixed with pigment of matching shade including rubbing, curing and polishing etc. all complete as specified and as directed by the Engineer-in- Charge, INCLUDING fixing by means of clamps, anchor fasteners and pins, etc. wherever required as directed by Engineer-In-Charge complete at all levels. 18 mm thick Flamed finish Granite stone slab of any colour and texture as approved with minimum base rate of Approx Rs. 2000/ sqm. | 100.00 | M2 |  | 3688.00 | 368800.00 | 4500.00 | 450000.00 | 4650.00 | 465000.00 | 368800.00 | MANNU LAL AND SONS
64.00 | Chequerred precast cement concrete tiles 22 mm thick in footpath & courtyard, jointed with neat cement slurry mixed with pigment to match the shade of tiles, including rubbing and cleaning etc. complete, on 20 mm thick bed of cement mortar 1:4 (1 cement: 4 coarse sand). Light shade pigment using white cement | 80.00 | M2 |  | 1600.00 | 128000.00 | 1600.00 | 128000.00 | 1775.00 | 142000.00 | 128000.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
65.00 | Providing and fixing of GFRC coarse stone wall cladding tiles of size 180x90 mm in minimum 12 mm thickness. Tiles to be made with white portland cement of Birla white, fine graded silica sand with fine aggregate, reinforced with glass fiber of owens corning or equivalent make and using synthetic inorganic colour pigments of Laxness make as per approved colour. Fixing of tiles to be done using exterior grade tile adhesive and necessary screws/ clamps etc. (COST INCLUDED) and Including grouting with matching pigment and two coats of silica paint FOR ALL HEIGHTS as per direction of engineer in charge. ALL ITEMS MENTIONED HEREIN ARE INCLUDED IN THE COST | 10.00 | M2 |  | 6100.00 | 61000.00 | 7500.00 | 75000.00 | 3650.00 | 36500.00 | 36500.00 | Innovations Workspace Solutions Pvt. Ltd.
66.00 | SECTION-G: ROOFING WORK
67.00 | Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as per IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with 6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the spacing of 1200 mm centre to centre, to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @ 230 mm interval, including fixing of gypsum board to ceiling section and perimeter channel with the help of dry wall screws of size 3.5 x 25 mm at 230 mm c/c, including jointing and finishing to a flush finish of tapered and square edges of the board with recommended jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm on both sides of joint and two coats of primer suitable for board, all as per manufacturer's specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge but excluding the cost of painting with : 12.5 mm thick tapered edge gypsum moisture resistant board | 4000.00 | M2 |  | 1280.00 | 5120000.00 | 1350.00 | 5400000.00 | 1018.00 | 4072000.00 | 4072000.00 | Innovations Workspace Solutions Pvt. Ltd.
68.00 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. GI Metal Ceiling Lay in perforated Tegular edge global white color tiles of size 595x595 mm and 0.5 mm thick with 8 mm drop; made of GI sheet having galvanizing of 100 gms/sqm (both sides inclusive) and 20% perforation area with 1.8 mm dia holes and having NRC (Noise Reduction Coefficient ) of 0.5, electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending and perforation, and backed with a black Glass fiber acoustical fleece. | 1000.00 | M2 |  | 1500.00 | 1500000.00 | 2100.00 | 2100000.00 | 1845.00 | 1845000.00 | 1500000.00 | MANNU LAL AND SONS
69.00 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. GI Metal Ceiling Lay in plain Tegular edge Global white color tiles of size 595x595 mm, and 0.5 mm thick with 8 mm drop; made of G I sheet having galvanizing of 100 gms/sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending. | 1100.00 | M2 |  | 1500.00 | 1650000.00 | 1300.00 | 1430000.00 | 1995.00 | 2194500.00 | 1430000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
70.00 | Wooden ceiling finish with veneer: Providing and fixing IS 710 12 mm thick plywood false ceiling as per drawing & instruction of EIC & sample approved (complete with frame work). finish with 4 mm th veneer gurjan base ply Semi glossy malamine finish polish. Plywood shall be fixed with required fabrication work and ply frame work with all necessary accessories Rate shall include cost of making of all cutouts for light fixtures, gadgets, gizmo, pelmets, grooves, beads and also provide support/template where ever required. The rate shall be in sq.mt for all floors and at all heights including all costs the shop drawing (or a sample mock of 5 Sqm minimum of the frame work and ceiling) shall be approved from EIC. 5mm Groove shall be provided at the junction of the false ceiling & the wall. (considering all levels with require all fabrication work and fitting from RCC slab to false ceiling 100 to 1000 mm) | 200.00 | M2 |  | 5600.00 | 1120000.00 | 8500.00 | 1700000.00 | 4075.00 | 815000.00 | 815000.00 | Innovations Workspace Solutions Pvt. Ltd.
71.00 | ACOUSTICAL SOUNDSCAPE PANEL Providing and Fixing SoundScapes - Acoustical clouds which are 30 mm thick, flat glass fiber panels with Humidity Resistance RH 90% & Recycled Content of minimum 30%, come in various shape options like Square / Convex / Concave / Circle / Hexagon / Trapezoid / Parallelogram (Left & Right) / Rectangle (Small & Large) and in standard Traffic White color with LR 90% or in the color specified by the Architect / Engineer in charge (Ivory / Pale Green / Pastel Blue / Traffic Grey / Pale Brown). or in the color specified by the Architect / Engineer in charge . The size and sound absorption details are as :2.12 metric sabin.Shape- Circle ,Nominal Size- circular- of different diameters as below. The back of each panel to have embedded square frame bracket system of 610 x 610mm in which provisions are already made for integration of installation system for suspension of individual or grouped panels.The panels to be suspended individually using the SoundScapes Deck hanging kit. Each kit to consist of gripper structure anchors with an outer diameter of 16mm and height 23mm, aircraft cables of 1.5mm dia 2.44 LM in length and bottom end cable adjusters of 8.9mm outer diameter. Each panel to be suspended using the aircraft cables which are suspended from the soffit using the gripper structure anchors and its other end passing through the bottom end cable adjuster which are screwed in the 4 corners of the frame bracket system.The height & level of the panels can be adjusted using the bottom end cable adjusters.
72.00 | 1200 mm dia | 10.00 | EA |  | 3800.00 | 38000.00 | 28000.00 | 280000.00 | 1000.00 | 10000.00 | 10000.00 | Innovations Workspace Solutions Pvt. Ltd.
73.00 | 900 mm dia | 5.00 | EA |  | 2900.00 | 14500.00 | 18000.00 | 90000.00 | 500.00 | 2500.00 | 2500.00 | Innovations Workspace Solutions Pvt. Ltd.
74.00 | 600 mm dia | 5.00 | EA |  | 2500.00 | 12500.00 | 90000.00 | 450000.00 | 350.00 | 1750.00 | 1750.00 | Innovations Workspace Solutions Pvt. Ltd.
75.00 | SITC of BAFFLE FALSE CEILING - Aluminium 50 BD Panel of approved colour consisting of panel 50 mm wide x 100mm depth x 1 mm thick panel length up to 6 mtrs coil coated on a continuous paint line double baked and roll formed from enameled corrosion Resistance Aluminum Alloy AA3005 / AA5050 for higher strength and good Roll forming characteristics. Panels shall be mounted in a module of 100 mm on a mullion profile grooved (Slotted Fastening Profile) by means Locking Clips and PopRivet. Slotted Fastening Profile shall be fixed at 150 mm from panel ends and at a distance of maximum 1200 mm center to center across the panel span and Slotted Fastening Profile shall be fixed to a suitable sub-structure by means of Square Brackets (contractor scope). Paint Finish: Panel shall be stove enamelled and finished with Luxacote, a patented special three layered coating system (consisting of first a conversion layer of thickness 800-2000mg/sq mtr, a polyurethane basecoat of 16-20 microns, and a special top coat of polyamide particles of 8-12 microns thick to provide excellent abrasion and damage resistance) in a continuous coil coating process of the approved colour on the exposed side and the reverse side with epoxy. Makes : Hunter Douglas, High Steel, Anutone, Armstrong, Prominance | 150.00 | M2 |  | 6000.00 | 900000.00 | 13500.00 | 2025000.00 | 6750.00 | 1012500.00 | 900000.00 | MANNU LAL AND SONS
76.00 | Frameless cloud ceiling - Frameless cloud ceiling: Providing and fixing cloud ceiling 1200x600x25mm or 1200x1200x30mm, a horizontal element with painted edges and without profiles, with painted epoxy surface in universal white on all sides and can be weekly wet cleaned and daily dusting or vacuum cleaned. the light reflectance of the ceiling should be 85% of which more than 99% is diffuse reflection. The element withstand a permanent ambient RH upto 95% at 30 degree C without saging, warping or delaminating (ISO 4611). The glasswool core of the element is tested and classified as non combustible. It should consist of four spiral anchor and four adjustable wire hangers for hanging from ceiling adjustable wire length should be adjustable upto 2 meters. | 1.00 | NUM |  | 20000.00 | 20000.00 | 28000.00 | 28000.00 | 18500.00 | 18500.00 | 18500.00 | Innovations Workspace Solutions Pvt. Ltd.
77.00 | Providing and fixing zinc alloy coated high tensile steel roofing sheets in 0.45 mm thickness and having minimum yield strength of 550 Mpa in colour as decided by EIC. The sheet shall be fixed with self drilling/ selp tapping screw with EPDM seal complete. The cost shall include the cost of erecting the sheets and fixing the same with approved make screw/ washer etc complete but excluding the cost of truss, crimp ridge and crimp eaves. The area measured in plan shall be measured for payment and no extra payment shall be made for overlaps. Accordingly the bidder is required to quote his rates. Approved make is Tata Bluscope DURASHINE | 10.00 | M2 |  | 900.00 | 9000.00 | 6000.00 | 60000.00 | 5245.00 | 52450.00 | 9000.00 | MANNU LAL AND SONS
78.00 | Providing and fixing Crimp Ridge of Tata Bluscope DURASHINE make including fixing with necessary self drilling screws and EPDM washer complete | 1.00 | M |  | 1000.00 | 1000.00 | 12500.00 | 12500.00 | 3850.00 | 3850.00 | 1000.00 | MANNU LAL AND SONS
79.00 | Providing and fixing Crimp Eaves of Tata Bluscope DURASHINE make on two ends of the sheet including fixing with necessary self drilling screws and EPDM washer complete | 2.00 | M |  | 1000.00 | 2000.00 | 12900.00 | 25800.00 | 3850.00 | 7700.00 | 2000.00 | MANNU LAL AND SONS
80.00 | Providing and fixing Gutter of Tata Bluscope DURASHINE make on two ends of the sheet including fixing with necessary self drilling screws and EPDM washer complete | 2.00 | M |  | 1000.00 | 2000.00 | 13500.00 | 27000.00 | 2375.00 | 4750.00 | 2000.00 | MANNU LAL AND SONS
81.00 | Providing & fixing Anavertical Linear Baffle Box Curtain Closed Ceiling made out of Aluminum Extrusion of 1 mm thickness. The baffle blade shall be in size of 30 x 100 x 3000mm in powder coated finish of approved shade or wooden texture. The baffle blade shall be suspended using Slotted U-profile powder coated to black colour at an on-center spacing of 100/150/200mm. The C-Channel/U profile shall be suspended at every 1200mm on-centre using 6mm threaded rod/4mm rod/12 gauge hanger wire from the structural soffit at every 1200mm intervals using U-profile hanger/C-channel hanger. Multiple lengths of U-profile/C-channel shall be connected using U-profile connector/ C-channel connector. The baffle blades shall be suspended from the C-channel/U-profile carrier bars at the required intervals (100/150/200/250mm) using baffle hangers. Spacing between blades shall be adjusted using the slots in carrier. | 25.00 | M2 |  | 8500.00 | 212500.00 | 11500.00 | 287500.00 | 1500.00 | 37500.00 | 37500.00 | Innovations Workspace Solutions Pvt. Ltd.
82.00 | SECTION-H STEEL WORKS
83.00 | Steel work in single section, fixed with or without connecting plate, riveted, bolted or welded in built up sections, trusses and framed work, in built up sections/ framed work (In stringers, treads, landings etc. of stair cases, including use of chequered plate wherever required, all complete, gratings, frames, guard bar, ladder, railings, brackets, gates, frames, door shutter and similar works, in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position, providing and fixing bolts including nuts and washers complete wherever required and INCLUDING Painting with synthetic enamel paint of approved brand and manufacture to give an even shade - two or more coats on new work and applying a priming coat of approved steel primer all complete. | 2000.00 | KG |  | 140.00 | 280000.00 | 125.00 | 250000.00 | 215.00 | 430000.00 | 250000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
84.00 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 m dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge. 10 x 60 mm | 250.00 | EA |  | 150.00 | 37500.00 | 150.00 | 37500.00 | 125.00 | 31250.00 | 31250.00 | Innovations Workspace Solutions Pvt. Ltd.
85.00 | Providing and fixing stainless steel (Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, INCLUDING fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.). | 2900.00 | KG |  | 750.00 | 2175000.00 | 650.00 | 1885000.00 | 645.00 | 1870500.00 | 1870500.00 | Innovations Workspace Solutions Pvt. Ltd.
86.00 | Providing Toughened glass 12 mm thickness fixed to stainless steel ( Grade 304) railing made of Hollow tubes including glass formwork/ mould of MDF/ PLY as per manufacture's requirement and fixing accessories such as nuts, bolts, fasteners, etc. (excluding Stainless steel railing) | 75.00 | M2 |  | 3500.00 | 262500.00 | 7500.00 | 562500.00 | 4950.00 | 371250.00 | 262500.00 | MANNU LAL AND SONS
87.00 | SECTION-I WOOD AND PVC WORK
88.00 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed, wooden moulded beading Including iron hold fast, bolts, nuts and wooden plugs, dash fasteners of required dia & length, iron screws, plugs and priming coat of wood primer and two or more coats of melamine/ french spirit polish - good quality chemically treated Seasoned hard wood | 3.00 | M3 |  | 130000.00 | 390000.00 | 142949.00 | 428847.00 | 192500.00 | 577500.00 | 390000.00 | MANNU LAL AND SONS
89.00 | Providing and fixing ISI marked flush door shutters 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws conforming to IS : 2202 (Part I) decorative type, core of block board construction with frame of 1st class hard wood and well matched teak 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters INCLDUING melamine polish complete and providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of flush door shutters and providing vision panel (rectangular/ square/ circular) not exceeding 0.1 sqm in all type of flush doors (cost of glass excluded) (over all area of door shutter to be measured) and INCLUDING Providing & fixing glass panes and glazing clips in Flush doors, windows, clerestory windows, all complete with : With clear toughened glass panes of 6 mm thickness and EXCLUDING all required fittings wherever required as directed by Engineer-In-Charge | 175.00 | M2 |  | 8721.00 | 1526175.00 | 3473.00 | 607775.00 | 9945.00 | 1740375.00 | 607775.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
90.00 | Providing and Fixing approved brand and manufacture of SS 304 Hinge Hettich (9268384) 100x75x3mm Round Ball Bearing Hinge, EN 1935 Certified for 200,000 Cycle,105 min Fire rated, 5 years Functional Warranty SS 304 Hinge 100x75x3mm Round Corner (Hole Pattern: C) complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 310.00 | EA |  | 761.00 | 235910.00 | 3500.00 | 1085000.00 | 295.00 | 91450.00 | 91450.00 | Innovations Workspace Solutions Pvt. Ltd.
91.00 | Providing and fixing approved brand and manufacture of Stainless Steel Tower bolt 300 mm long with 10 mm dia along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 160.00 | EA |  | 450.00 | 72000.00 | 1500.00 | 240000.00 | 575.00 | 92000.00 | 72000.00 | MANNU LAL AND SONS
92.00 | Providing and approved brand and manufacture of Stainless Steel Door stopper Hettich (9228709) - Door Mounted Hanging Type SS Satin Finish along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 80.00 | EA |  | 585.00 | 46800.00 | 1300.00 | 104000.00 | 215.00 | 17200.00 | 17200.00 | Innovations Workspace Solutions Pvt. Ltd.
93.00 | Providing and fixing approved brand and manufacture of Stainless Steel Door Buffer wall mounted 22 mm dia,75 mm long (DB (22) along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 80.00 | EA |  | 200.00 | 16000.00 | 1250.00 | 100000.00 | 200.00 | 16000.00 | 16000.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
94.00 | Providing and fixing Sliding bolt (baby latch) with SS lock strip 5'' (BL(B)) along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 5.00 | EA |  | 350.00 | 1750.00 | 1150.00 | 5750.00 | 350.00 | 1750.00 | 1750.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
95.00 | Providing and fixing approved brand and manufacture of Surface Mounted with slide rail K (Symmetric) Mechanism Door Closer Hettich (9227816), Weight of door: 40-80 Kg, Width of door: 850-1100 mm, Tested & Certified 200,000 cycles, Silver Finish, Door closer power adjustment by change of position from hinge line along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 70.00 | EA |  | 2290.00 | 160300.00 | 1650.00 | 115500.00 | 3995.00 | 279650.00 | 115500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
96.00 | Providing and fixing approved brand and manufacture of SS 304 Solid die cast Mortice Lever handle Hettich (9228111) with 8 mm spindle, With Restoring spring along with Steel base PVD coating: 16 micron with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 70.00 | EA |  | 3000.00 | 210000.00 | 3500.00 | 245000.00 | 1150.00 | 80500.00 | 80500.00 | Innovations Workspace Solutions Pvt. Ltd.
97.00 | Providing and fixing approved brand and manufacture of Mortice Sash lock Lock type : PZ - 72 W (W = handle/knob execution), Basket : 55mm, Face plate: Stainless steel, Face plate width: 24 mm / Hub: 8 mm, With closed lock case with 3 - fold fastening, Lock case: zinc - plated, Shiftable latch bolt. Latch bolt can be shifted without opening the lock case, with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-incharge. | 70.00 | EA |  | 1500.00 | 105000.00 | 4500.00 | 315000.00 | 2150.00 | 150500.00 | 105000.00 | MANNU LAL AND SONS
98.00 | Providing and fixing approved brand and manufacture of Euro Profile Cylinder hettich (9228176) with One side key and one side knob 60 mm, for max door thickness - 40 mm - SS Finish along with necessary accessories and screws etc. complete in all respects as per manufacture specifications & as directed by Engineer-in-charge. | 2.00 | EA |  | 1220.00 | 2440.00 | 6500.00 | 13000.00 | 2650.00 | 5300.00 | 2440.00 | MANNU LAL AND SONS
99.00 | SECTION-J MISCELLANEOUS WORK
100.00 | Providing and fixing 12mm thk. Toughened float glass glazing cut including glass formwork/ mould of MDF/ PLY as per manufacture's requirement using a special extruded aluminium structure and fixed in openings of desired shape as per drawing with 3/4" beveling all around, fixed with the help of SS patch fittings, with top and bottom 'C' channels as per manufacture's specifications, fixed firmly to the slab/ MS Structure , including filling of Silicon sealant in the joints or optional vertical transparent polycarbonate joints to ensure that the glass panes remain perfectly flush with each other as directed by Engineer in Charge. Stability and soundproofing are ensured by a series of soft extruded PVC seals, located along the outside perimeters, securing the glass panes. Area of openings to be measured. Rate of above item to include P/F of : 20x20mm "C" channel or as specified by manufacturer, SS patch Fittings. Makes: - KUBIK, KLIO, OR EQUIVALENT | 800.00 | M2 |  | 5000.00 | 4000000.00 | 9502.00 | 7601600.00 | 3115.00 | 2492000.00 | 2492000.00 | Innovations Workspace Solutions Pvt. Ltd.
101.00 | Providing and fixing 12mm thk. Toughened glass door, cut and fixed in openings of desired shape as per drawing with 3/4" beveling all around and acid wash etching, fixed with the help of SS patch fittings as per drawing and as directed by Engineer in Charge / Architect.( Area of openings to be measured). Assume frameless glass. Rate of above item to include P/F of : 1) Pin cylinder lock in Stainless Steel finish (Hettich make ) as directed by Engineer in Charge | 310.00 | M2 |  | 9808.00 | 3040480.00 | 5325.00 | 1650750.00 | 5625.00 | 1743750.00 | 1650750.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
102.00 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315, having brand logo embossed on the body / plate with double spring mechanism and door weight upto 125 kg, for doors, including cost of cutting floors, embedding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge. With stainless steel cover plate minimum 1.25 mm thickness | 100.00 | EA |  | 4933.00 | 493300.00 | 1715.00 | 171500.00 | 10150.00 | 1015000.00 | 171500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
103.00 | Providing and fixing Back to Back Set of Pull Handles Hettich (9228527) Dia. 25mm, CTC Length upto 450 mm approx., SS Finish O/A 400 in satin stainless steel. | 85.00 | EA |  | 1782.00 | 151470.00 | 3500.00 | 297500.00 | 950.00 | 80750.00 | 80750.00 | Innovations Workspace Solutions Pvt. Ltd.
104.00 | Providing and fixing Stainless steel 304 Grade H- type pull handle Hettich(9228554)of size min 32 mm dia and 1200mm long of approved make including SS screws, including making holes of required size in shutter etc. complete as per direction of Engineer-in-Charge. | 30.00 | EA |  | 3402.00 | 102060.00 | 4500.00 | 135000.00 | 4150.00 | 124500.00 | 102060.00 | MANNU LAL AND SONS
105.00 | Partition Work - Providing and fixing in position opaque partition consisting of frame work in extruded aluminium sections 1.6 mm thick, of approx size 50 x50 mm , placed at center to center at not more than 600 mm vertically and 1200 mm horizontally, joined using angle 35x35x 3 mm . Securely fixed to wall and , floor and ceiling complete in all respect . The rates shall be inclusive of cutting , punching of holes for drawings conduits and boxes for electrical works etc. Providing and fixing to aluminium frame work , Particle/ MDF / Ply Boards etc., fixed with fully threaded parallel shank screws at 200 to 300 mm centre to centre , on both sides of framework. Joints staggered on either sides of the partitions to avoid through joints complete as per directions of Engineer-in-Charge. (Ply Board work to be measured and paid separately). | 2100.00 | M2 |  | 1875.00 | 3937500.00 | 1150.00 | 2415000.00 | 1540.00 | 3234000.00 | 2415000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
106.00 | Panelling Work - Providing and fixing in position opaque panelling consisting of frame work in extruded aluminium sections 1.6 mm thick, of approx size 50 x25 mm , placed at center to center at not more than 600 mm vertically and 1200 mm horizontally, joined using angle 35x35x 3 mm . Securely fixed to wall and , floor and ceiling complete in all respect . The rates shall be inclusive of cutting , punching of holes for drawings conduits and boxes for electrical works etc. Providing and fixing to aluminium frame work , Particle/ MDF / Ply Boards etc., fixed with fully threaded parallel shank screws at 200 to 300 mm centre to centre , on both sides of framework. Joints staggered on either sides of the partitions to avoid through joints complete as per directions of Engineer-in-Charge. (Ply Board work to be measured and paid separately). | 200.00 | M2 |  | 1526.00 | 305200.00 | 1265.00 | 253000.00 | 1534.50 | 306900.00 | 253000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
107.00 | Providing and fixing infill of 50mm thick & min. 60 kg / m3 density Mineral Wool Insulation. Mineral wool packed in polyweave packets inside partition frame work fixed to wall with Clip, screw, rawel plug & washers and held in position by criss crossing GI wire etc. complete as per directions of Engineer-in-Charge. | 200.00 | M2 |  | 240.00 | 48000.00 | 1800.00 | 360000.00 | 375.00 | 75000.00 | 48000.00 | MANNU LAL AND SONS
108.00 | Providing and fixing - Panelling with 12.5 mm thick Gypsum double skin fire rated board including taping and jointing complete (Rate Includes cost of two skin) | 100.00 | M2 |  | 1200.00 | 120000.00 | 1750.00 | 175000.00 | 1495.00 | 149500.00 | 120000.00 | MANNU LAL AND SONS
109.00 | VENEER PANELING Providing and fixing of 3.5 mm thick Ply Veneer cladding of Maple or approved shade on existing partitions/ panelling fixed with adhesive, matching grains and including spray applied matte melamine polishing, primer, groove etc. complete. Veneer to be fixed in panels of width as specified and 4mm grooves as per drawing including taping jointing and groove etc complete. Minimum Basic price of Veneer @ Rs.1000/ Sqmt + taxes | 320.00 | M2 |  | 2243.00 | 717760.00 | 1150.00 | 368000.00 | 3375.00 | 1080000.00 | 368000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
110.00 | GLOSSY/ MATT LAMINATE 1 mm thick - Supply and installation of approved shade Glossy/ Matt Laminated sheets of desired colour and shade including taping jointing and groove and glue/ adhesive to applied on laminate and ply etc. complete. | 4100.00 | M2 |  | 762.00 | 3124200.00 | 1000.00 | 4100000.00 | 1125.00 | 4612500.00 | 3124200.00 | MANNU LAL AND SONS
111.00 | Supplying and providing Duco Paint on new work two or more coats including preparing surface and primer etc. complete | 100.00 | M2 |  | 2500.00 | 250000.00 | 1500.00 | 150000.00 | 1950.00 | 195000.00 | 150000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
112.00 | Providing and fixing - 4/6 mm thick charcoal board panel including taping jointing and groove etc complete | 100.00 | M2 |  | 1000.00 | 100000.00 | 850.00 | 85000.00 | 150.00 | 15000.00 | 15000.00 | Innovations Workspace Solutions Pvt. Ltd.
113.00 | Providing and fixing - 6 mm thick commercial ply including taping jointing and groove etc complete | 80.00 | M2 |  | 715.00 | 57200.00 | 950.00 | 76000.00 | 1050.00 | 84000.00 | 57200.00 | MANNU LAL AND SONS
114.00 | Providing and fixing - 12 mm thick both sides Pre-laminated cement bonded wood particle board including taping jointing and groove etc complete | 60.00 | M2 |  | 865.00 | 51900.00 | 1050.00 | 63000.00 | 850.00 | 51000.00 | 51000.00 | Innovations Workspace Solutions Pvt. Ltd.
115.00 | Providing and fixing Single layer of 12mm thick BWP Ply as per details on single side of the existing aluminium partitions framework or elsewhere as required as per drawing details/site requirement including taping jointing and groove etc complete and shall be provided as per the direction of EIC. | 4100.00 | M2 |  | 1053.00 | 4317300.00 | 980.00 | 4018000.00 | 1045.00 | 4284500.00 | 4018000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
116.00 | Providing and fixing Single layer of 12mm thick MDF Ply as per details on single side of the existing aluminium partitions framework or elsewhere as required as per drawing details/site requirement including taping jointing and groove etc complete and shall be provided as per the direction of EIC. | 300.00 | M2 |  | 820.00 | 246000.00 | 1800.00 | 540000.00 | 1025.00 | 307500.00 | 246000.00 | MANNU LAL AND SONS
117.00 | Providing & applying exterior texture paint (Finished thickness 1.2mm to1.5 mm ) SUZUKA STONEY of Ultratech make or equivalent make of OIKOS, and SKK with natural stone crushed powder applied over plaster surface within grooves comprising of following operations :- First coat of Acrylic primer added with wall sealer to be applied over the surface for better adhesion of the texture with surface. Second coat- Texture coat to be applied with chips of stone powder having available natural stone base shade with stainless steel trowel finished with spray gun to be applied with spray gun with 2hp pressure. Final coat of siloxiene FSI Clear base protection coat to be applied which make the product completely water repellent / dust resistant / anti fungal Warranty of 07 years on shades and sustainability is to be provided by the applicator Grooves are to be crafted in plaster as per approved design approved by engineering in charge. All works upto floor seven level including scaffolding etc complete. APPROVED MAKE ULTRATECH, OIKOS, SKK, THIS IS A HIGH VALUE SPECIALISED ITEM TO BE APPLIED AT SITE BY TRAINED APPLICATOR OF THE MANUFACTURERS OF APPROVED MAKE, AND THE BIDDERS ARE THEREFORE REQUESTED TO CONFIRM THE RATES BEFORE QUOTING | 50.00 | M2 |  | 1875.00 | 93750.00 | 1980.00 | 99000.00 | 550.00 | 27500.00 | 27500.00 | Innovations Workspace Solutions Pvt. Ltd.
118.00 | Providing and fixing 10x10x7.50 cm Granite stone block hand cut and chisel dressed on top, for CORBELLED paving in floors, drains etc. laid over 20mm thick base mortar 1:4 (1cement:4 coarse sand) with joints 10mm wide filled with same mortar including ruled pointing etc. complete as per direction of engineer-in charge. | 50.00 | M2 |  | 1800.00 | 90000.00 | 2189.00 | 109450.00 | 650.00 | 32500.00 | 32500.00 | Innovations Workspace Solutions Pvt. Ltd.
119.00 | Supplying and installing roller blinds of approved make, model and shade at all heights and location and required width and comprising of approved shade and quality fabric, 1 mm thick anodized extruded Aluminium alloy roller tube of 38-mm O.D , a bidirectional operating Clutch mechanism designed for adjustment-free, slippage-free, crash proof smooth operation for all heights, high strength fiber glass reinforced polyester idler, powder coated steel Insert type brackets fitted with roller tube, round bottom rail, control unit engrooved with a Ball Pitch of minimum 6.5mm, Stainless Steel Ball Chain, and powder coated atomized steel installation brackets. The clutch mechanism comprises of a SS beaded chain and carbon steel spring wrapped by means of a high strength fiber glass reinforced polyester assembly to transmit motion from driving to driven members. The installation brackets shall facilitate overhead, side or face mounting with clutch assembly on either end of the roller. Idler shall consist of a centre shaft and outside sleeve which provide bearing surface for roller tube and rotate freely on centre shaft for smooth and quiet operation. | 1400.00 | M2 |  | 1500.00 | 2100000.00 | 1450.00 | 2030000.00 | 1095.00 | 1533000.00 | 1533000.00 | Innovations Workspace Solutions Pvt. Ltd.
120.00 | Bottom rail along with the fabric shall be enclosed in a suitably created pocket and shall be of powder coated aluminium tube and closed from sides with end caps. The item includes all fittings, accessories, brackets, screws, anchor fasteners, fabric as per approved sample and shade all complete as per drawings, tender specifications, relevant standards and direction of Engineer in charge. (Height of blind from top bracket to bottom tube and width from bracket to bracket shall be measured for payment)
121.00 | Manual Roller Blinds with following specification:
122.00 | Composition- 30% Polyester (max),70% PVC on Polyester(min), Openness factor- 3-5%(as approved) Weight (gram/ sqm)- min 440 gm/sqm Thickness- min 0.60 mm Fire Classification- Class A( NFPA 101 or Class 1 (UNE EN 13773) or equivalent as per relevant standards and specifications Fastness to light- 6-7/8 or higher Indoor Air Quality- GreenGuard / Eco-Codice Certified. Manufacturer's warrantee- minimum 5 years
123.00 | Providing and fixing Glass Reinforced Concrete (G.R.C) Screen at all levels & heights in approved size, pattern, design, thickness (minimum 35mm) and color. The Screens should be made from White Portland Cement, Quartz, Fine Silica Sand, Alkali Resistant Glass Fiber, Super Plasticizers, Polymers and U.V resistant Synthetic inorganic pigments should be used for pigmentation. The material casting should take place in Synthetic Rubber / FRP Mould. The fixing of Jali should be ‘Dry fixing’ i.e. to be done with MS/SS ‘L’ shaped Clamps, dash fasteners and pins etc complete as per site requirement and direction of Engineer-in-charge. | 10.00 | M2 |  | 8400.00 | 84000.00 | 350.00 | 3500.00 | 750.00 | 7500.00 | 3500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
124.00 | Designing, Fabricating, Manufacturing, Installation and testing of Glass Reinforced Concrete G.R.C. from liners in approved size, pattern, design, thickness and color with dry fixing method, the form liners should be made from approved white Portland cement in grade 18, quartz, fine silica sand, alkali resistant glass fiber manufactured. Polymers manufactured by approved manufacturer or equivalent, super plasticizers manufactured by approved manufacturer or equivalent with UV resistant synthetic inorganic pigments made by approved manufacturer or equivalent. The material casting should be done in synthetic rubber/FRP. Fixing of GRC form liners to be fixed on/between RCC/Block work column or structural steel work with dry fixing method with appropriate steel frame work, using fasteners, and necessary hardware etc. In building façade the form liners shall be securely fixed with stainless steel bolts and anchor fasteners (304 Grade) of required size at specified locations. The fixing shall be done by the specialized approved agency as directed by Engineer-in-charge. | 50.00 | M2 |  | 2700.00 | 135000.00 | 350.00 | 17500.00 | 850.00 | 42500.00 | 17500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
125.00 | Room Signages (Stainless Steel with single color/Multi color engravings) Providing and Fixing Room Signages for Office/ Reception/ Conference room/Cabin/Stationary/ Store room/Server / ups /electrical room/G.Toilet & Ladies Toilet with symbol/Pantry/Fire exist/rest room or for any other area as per the direction of EIC. The SS plate shall be 304 grade 2 mm thick glossy matt finish of approved shape as per drawing. single color/Multi color engraved signage Font and letter sizing shall be got approved by the architect-sample shall be submitted. Rate shall include all hardware and necessary arrangement for fixing. | 14.00 | M2 |  | 9600.00 | 134400.00 | 9500.00 | 133000.00 | 16950.00 | 237300.00 | 133000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
126.00 | MDF Jali in S.S : Providing and making and fixing 18 mm thick exterior grade MDF Jali fixing 35x 50 mm Stainless steel frame as per suggested pattern CNC cutting work complete. All wooden surfaces finish with semi gloss PU finish The work shall be done as per the specifications, sample approved and as directed by the Architect and Engineer-in-charge. The rate shall be for complete item inclusive of all material, labour, wastages, necessary tools & tackles, adhesives, consumable hardware & required SS 304 grade hardware/ accessories of approved make. (At all floor) | 25.00 | M2 |  | 7200.00 | 180000.00 | 500.00 | 12500.00 | 8550.00 | 213750.00 | 12500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
127.00 | Providing and laying modular carpet of approved make and shade and made with 100% nylon 6/6.6 tufted textured tip sheared/ cut & loop piles, tiles of minimum 500mm x 500mm in size, stain resistant, anti microbial, and having colour fastness to water, fastness to light, rubbing fastness and castor chair suitability as per relevant standard for heavy commercial usage, with PVC free backing, nominal total thickness of minimum 6.50 mm, pile height minimum 3.4 mm, minimum Total Pile weight – 800g/sqm). Material shall be CRI GREEN LABEL PLUS certified, and shall have recycled content complying to GRIHA requirement, including fixing with GRIHA compliant adhesive of approved make, all complete as per drawings, manufacturer's specifications and direction of Engineer in Charge. | 300.00 | M2 |  | 2000.00 | 600000.00 | 150.00 | 45000.00 | 2145.00 | 643500.00 | 45000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
128.00 | FABRIC PANELING Providing& fixing in position wall panelling at all heights of thickness 25 mm with Fiber Glass Acoustical Wall Panels of size 600X600 /600x1200 mm creda, resin bonded square edges having NRC of 0.9 minimum. The panels should be manufactured from high density bio-soluble resin bonded glass wool absorber having density of 96 Kgs/m3 and wrapped on the front side with an acoustically transparent fabric having option of colours and fabric options like jute etc. as per approved by architect/engineer-in-charge, plain tissue backer and fabric wrapped hardened edges. Panels should have humidity resistance up to 90 %, thermal conductivity ≤ 0.03 (m² k / w) thermal resistance ≥ 0.9 (m² k / w) & moisture rate ≤ 1% (JC/T670 – 2005). The panel should be fully recycled and fire retardant as per Class A. The installation comprises surface impalers having projecting elements called spikes shall be fixed on the plain surface at 1200 mm center to center horizontally and 600 mm center to center vertically or as per approved by engineer-in-charge, using self-tapping screws. Silica based construction adhesive to be dabbed on to the projecting elements (spikes) of the impalers. Wall Panels shall be pierced through the spikes of the impalers ensuring line & level of panel are maintained. The panels should be mounted on the impalers horizontally or vertically as per the approved design or as per the directions of the engineer-in-charge. | 25.00 | M2 |  | 3400.00 | 85000.00 | 3117.00 | 77925.00 | 5450.00 | 136250.00 | 77925.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
129.00 | LAQUER GLASS PARTITION/ PANELLING Providing & Fixing of lacquer glass 4 mm thick as per approval in any color fixed on existing ply/ any other similar base with all other accessories as per architectural drawing. The Lacquered glass shall be highly durable, humid resistance, polyurethane lacquer glass. The glass to be manufactured by industrial curtain coating process. It should meet quality standards as per BS EN 1036 1999 & conform to persoz hardness test of at least 220 oscillations. The substrate of the glass should confirm to Standard BS EN 572 1995 parts 1 & 2. Lacquered glass to be manufactured to tight specifications, relating to consistency of color, opacity and homogeneity throughout production campaigns and also to the ageing properties, mechanical resistance, and resistance to humidity and to chemical agents of the lacquer. The color of the lacquer should remain stable when exposed to normal levels of ultra-violet light in interior applications. (Ply Board/ any other similar base work to be measured and paid separately). | 150.00 | M2 |  | 5500.00 | 825000.00 | 450.00 | 67500.00 | 3975.00 | 596250.00 | 67500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
130.00 | WALLPAPER Providing and fixing of approved shade of Wallpaper with minimum base rate of Approx Rs. 100/ sqft. Wallpaper to be sticked using Adhesives , including all necessary hardware required for it etc., complete as per the detail drawing. | 300.00 | M2 |  | 1700.00 | 510000.00 | 850.00 | 255000.00 | 1445.00 | 433500.00 | 255000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
131.00 | Aluminium Corrugated Louvers - Providing and fixing Horizontal / Vertical Aluminium Corrugated Louvers as per approved shade, fabricated out of heavy duty aluminium extruded profiles ( Powder coated / anodised ) fixed with Aluminium tube outer frame. All aluminium members & profiles shall be of AC 25 grade as per specification. The Aluminium members shall be protected with Masking Tapes all around the profiles for safety against external scratches at site (Masking Tapes shall be removed only at the time of handing over as per the instructions of Developer). The fabrication shall be done with all the joints mitered; the Outer Frames and Mullions jointed with appropriate Stainless Steel Screws, Heavy Duty Aluminium Angle, Cleat, box sleeve etc. EPDM gaskets to be used for preventing bimetallic corrosion wherever required. The fixing shall be done on to Aluminium frames or existing openings at anchorage locations, in windows , walls , Glazing jambs, cills and heads etc by drilling holes with an electric drill, inserting fasteners, stainless steel counter sunk screws etc. | 50.00 | M2 |  | 9500.00 | 475000.00 | 1500.00 | 75000.00 | 375.00 | 18750.00 | 18750.00 | Innovations Workspace Solutions Pvt. Ltd.
132.00 | BUILT IN /JOINERY & MISCELLANEOUS General Note: - The dimensions of the furniture as given in the respective items as below are indicative and there shall be no deviation of cost on account of this. However, the dimensions mentioned below may vary in between ± 10% during execution as directed by Engineer-In-Charge.
133.00 | Providing and fixing in desired position STORAGE 450mm deep. The front shutter, side of cupboard top, bottom and back shall be made of 19mm thick factory pressed BWP grade marine ply as per IS 710, all exposed edges to be finished with teak wood lipping. The front shutter and all other exposed surface of 19mm thick factory pressed BWP grade marine ply board shall be cladded with 1mm thick laminate of required shade and texture and all internal surfaces shall be finished with 1 mm thick frosty white backing laminate as/specified. The item shall include P/F all fittings/ stainless steel hardware like handles/ knobs tower bolts, ball magnetic catchers, lock, SS soft closing hinges etc. including making of trough /pelmet for lighting. The rear side of the cupboard to be treated with the anti-termite oil as approved by the EIC/ Architect. Complete as drawings ,for the purpose of payment, the front plan area of the cupboard excluding the trough/ pelmet for lighting shall be measured. COST OF ALL ITEMS MENTIONED HEREIN ARE INCLUDED. | 80.00 | M2 |  | 12500.00 | 1000000.00 | 650.00 | 52000.00 | 11950.00 | 956000.00 | 52000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
134.00 | Providing and fixing film etching with plotter cutting and application of 3MM/ LUMAR/ GARWARE make as per approved design on glass surfaces all complete as per instructions and patterns and design of the Architect/ Engineer-In-Charge. | 300.00 | M2 |  | 1250.00 | 375000.00 | 95.00 | 28500.00 | 1425.00 | 427500.00 | 28500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
135.00 | Providing and fixing coloured glass film etching with plotter cutting and application of 3MM/ LUMAR/ GARWARE make as per approved design on glass surfaces all complete as per instructions and patterns and design of the architect. | 250.00 | M2 |  | 2098.00 | 524500.00 | 150.00 | 37500.00 | 1125.00 | 281250.00 | 37500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
136.00 | CORE CUTTING Drilling with core cutting machine in Post RCC beams, slabs, floors etc. if not mentioned in the drawing but required by Project Manager for laying pipes and rendering the same in RCC 1:2:4, finishing the same to the satisfaction of the Project Manager, including nominal reinforcement wherever required, complete. The quoted rate shall also include for providing EPOXY based water proofing compound for sealing the joints around the pipes. (Maximum thickness of RCC members shall be 300mm for slab & wall , 600 mm for beam).
137.00 | RCC Slabs
138.00 | 75 mm dia | 20.00 | EA |  | 670.00 | 13400.00 | 1500.00 | 30000.00 | 650.00 | 13000.00 | 13000.00 | Innovations Workspace Solutions Pvt. Ltd.
139.00 | 100mm dia. | 15.00 | EA |  | 800.00 | 12000.00 | 2000.00 | 30000.00 | 800.00 | 12000.00 | 12000.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
140.00 | 150mm dia | 12.00 | EA |  | 1400.00 | 16800.00 | 25000.00 | 300000.00 | 950.00 | 11400.00 | 11400.00 | Innovations Workspace Solutions Pvt. Ltd.
141.00 | 200mm dia | 5.00 | EA |  | 2000.00 | 10000.00 | 3000.00 | 15000.00 | 1100.00 | 5500.00 | 5500.00 | Innovations Workspace Solutions Pvt. Ltd.
142.00 | RCC Beams
143.00 | 65mm dia. | 25.00 | EA |  | 500.00 | 12500.00 | 1500.00 | 37500.00 | 800.00 | 20000.00 | 12500.00 | MANNU LAL AND SONS
144.00 | 160mm dia | 10.00 | EA |  | 1600.00 | 16000.00 | 2500.00 | 25000.00 | 950.00 | 9500.00 | 9500.00 | Innovations Workspace Solutions Pvt. Ltd.
145.00 | 180mm dia | 5.00 | EA |  | 1800.00 | 9000.00 | 3000.00 | 15000.00 | 1100.00 | 5500.00 | 5500.00 | Innovations Workspace Solutions Pvt. Ltd.
146.00 | RCC Walls
147.00 | 65mm dia. | 5.00 | EA |  | 600.00 | 3000.00 | 1500.00 | 7500.00 | 725.00 | 3625.00 | 3000.00 | MANNU LAL AND SONS
148.00 | 160mm dia | 10.00 | EA |  | 1600.00 | 16000.00 | 2500.00 | 25000.00 | 875.00 | 8750.00 | 8750.00 | Innovations Workspace Solutions Pvt. Ltd.
149.00 | 180mm dia | 8.00 | EA |  | 1900.00 | 15200.00 | 3000.00 | 24000.00 | 1025.00 | 8200.00 | 8200.00 | Innovations Workspace Solutions Pvt. Ltd.
150.00 | Tensile Fabric Roof: Providing, Designing , fabricating, assembling and erection of Tensile Fabric Roof along with Insulation. Top Skin Membrane: Type III Opaque fabric having minimum weight of 1050 g/sqm. Flame retardant as per particular specifications .PVDF lacquer on both sides. Any Color of the fabric. warranty of minimum 10 years or as per manufacturer’s specifications whichever is higher on the fabric. Second Skin (Middle Insulation Skin): 50mm + 50mm Fiberglass insulation of 0.036 w/mk of thermal conductivity as per ASTM C 518 or IS3346. Product should have density of minimum 24 Kg/m3 density and two layers of 50mm to be installed to get desired thermal and acoustics performance. Incombustibility rating of BS476 – part 4 insulation of 24kg/cum density. Third Skin: PVDF lacquered on Top side having min. weight of 650 gms/ sqm, with flame retardant as per manufacturer’s specification. (any colour), Warranty of minimum 10 years or as per manufacturer’s specifications whichever is higher on the fabric, over steel frames with all fittings and fixtures such as Galvanised MS Membrane/ End Plate, Shackles, Rigging Screws, Turnbuckles, swedge, fork, keder rods & galvanized MS strands/ cables with stainless steel end terminals complete as per Drawing/ Detail & as per technical specifications and as per the directions of Engineer-in-charge. All the required civil works such as excavation, RCC/Brick foundation whatever is required shall be in the scope of the contractor. All the MS structure work such as base plate , Bolt, Pole , truss, etc shall be in the scope of the contractor. The shop drawing including Design Calculation shall be submitted and Approved from the architect before execution. Accessories wherever required complete including lifts upto all heights, tools and plants, and necessary scaffolding and all civil works etc. required for all operations in all respect as per particular specifications & direction of Engineer-In-Charge. | 260.00 | M2 |  | 9550.00 | 2483000.00 | 550.00 | 143000.00 | 4750.00 | 1235000.00 | 143000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
151.00 | Corian Surface:- Providing & fixing 'Corian' finish using Acrylic solid surface wherever required of 6 mm thickness on top of tables, facia, storage units, door jams, columns, cladding, skirting etc. at all heights wherever directed by Engineer-In-Charge. The rate to include all materials, labour, transportation, wastages etc. complete. | 300.00 | M2 |  | 8881.00 | 2664300.00 | 1350.00 | 405000.00 | 7450.00 | 2235000.00 | 405000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
152.00 | Automatic Sliding Doors Automatic sliding door operator - supply of automatic sliding door Set 1 operator of DORMA/ OZONE/ HAFELE (ES 200 easy) as per approved dwg. Compliant with European standards and produced according to the guidelines for power-operated windows, doors and gates, BGR 232, the UVV and the VDE regulations. TÜV design tested, tested according to the low voltage guidelines, fulfils DIN 18650 standards for Pedestrian Safety, TUV Design Tested for Durability of 1 Million Cycles. The track profile should be separate from the main profile for enabling reduction in vibration insulation. Operator length = 6250 mm, clear passage opening width = 3000 mm, clear passage height = 2500 mm, includes micro processor controlled drive unit, with self learning mechanism, program selector with knob, motion detector (eagle 6 radars, 02 nos), mechanical components, toothed belt, cover profile, floor guide for frameless glass (02 nos), glass clamping rail (02 nos), safety device-light barrier (01 pair). Body finish : standard silver anodised operator profile, electromechanical lock with 12 mm plain toughened frameless glass for complete elevation - 2 moving panels, Including motor control unit, return pulley, end stopper, belt, etc. all as required. The above work complete in all respect as per approved drawings and to the satisfaction of engineer-in-charge / architect consultant. | 1.00 | EA |  | 292969.00 | 292969.00 | 278000.00 | 278000.00 | 274500.00 | 274500.00 | 274500.00 | Innovations Workspace Solutions Pvt. Ltd.
153.00 | Providing & Fixing Of ​Rhythmscape/Hunterdouglas/Techno Ceiling/Armstrong/ Continuum Acoustic Hastag Ceiling of depth 120mm made of 9mm thick of acoustic Pet Flake with NRC of 0.5 as approved to be installed using special aircraft suspension system with custom caps capable of locking at any distance as per the manufacture specification, Including Scaffolding, etc. all complete All material should be of approved make & complete as per the drawing, specification and approval of architect. | 125.00 | M2 |  | 6400.00 | 800000.00 | 850.00 | 106250.00 | 250.00 | 31250.00 | 31250.00 | Innovations Workspace Solutions Pvt. Ltd.
154.00 | Providing & Fixing Of ​Rhythmscape/Hunterdouglas/Techno Ceiling/Armstrong/ Continuum Fabric Wood Panel 1800mm x 600mm as per the drawing made of 12mm real walnut wood species with Custom wooden stain finish with an Organic base and a trimer of cyanamide with 1‐3‐5 Triazine with custom machine coat finish as approved to be installed using z profile system as per the manufacturer specification. All material should be of approved make & complete as per the drawing, specification, and approval of the architect. | 4.00 | NUM |  | 105000.00 | 420000.00 | 8500.00 | 34000.00 | 750.00 | 3000.00 | 3000.00 | Innovations Workspace Solutions Pvt. Ltd.
155.00 | Providing & Fixing Of ​Rhythmscape/Hunterdouglas/Techno Ceiling/Armstrong/ Continuum Ripple Light Ceiling made of 25mm thick & 150mm depth coherent air ply bonded with custom polymer wooden finish with an Organic base and a trimer of cyanamide with 1‐3‐5 Triazine with the edge perimeter of 1mm polymethyl from evonika to be integrated with flexible 3000k Edison Led in White/Warm White as approved to be installed using air craft suspension system with brass jammers capable of locking at any distance and angle as per the manufacture specification. All material should be of approved make & complete as per the drawing, specification and approval of architect. | 120.00 | M |  | 2500.00 | 300000.00 | 2500.00 | 300000.00 | 350.00 | 42000.00 | 42000.00 | Innovations Workspace Solutions Pvt. Ltd.
156.00 | Providing & Fixing Of ​Rhythmscape/Hunterdouglas/Techno Ceiling/Armstrong/ Continuum Acoustic Trapezium Panels 300mm x 450mm in custom size as per the drawing made of 35mm thick high performance wood fibre with custom stretchable scuba with owen cornings fibre class 24kg/m3 Nrc 0.9 in petal form with special Organic base and a trimer of cyanamide with 1‐3‐5 Triazine with custom shade as approved to be installed using Z profile system with special hook as per the manufacture specification. All material should be of approved make & complete as per the drawing, specification and approval of architect, Including Scaffolding etc. all complete | 90.00 | NUM |  | 2000.00 | 180000.00 | 3500.00 | 315000.00 | 250.00 | 22500.00 | 22500.00 | Innovations Workspace Solutions Pvt. Ltd.
157.00 | Providing & Fixing Of ​Rhythmscape/Hunterdouglas/Techno Ceiling/Armstrong/ Continuum Acoustic Petal Ceiling in modules of 212mm x 300mm with 100mm depth made of high performance Acoustic 12mm Pet Flake as approved to be installed using special clip system as per the manufacture specification. Including Scaffolding etc. all complete. All material should be of approved make & complete as per the drawing, specification and approval of architect. | 50.00 | M2 |  | 6500.00 | 325000.00 | 1250.00 | 62500.00 | 350.00 | 17500.00 | 17500.00 | Innovations Workspace Solutions Pvt. Ltd.
158.00 | Providing and fixing certified restroom cubicle system of approved make comprising of green guard certified solid compact laminated water proof board, minimum 18 mm thick made as per IS: 2046 (phenolic core board) and as per BS-476/97 for fire retardant for toilet showers, water closet etc . The board shall be manufactured under high pressure and temperature by impregnating kraft papers and outer decorative papers with thermosetting phenolic/ melamine resins (low VOC). The cubicle system shall be resistant towards water, chemical, scratch, impact and heat and shall be anti bacterial, colour fast and shall have accessories like door knob, Gravity/ auto return hinges, privacy thumb turn with occupancy indicator, coat Hook, etc all in SS 304. The hardware and fixings includes anchoring of all fixed front panel to floor with SS 316 L brackets/ base plates with a clearance height upto 110 mm, and covered with SS 316 Shoe box plates, wall and corner joineries (brackets and channels) shall be SS 304 grade, SS 304 screws, rubber noise reduction tape . The cubicle unit shall be installed in approved finish, shades and colours as per specifications and directions of Engineer-In-Charge, including minimum 5 (five) years warranty against any moisture related damages to all intermediate panels, doors, hardwares etc. Standard dimension of the cubicle system shall be of approx. 2100 mm Height(overall) x 1500mm Depth and 1000 mm Width which includes 750mm door size width. L shaped Cubicle System consisting of front face panel including door, intermediate panel and all necessary accessories, fittings and hardware etc. | 21.00 | EA |  | 56000.00 | 1176000.00 | 9500.00 | 199500.00 | 35500.00 | 745500.00 | 199500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
159.00 | Approval & running permission for required capacity of DG Set Following are the scope of work:- 1.Preparation of drawing & document. 2.Submission of drawing & document to the concerned authority / office with a copy of all correspondence to EIC. 3.Payment of drawing approval fees. (Shall be reimbursed on production of original challan/bill) 4.Submission of work completion report as per approved drawing. 5.Arranging the inspection of the installation. The traveling, lodging, boarding and other expenses of statutory authorities for inspections shall be born by the contractor. 6.Follow up at various level. 8.Payment of inspection fees. (Shall be reimbursed on production of original challan/ bill) 9. Any other related job to obtain approval and running permission. Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 100000.00 | 100000.00 | 350000.00 | 350000.00 | 100000.00 | 100000.00 | 100000.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
160.00 | Making `T' connection from the Corporation water supply main line with all necessary works and specials including road cutting and making good the road after the connection etc., complete. The quoted rate shall include for the necessary road cutting charges to be paid to corporation/ statutory body and liason work with the authorities for obtaining orders (The necessary official deposits, etc. shall be paid reimbursed by GAIL on submission of demand note and challan/ bill in proof of submission of fees). Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 25000.00 | 25000.00 | 350000.00 | 350000.00 | 45000.00 | 45000.00 | 25000.00 | MANNU LAL AND SONS
161.00 | Making `T' connection from the Corporation sewer line with all necessary works and specials including road cutting and making good the road after the connection etc., complete. The quoted rate shall include for the necessary road cutting charges to be paid to corporation/ statutory body and liason work with the authorities for obtaining orders (The necessary official deposits, etc. shall be paid reimbursed by GAIL on submission of demand note and challan/ bill in proof of submission of fees). Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 25000.00 | 25000.00 | 350000.00 | 350000.00 | 45000.00 | 45000.00 | 25000.00 | MANNU LAL AND SONS
162.00 | Getting approval and completion certificate from LOCAL municipal corporation/development authority including liasoning, submission of as built drawings, inspection and clearance etc complete. Statutory fees to be paid if any shall be reimbursed by GAIL on submission of demand note and challan/ bill in proof of submission of fees. The scope of contractor shall be to get the completion certificate from corporation. Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 150000.00 | 150000.00 | 1000000.00 | 1000000.00 | 150000.00 | 150000.00 | 150000.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
163.00 | Approval for load sanction and contract demand of required load capacity with State Electricity Borad as per following scope of work:- 1.Prepration of all drawings and documents required for obtaining approval/sanction. 2.Submission of drawings and documents to the appropriate authority/office with a copy to EIC. 3.Complete liasoning with state electricity board. 4.Payment of all statutory fees. The statutory fees, security deposits and contract demand charges shall be reimbursed by GAIL on production of original Challan. 5.Arranging inspections by statutory authorities. The travelling, lodging, boarding and other expenses of statutory authorities shall be born by the contractor. 6.Doing regular follow-up. 7.Any other related job to obtaining the load approval / contract demand. 8.Final charging of 11 KV Sub - Station. Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 120000.00 | 120000.00 | 500000.00 | 500000.00 | 300000.00 | 300000.00 | 120000.00 | MANNU LAL AND SONS
164.00 | FIRE APPROVAL - Following are the scope of work:- 1.Preparation of drawing & document. 2.Submission of drawing & document to the concerned authority / office with a copy of all correspondence to EIC. 3.Payment of drawing approval fees. (Shall be reimbursed on production of original challan) 4.Submission of work completion report as per approved drawing. 5.Arranging the inspection of the installation. The traveling, lodging, boarding and other expenses of statutory authorities for inspections shall be born by the contractor. 6.Follow up at various level. 8. Completion of all fire related works such as fire-fighting works, PA/ Fire Alarm etc. all as per norms of the Building Approval Authority/ any other regulator as required and instructed by Engineer- In-Charge 10. Any other related job to obtain approval and running permission. Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 75000.00 | 75000.00 | 500000.00 | 500000.00 | 200000.00 | 200000.00 | 75000.00 | MANNU LAL AND SONS
165.00 | Supply and Installation of 6mm thick Exterior grade F- Quality panels of standard size with both side décor. Exterior panels are Duromer high-pressure laminates (HPL) as per EN 438-6 type EDF manufactured with norm conformity of EN 438-7 using patented NT Technology (NT is Non fading high performance acrylic polyurethane surface Technology). Panels will be double hardened including acrylic polyurethane resin and thermally cured under high pressure. These Panels will have CE-Mark necessary for their use in building applications. Installation of panels will be done by MBE Rivets (with Fixed and Sliding Points) with recommended Aluminium T section of 75x37x2.8 mm thick and L section 38x38x2.8mm thick held by Aluminium Wall Bracket with Wind load and Dead load slot as designed, anchored by standard anchor fasteners along with Thermal Separator. Installation of Panels will be done using Rear Ventilated Principles only, which is ensured by providing ventilation gap minimum 200 cm2/ per Meter (for free flow of air behind the façade) for the façade and using the framework with no horizontal section (for all levels and all height upto 35 m including scaffolding etc. complete) | 10.00 | M2 |  | 8000.00 | 80000.00 | 3500.00 | 35000.00 | 5850.00 | 58500.00 | 35000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
166.00 | Providing and supplying ‘Optra Acoustical Wall Paneling with square edges made of fibre glass substrate 25mm thick and wrapped on the front side with an acoustically transparent and classified for Fire reaction Class A as per ASTM E-84, fabric with an option of colors – Husk, Copper, Sangria, Sesame, Coffee, Charcoal, Titanium, Flame, Peanut & Shell as per the choice of the Architect/ Engineer-In-Charge of size 600X600 mm providing a minimum sound absorption level of 0.85 NRC to be affixed to wall using Wall panel impalers and construction adhesives as per the instructions laid down by the manufacturer. | 20.00 | M2 |  | 6000.00 | 120000.00 | 3500.00 | 70000.00 | 5850.00 | 117000.00 | 70000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
167.00 | Providing and fixing Trap doors in ceiling made of 19mm thick factory pressed BWP grade marine ply as per IS 710 & finished in 1 mm thick laminate (Laminate of approved shade and sample) from both side with concealed solid wooden frame as per detail drawing with framework in 100mm x 50mm teak wood section @ hinged supports on both sides. Shutter panels (2 no's) shall consisting of plywood strip of size 40mm x 19mm in section around periphery fixed for holding 19 mm thick factory pressed BWP grade marine ply as per IS 710 skinning on both side with 12mm thk TW lipping on exposed edges to form shutter panel. Top of the panel to be treated with anti-termite treatment and finished with 1 coat of approved colour polish. Door shutters should be complete with necessary hardware such as brass hinges, locking system, hanging SS chain etc. All exposed surface should be finished with TW lipping & matching colour polish. All complete as per detailed drawings & instruction of Architect. Quoted Rates are for all heights , scaffolding, depths, levels, leads and lifts and for all design and pattern shown in drawings | 50.00 | M2 |  | 2500.00 | 125000.00 | 4500.00 | 225000.00 | 5450.00 | 272500.00 | 125000.00 | MANNU LAL AND SONS
168.00 | BOREWELL PERMISSION - Getting approval for Borewell permission for Building Construction works etc. all from LOCAL municipal corporation/ development authority including liasoning, submission of drawings, inspection and clearance etc complete. Statutory fees to be paid if any shall be reimbursed by GAIL on submission of demand note and challan/ bill in proof of submission of fees. The scope of contractor shall be to get the permission from corporation. Commissioning of Borewell complete as per norms of the Building Approval Authority/ any other regulator as required and instructed by Engineer- In-Charge. Any other related job to obtain approval and running permission. Lump sum rate is to be quoted for one complete activity unit/job (EA means 1 Job here) | 1.00 | EA |  | 100000.00 | 100000.00 | 250000.00 | 250000.00 | 15000.00 | 15000.00 | 15000.00 | Innovations Workspace Solutions Pvt. Ltd.
169.00 | Providing and laying factory made coloured chamfered edge Cement Concrete paver blocks of required strength, thickness & size/shape, made by table vibratory method using PU mould, laid in required colour & pattern over 50mm thick compacted bed of fine sand, compacting and proper embedding/laying of inter locking paver blocks into the sand bedding layer through vibratory compaction by using plate vibrator, filling the joints with jamuna sand and cutting of paver blocks as per required size and pattern, finishing and sweeping extra sand in footpath, parks, lawns, drive ways or light traffic parking etc. complete as per manufacturer’s specifications & direction of Engineer-in-Charge. 60mm thick cement concrete paver block of M-35 grade with approved colour, design & pattern. | 1500.00 | M2 |  | 850.00 | 1275000.00 | 850.00 | 1275000.00 | 725.00 | 1087500.00 | 1087500.00 | Innovations Workspace Solutions Pvt. Ltd.
170.00 | Multi – B Ceiling System - Supply of LUXALON® Aluminium, un-perforated, Multi B Ceiling System with V closed groove: Providing & Fixing of Luxalon 80B / 130B / 180 Bun-perforated Aluminium panel ceiling 0.4mm thick with square edges, panel length upto 6mtrs, Coil Coated on a Continuous Paint Line, Double baked and roll formed from enamelled corrosion resistance Aluminium Alloy AA5050 (Al.Mg) for higher strength and good roll forming characteristics. The ceiling panel shall be manufactured on high speed, high precision roll forming machinewith ARKUSIX Hi configuration roller levelling process to ensure the flatness and to avoid the failure of metal at corners which may occur normally on press brake machine. Panel shall be clipped to baked enamelled Aluminium panel carrier of 62mm wide x 29mm deep made of 0.95mm thick in standard length of 5mtrs made of double Baked enamelled Aluminium alloy AA5050 (Al.Mg.) black with cutouts to hold the panels in a module of 50mm (width of gap 20mm open) The Carrier shall be suspended by means of G.I. suspension rod 4mm diameter and a Galvanised suspension spring clip at a distance of 1.7mtrs c/c. Paint finish: Aluminium panels shall be chromatised for maximum bond between metal and paint enamelled twice under high temperature, one side with full primer and finish coat the other side (innerside) with a primer coating and Skin Coat on a Continuous Paint Line. The ceiling system should meet the required standards for GreenPro certification and should qualify as green product as per CII green products and services council. The manufacturer should be ISO 9001:2015 Quality Management System Certification compliant with in house testing facility and should have their own manufacturing plant in India. Mode of Measurements: Measurements shall be wall to wall without any deductions for lights, diffusers, columns etc. All ceiling shall be Green pro Certified: For LEED certification by Indian Green Building council (IGBC). Ceiling manufacturer should have local manufacturing unit in India. Manufacturer should have Roll-forming machine to produce Baffle panels & in-house testing lab in India & having more than 20 years of existence in India. Approved Makes - Hunter Douglas, Gorden, SAS, Armstrong | 20.00 | M2 |  | 9850.00 | 197000.00 | 1150.00 | 23000.00 | 4250.00 | 85000.00 | 23000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
171.00 | "Luxalon® Aluminium Plain U-Baffle Roll Formed coil coated Ceiling: Supply of U Baffle made up of Aluminium panel multi level / size baffle panel ceiling of approved colour consisting of panel size 55 mm wide and 110 mm deep and 55 mm wide and 145 mm deep using 0.7mm thick, minimum length of panel is 5mt, Coil Coated on a Continuous Paint Line, Double baked and roll formed from enamelled corrosion resistance Aluminium alloy for higher strength and good roll forming characteristics. The ceiling panels coil undergoes through levelling process on advanced CAD/CAM equipment to achieve levelling through ARKU SIX Hi configuration roller levelling process to ensure the flatness of the coil in the manufacturing process and relives stresses of coil. Baffle Panels should be manufactured from Roll forming machine only in India to get the high-quality Baffle panels with accurate dimensions. The baffle coils to go through 4 stages of pre-treatment, three times oven baked through conversion coating, priming and finish coat ensuring superior adhesion, high corrosion resistance and good colour stability. The coils to be painted on both sides after degreasing. Inside surface to have a primer of 5microns and a coat of natural colour of 5microns, exposed surface to have a primer of 5microns, binder of 5microns and topcoat of approved colour of 15 microns. Panels shall be clipped to a galvanized steel carrier of 0.5 mm thick, Black Colour coated, one leg of the carriers with cut outs to hold the panels in a module of 150 mm. | 15.00 | M2 |  | 8950.00 | 134250.00 | 2580.00 | 38700.00 | 4450.00 | 66750.00 | 38700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
172.00 | Panel carrier shall be suspended by means of threaded rod at a distance of 1.8 mtr. c/c. The Metal ceiling should be Tested for Seismic Zone V compliance as per IS 1893 part 1-2016. Paint Finish: The baffle coils to go through 4 stages of pre-treatment, three times oven baked through conversion coating, priming and finish coat ensuring superior adhesion, high corrosion resistance and good colour stability. The coils to be painted on both sides after degreasing. Inside surface to have a primer of 5microns and a coat of natural colour of 5microns, exposed surface to have a primer of 5microns, binder of 5microns and topcoat of approved colour of 15 microns. All ceiling shall be Green pro Certified: For LEED certification by Indian Green Building council (IGBC). Ceiling manufacturer should have local manufacturing unit in India. Manufacturer should have Roll-forming machine to produce Baffle panels & in-house testing lab in India & having more than 20 years of existence in India. Approved Makes - Hunter Douglas, Gorden, SAS, Armstrong
173.00 | Triangular Cell Ceiling System Supply & Installation of Luxalon® Aluminium AA3105 Cell Ceiling 50E manufactured by HDI of approved colour consisting of Main Runner, Cross Runner, Upper Sections, Lower Sections all of U-Shaped Profiles 10mm wide x 50mm deep x 0.5mm thick with inwardly returned edges of 2.5mm. Coil coated on a continuous Paint Line, Double baked and roll formed from enamelled corrosion resistance Aluminium alloy for higher strength and good roll forming characteristics. The ceiling panels coil undergoes through levelling process on advanced CAD/CAM equipment to achieve levelling through ARKU SIX Hi configuration roller levelling process to ensure the flatness of the coil in the manufacturing process and relives stresses of coil. Cell ceiling panels should be manufactured from Roll forming machine to get the high-quality panels with accurate dimensions. Aluminium Alloy (Al.Mg) AA3105 for higher strength and good Roll Forming characteristics. The Main Runner shall be fixed at a distance of 1.2mtrs c/c and shall be suspended by means of G.I. Suspension Rod 4mm diameter and a Galvanized Suspension Spring Clip at a distance of 1.2mtr c/c. The Cross-Runner shall be fixed to the Main Runner at a distance 0.6mtrs c/c., with a self-locking device. The Upper Section and Lower section shall be fixed to the Main Runner and Cross Runner in a form of a Cell Structure of module 100 X 100 mm x 100mm in triangular cell shape with a self-locking device. Paint Finish: The baffle coils to go through 4 stages of pre-treatment, three times oven baked through conversion coating, priming and finish coat ensuring superior adhesion, high corrosion resistance and good colour stability. The coils to be painted on both sides after degreasing. Inside surface to have a primer of 5microns and a coat of natural colour of 5microns, exposed surface to have a primer of 5microns, binder of 5microns and topcoat of approved colour of 15 microns. All ceiling shall be Green pro Certified: For LEED certification by Indian Green Building council (IGBC). Ceiling manufacturer should have local manufacturing unit in India. Manufacturer should have Roll-forming machine to produce Baffle panels & in-house testing lab in India & having more than 20 years of existence in India. Approved Makes - Hunter Douglas, Gorden, SAS, Armstrong | 20.00 | M2 |  | 10500.00 | 210000.00 | 2500.00 | 50000.00 | 8375.00 | 167500.00 | 50000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
174.00 | BXD Ceiling System Supply of LUXALON® Aluminium, un-perforated, Multi BXD Ceiling System with V closed groove: Providing & Fixing of Luxalon BXD ceiling of Aluminium panel of panel of size 30 X15 / 30X39 / 30X64 /80X15 /80X64 /120 X 15 /130 X 64 of 0.5mm/0.6mm thick, with square edges, panel length up to 6 mtr, Coil Coated on a Continuous Paint Line. Double baked and roll formed from enamelled corrosion resistance Aluminium Alloy AA5050 (Al.Mg) for higher strength and good roll forming characteristics. The ceiling panel shall be manufactured on high speed, high precision roll forming machine with ARKUSIX Hi configuration roller levelling process to ensure the flatness and to avoid the failure of metal at corners which may occur normally on press brake machine. Panel shall be clipped to baked enamelled Aluminium panel carrier of 62mm wide x 29mm deep made of 0.95mm thick in standard length of 5mtrs made of double Baked enamelled Aluminium alloy AA5050 (Al.Mg.) black with cutouts to hold the panels in a module of 50mm (width of gap 20mm open) The Carrier shall be suspended by means of G.I. suspension rod 4mm diameter and a Galvanised suspension spring clip at a distance of 1.7mtrs c/c. Paint finish: Aluminium panels shall be chromatised for maximum bond between metal and paint enamelled twice under high temperature, one side with full primer and finish coat the other side (innerside) with a primer coating and Skin Coat on a Continuous Paint Line. The ceiling system should meet the required standards for GreenPro certification and should qualify as green product as per CII green products and services council. The manufacturer should be ISO 9001:2015 Quality Management System Certification compliant with in house testing facility and should have their own manufacturing plant in India. Mode of Measurements: Measurements shall be wall to wall without any deductions for lights, diffusers, columns etc. All ceiling shall be Green pro Certified: For LEED certification by Indian Green Building council (IGBC). Ceiling manufacturer should have local manufacturing unit in India. Manufacturer should have Roll-forming machine to produce Baffle panels & in-house testing lab in India & having more than 20 years of existence in India. Approved Makes - Hunter Douglas, Gorden, SAS, Armstrong | 20.00 | M2 |  | 10500.00 | 210000.00 | 2500.00 | 50000.00 | 9950.00 | 199000.00 | 50000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
175.00 | PERFORATED METAL LINEAR PLANK CEILING 300mm wide Perforated panel + NWT - Providing 300mm wide perforated 2.0 mm diameter 5mm c/c pasted with NWT corrosion resistant Aluminium Magnesium Alloy metal ceiling consisting of panel 300m wide x 30 mm deep x 0.7 mm thick with bevel edge having panel minimum length of 5mtrs. coil coated on a continuous paint line, Double baked and roll formed for higher straight and good roll forming characteristics with 21% perforation in White finish color. The ceiling panel shall be manufactured on high speed, high precision roll forming machinewith ARKUSIX Hi configuration roller levelling process to ensure the flatness and to avoid the failure of metal at corners which may occur normally on press brake machine. The panel ends are raised up to 29 mm . The panel about each other with a narrow V groove. Panel shall be clipped to a backed enamelled aluminium panel carrier of 41.5 mm wide x 62 mm deep x 0.95 mm thick in standard length of 5 mtrs. made of double baked enamelled aluminium magnesium alloy black with cut outs to hold panels module of 300 mm and at distance of 2.4 mtrs. the carrier shall be suspended by means of GI suspension rod 4mm diameter and suspension clip at 1.3 mtr. distance. The coils to go through 4 stages of pre-treatment, three times oven baked through conversion coating, priming and finish coat ensuring superior adhesion, high corrosion resistance and good colour stability. The coils to be painted on both sides after degreasing. Inside surface to have a primer of 5 microns and a coat of natural colour of 5 microns, exposed surface to have a primer of 5 microns, binder of 5 microns and topcoat of approved colour of 15 microns. If any MS Sub structure is required, it shall be paid separately in the respective individual item. The Metal ceiling should be Tested for Seismic Zone V compliance as per IS 1893 part 1-2016. | 20.00 | M2 |  | 8550.00 | 171000.00 | 1500.00 | 30000.00 | 3450.00 | 69000.00 | 30000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
176.00 | Paint finish : The coils to go through various stages of pre-treatment, oven baked through conversion coating, priming and finish coat ensuring superior adhesion, high corrosion resistance and good colour stability. The coils to be painted on both sides after degreasing. Inside surface to have a primer of 5 microns and a coat of natural colour of 5 microns, exposed surface to have a primer of 5 microns, binder of 5 microns and topcoat of approved colour of 15 microns. Green-pro certification: For LEED certification by Indian Green Building Council (IGBC) and ISO 9001: 2015 Quality Management System Certification. Approved Makes - Hunter Douglas, Gorden, SAS, Armstrong
177.00 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF Spider Rope Descender System along with Full Body Harness for minimum 30 mtr. height for Building facade cleaning and maintenance consisting of following equipments which collectively makes 1 SET: Grip Descender - EN 34 Type E2 Class A & EN 12841 Type C - 1 No. Edge Protector - EN 12278 - 1 No. HPPE liner with Embossed latex - EN 388 & EN 407 - 1 Pair Set Kernmantle rope with connector - EN 1891 - 50 mtr. - 2 Set Steel Screw locking Karabiner - PN112 EN 362 (Class B) (Class M) Anchorage webbing sling - EN 795 Type B - 1.2 mtr. - 2 No. Guided type fall arrestor system on flexible anchorage line - EN 353.2 - 1 No. Tower harness - EN 361/ 358/ 813 - 1 No. Bag - BG 12 - 1 No. Parapet Anchor of Minimum Breaking Strength : 23kN, Flange width adjustable from 60mm to 360mm - EN 795 : 2012 - 1 No. The rate includes 1 Site Demonstration of complete setup by trained personnel in front of client/ end user. Approved Makes - Karam, IBS Safety, Neo Safety Products, 3M, Udyogi | 5.00 | SET |  | 34000.00 | 170000.00 | 100000.00 | 500000.00 | 44500.00 | 222500.00 | 170000.00 | MANNU LAL AND SONS
178.00 | Demolishing of C.C./ R.C.C./ R.B./ Brick/ Concrete Block/ Stone Masonary/ Dressed stone work/ steel, etc. work manually/ by mechanical means including stacking of steel bars and disposal of complete unserviceable material/ debris/ steel/ moorum/ building rubbish/ malba/ similar unserviceable, dismantled or waste material by mechanical transport including loading, transporting, unloading to approved municipal dumping ground for lead upto 5 KM away from the site and for all lifts (considering the maximum disposal location at 5 KM distance and is to be done at designated area as per prevailing local norms at Contractor's own responsibility including any royalties, etc. all), complete as per directions of Engineer-in-charge. Note - item to be applicable in urban areas having directions for restricted hours for movement/ plying of load carrying motor vehicle of 3.5 cum or more as per direction of Engineer - in- charge. All such unserviceable material/ debris/ steel/ moorum/ building rubbish/ malba/ similar unserviceable, dismantled or waste material to be completely cleared as directed by Engineer-In-Charge. The cost is inclusive of all to complete all demolishing, disposal, transportation, loading/ unloading, stacking etc. Bidders are requested to visit site to analyze all such quantum of work before quoting. | 11.00 | M3 |  | 3000.00 | 33000.00 | 8500.00 | 93500.00 | 2450.00 | 26950.00 | 26950.00 | Innovations Workspace Solutions Pvt. Ltd.
179.00 | FIRE FIGHTING WORK
180.00 | FIRE FIGHTING WORK
181.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges,tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required :
182.00 | 25 mm dia | 1400.00 | M |  | 539.00 | 754600.00 | 118.00 | 165200.00 | 595.00 | 833000.00 | 165200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
183.00 | 32 mm dia | 100.00 | M |  | 590.00 | 59000.00 | 155.00 | 15500.00 | 705.00 | 70500.00 | 15500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
184.00 | 40 mm dia | 200.00 | M |  | 715.00 | 143000.00 | 180.00 | 36000.00 | 915.00 | 183000.00 | 36000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
185.00 | 50 mm dia | 200.00 | M |  | 781.00 | 156200.00 | 265.00 | 53000.00 | 1240.00 | 248000.00 | 53000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
186.00 | 65 mm dia | 200.00 | M |  | 1089.00 | 217800.00 | 350.00 | 70000.00 | 1455.00 | 291000.00 | 70000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
187.00 | 80 mm dia | 300.00 | M |  | 1260.00 | 378000.00 | 424.00 | 127200.00 | 1815.00 | 544500.00 | 127200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
188.00 | 100 mm dia | 70.00 | M |  | 1722.00 | 120540.00 | 634.00 | 44380.00 | 2345.00 | 164150.00 | 44380.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
189.00 | 150 mm dia | 300.00 | M |  | 2080.00 | 624000.00 | 938.00 | 281400.00 | 3255.00 | 976500.00 | 281400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
190.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required :
191.00 | 150 mm dia | 7.00 | EA |  | 6050.00 | 42350.00 | 9188.00 | 64316.00 | 7700.00 | 53900.00 | 42350.00 | MANNU LAL AND SONS
192.00 | 80mm dia | 16.00 | EA |  | 4637.00 | 74192.00 | 2382.00 | 38112.00 | 5390.00 | 86240.00 | 38112.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
193.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS:5312 complete with rubber gasket, GI bolts, nuts,washers etc.as required : 150 mm dia | 1.00 | EA |  | 10800.00 | 10800.00 | 11718.00 | 11718.00 | 770.00 | 770.00 | 770.00 | Innovations Workspace Solutions Pvt. Ltd.
194.00 | Supplying and fixing single headed internal hydrant valve with instantaneous Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required : Single headed Gunmetal | 16.00 | EA |  | 5720.00 | 91520.00 | 4685.00 | 74960.00 | 5915.00 | 94640.00 | 74960.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
195.00 | Providing & fixing flow switch in following sizes M.S.pipe including connection etc as required. 100 mm dia | 14.00 | EA |  | 11220.00 | 157080.00 | 4945.00 | 69230.00 | 10010.00 | 140140.00 | 69230.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
196.00 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red,conforming to IS 884 complete with the following as required. 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket. 40 m | 14.00 | EA |  | 8470.00 | 118580.00 | 3861.00 | 54054.00 | 10935.00 | 153090.00 | 54054.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
197.00 | Providing & fixing angle iron (40 mm x 40 mm x 5mm) door frame and MS sheet (2mm thick) cum glass shutter of size 2.1 mtr. X 1.2 mtr. (N.S.) with 25 mm x 25 mm x 3 mm angle fram all around & stiffened in between i/c hinges, handle, locking arrangement, painting with approved synthetic enamel paint i/c sign writing on grass at internal hydrant including providing & fixing M.S.Sheet 2 mm thick on remaining portion above door to close opening i/c painting etc. as required. | 14.00 | EA |  | 16500.00 | 231000.00 | 9000.00 | 126000.00 | 20330.00 | 284620.00 | 126000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
198.00 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required : Gun Metal | 32.00 | EA |  | 4300.00 | 137600.00 | 1758.00 | 56256.00 | 5390.00 | 172480.00 | 56256.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
199.00 | Providing and fixing standard fire man's axe (Tested for 20000 volts) with heavily insulated rubber handle (ISI marked) | 16.00 | EA |  | 1200.00 | 19200.00 | 700.00 | 11200.00 | 280.00 | 4480.00 | 4480.00 | Innovations Workspace Solutions Pvt. Ltd.
200.00 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories :
201.00 | Upright Sprinkler | 670.00 | EA |  | 460.00 | 308200.00 | 400.00 | 268000.00 | 395.00 | 264650.00 | 264650.00 | Innovations Workspace Solutions Pvt. Ltd.
202.00 | Pendent Sprinkler | 670.00 | EA |  | 456.00 | 305520.00 | 400.00 | 268000.00 | 380.00 | 254600.00 | 254600.00 | Innovations Workspace Solutions Pvt. Ltd.
203.00 | Horizontal side wall sprinkler | 14.00 | EA |  | 495.00 | 6930.00 | 450.00 | 6300.00 | 620.00 | 8680.00 | 6300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
204.00 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets,center bracket, stockbar of following sizes complete as required.
205.00 | 700mm | 70.00 | EA |  | 943.00 | 66010.00 | 795.00 | 55650.00 | 4120.00 | 288400.00 | 55650.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
206.00 | 1000mm | 70.00 | EA |  | 1127.00 | 78890.00 | 945.00 | 66150.00 | 1210.00 | 84700.00 | 66150.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
207.00 | 1200mm | 70.00 | EA |  | 1690.00 | 118300.00 | 1015.00 | 71050.00 | 4525.00 | 316750.00 | 71050.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
208.00 | 1500mm | 70.00 | EA |  | 2100.00 | 147000.00 | 1137.00 | 79590.00 | 1305.00 | 91350.00 | 79590.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
209.00 | Providing & fixing dial type pressure gauge (dial diameter 100 mm, caliberation 0-15 kg/sqcm) with ball valve and pipe at hydrant station. | 30.00 | EA |  | 1996.00 | 59880.00 | 2200.00 | 66000.00 | 2555.00 | 76650.00 | 59880.00 | MANNU LAL AND SONS
210.00 | Providing, fixing and installation of 25mm dia gunmetal inspecting & testing assembly with ball valve, gunmetal sight glass, bye pass valve & connected to drain line complete in all respects. (Flow switch shall be set to activate between 30 to 60 second upon opening of the test valve.) | 14.00 | EA |  | 6050.00 | 84700.00 | 1200.00 | 16800.00 | 7810.00 | 109340.00 | 16800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
211.00 | Supplying and fixing orifice plate made out of 6 mm thick stainless steel (Grade 304) with orifice of required size to be fitted between flange & landing valve of external and internal hydrants to reduce pressure at the outlet to the level of 3.5 kg/cm 2 complete as required. | 14.00 | EA |  | 5000.00 | 70000.00 | 4500.00 | 63000.00 | 4970.00 | 69580.00 | 63000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
212.00 | Providing and fixing MS cabinet (size 600 x 450 x 150 mm) fabricated from 16 gauge MS sheet with full front glass door & locking arrangement with suitable shelves for keeping 60 Nos. spare sprinklers & one no. spanner properly fixed in shelves. Cabinet shall be painted with enamel paint of approved shade. (Cost shall include 25 Nos. (Pendent 15 Nos, upright 5 & extended through Side wall 5 Nos) spare sprinklers & one No. spanner). | 1.00 | EA |  | 6000.00 | 6000.00 | 8700.00 | 8700.00 | 7100.00 | 7100.00 | 6000.00 | MANNU LAL AND SONS
213.00 | Providing and fixing gunmetal single acting air release valve for each risers with screwed inlet with ball valve as per IS : 12992 rated for 16 Kg/cm2 pressure rating. (25 mm dia) | 4.00 | EA |  | 2695.00 | 10780.00 | 2500.00 | 10000.00 | 6815.00 | 27260.00 | 10000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
214.00 | Providing and fixing in position approved make fire bucket of 24 gauge, galvanized steel, standard 9 liters capacity and of round bottom shape, panted white inside and red outside and black on bottom dome with letters ‘FIRE’ in black and gold with all mounting bracket and screws. | 4.00 | EA |  | 550.00 | 2200.00 | 2500.00 | 10000.00 | 335.00 | 1340.00 | 1340.00 | Innovations Workspace Solutions Pvt. Ltd.
215.00 | Providing and fixing of fire Bucket Stand including sheet metal (16 gauge) shade for 4 buckets. Platform and associated civil works complete. | 8.00 | EA |  | 1500.00 | 12000.00 | 3500.00 | 28000.00 | 3150.00 | 25200.00 | 12000.00 | MANNU LAL AND SONS
216.00 | Providing and fixing of ISI marked Portable Fire Extinguisher, CO2 type of 6 Kg capacity flat base conforming to IS: 15683 : 2006 including valve, discharge hose of not less than 10mm dia. 1m long and complete in all respect including initial fill with CO2 gas conforming to IS: 307-1966 filled to a filling ratio of not more than 0.667 and wall suspension bracket. | 14.00 | EA |  | 5720.00 | 80080.00 | 4500.00 | 63000.00 | 8370.00 | 117180.00 | 63000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
217.00 | Providing and fixing of 6 Kg capacity Dry Chemical Powder, Portable Fire Extinguisher, dry powder type (Gas Cartridge) conforming to IS: 15683 : 2006 with cylinder initially fully charged with dry powder, ISI marked confirming to IS:15683 : 2006 complete with standard discharge valve with tube, CI bracket for wall mounting. | 14.00 | EA |  | 2640.00 | 36960.00 | 4200.00 | 58800.00 | 3175.00 | 44450.00 | 36960.00 | MANNU LAL AND SONS
218.00 | Providing and fixing of ISI marked portable fire extinguisher Mech. Foam type capacity 9 liters conforming to IS: 15683 : 2006 with gunmetal cap and nozzle and complete in all respects including initial fill and wall suspension. | 3.00 | EA |  | 2695.00 | 8085.00 | 9000.00 | 27000.00 | 3335.00 | 10005.00 | 8085.00 | MANNU LAL AND SONS
219.00 | Providing and fixing of ISI marked Fire and wall suspension bracket, Extinguisher, Trolley mounted carbon-dioxide type capacity 22.5 Kg. conforming to IS: 2878 Flat base including valve, discharge hose of not less than 10mm dia 1m long complete in all respects including wheeled trolley, carrying handle and initial fill with CO2 gas as per IS: 307-1996 filled to a filling ratio of not more than 0.667. | 3.00 | EA |  | 24420.00 | 73260.00 | 17000.00 | 51000.00 | 19575.00 | 58725.00 | 51000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
220.00 | Providing and fixing of ISI marked fire extinguisher Trolly mounted Mechanical Foam type capacity 50 liters with gunmetal cap and nozzle, trolley mounted and complete in all respects including initial fill. | 3.00 | EA |  | 14311.00 | 42933.00 | 37000.00 | 111000.00 | 9990.00 | 29970.00 | 29970.00 | Innovations Workspace Solutions Pvt. Ltd.
221.00 | Providing & fixing ISI marked portable fire extinguisher, water Carbon dioxide (CO2) type of 9 liters capacity conforming to IS : 15683 : 2006 with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets. | 14.00 | EA |  | 2860.00 | 40040.00 | 8500.00 | 119000.00 | 2835.00 | 39690.00 | 39690.00 | Innovations Workspace Solutions Pvt. Ltd.
222.00 | Providing & fixing of weather proof hose cabinets fabricated from 16 g M.S. sheet with full glass door and locking arrangement, suitable to accommodate 2 nos.15m long 63mm dia hose, 1 branch pipe, 1 No fire man's axe."Fire Hose" written on front including suitably mounted on a raised masonry platform as required. (Approx.size 0.6 m x 0.6m x 0.45m). Cabinet shall be provided with angle at the edges to reinforced the cabinet. | 2.00 | EA |  | 3520.00 | 7040.00 | 8700.00 | 17400.00 | 4715.00 | 9430.00 | 7040.00 | MANNU LAL AND SONS
223.00 | Providing of ABC modular type Fire Extinguisher, ceiling mounted 5 KG. Capacity, complete in all respect.(automatic) | 35.00 | EA |  | 2420.00 | 84700.00 | 7100.00 | 248500.00 | 2610.00 | 91350.00 | 84700.00 | MANNU LAL AND SONS
224.00 | PLUMBING WORK
225.00 | INTERNAL COLD WATER SUPPLY SYSTEM
226.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings INCLUDING bend, elbow, door, tee, Y tee, end cap etc. all complete wherever required with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls
227.00 | 15mm dia nominal bore | 370.00 | M |  | 400.00 | 148000.00 | 50.00 | 18500.00 | 365.00 | 135050.00 | 18500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
228.00 | 20mm dia nominal bore | 220.00 | M |  | 475.00 | 104500.00 | 55.00 | 12100.00 | 515.00 | 113300.00 | 12100.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
229.00 | 25mm dia nominal bore | 100.00 | M |  | 600.00 | 60000.00 | 60.00 | 6000.00 | 695.00 | 69500.00 | 6000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
230.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes,having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings INCLUDING bend, elbow, door, tee, Y tee, end cap etc. all complete wherever required with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall
231.00 | 20mm dia nominal bore | 20.00 | M |  | 300.00 | 6000.00 | 335.00 | 6700.00 | 475.00 | 9500.00 | 6000.00 | MANNU LAL AND SONS
232.00 | 25mm dia nominal bore | 20.00 | M |  | 400.00 | 8000.00 | 401.00 | 8020.00 | 665.00 | 13300.00 | 8000.00 | MANNU LAL AND SONS
233.00 | 32mm dia nominal bore | 40.00 | M |  | 500.00 | 20000.00 | 518.00 | 20720.00 | 1115.00 | 44600.00 | 20000.00 | MANNU LAL AND SONS
234.00 | 40mm dia nominal bore | 150.00 | M |  | 625.00 | 93750.00 | 702.00 | 105300.00 | 1120.00 | 168000.00 | 93750.00 | MANNU LAL AND SONS
235.00 | 50mm dia nominal bore | 100.00 | M |  | 900.00 | 90000.00 | 934.00 | 93400.00 | 1125.00 | 112500.00 | 90000.00 | MANNU LAL AND SONS
236.00 | 65mm dia nominal bore | 40.00 | M |  | 1300.00 | 52000.00 | 1214.00 | 48560.00 | 2325.00 | 93000.00 | 48560.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
237.00 | 80mm dia nominal bore | 5.00 | M |  | 1800.00 | 9000.00 | 1494.00 | 7470.00 | 2995.00 | 14975.00 | 7470.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
238.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
239.00 | 25 mm nominal bore | 30.00 | EA |  | 500.00 | 15000.00 | 622.00 | 18660.00 | 1250.00 | 37500.00 | 15000.00 | MANNU LAL AND SONS
240.00 | 20 mm nominal bore | 10.00 | EA |  | 450.00 | 4500.00 | 539.00 | 5390.00 | 1050.00 | 10500.00 | 4500.00 | MANNU LAL AND SONS
241.00 | 40 mm nominal bore | 4.00 | EA |  | 650.00 | 2600.00 | 828.00 | 3312.00 | 3150.00 | 12600.00 | 2600.00 | MANNU LAL AND SONS
242.00 | 50 mm nominal bore | 1.00 | EA |  | 800.00 | 800.00 | 1026.00 | 1026.00 | 5250.00 | 5250.00 | 800.00 | MANNU LAL AND SONS
243.00 | 80 mm nominal bore | 1.00 | EA |  | 2050.00 | 2050.00 | 2604.00 | 2604.00 | 8550.00 | 8550.00 | 2050.00 | MANNU LAL AND SONS
244.00 | 32 mm nominal bore | 3.00 | EA |  | 550.00 | 1650.00 | 689.00 | 2067.00 | 2250.00 | 6750.00 | 1650.00 | MANNU LAL AND SONS
245.00 | 63 mm nominal bore | 3.00 | EA |  | 1300.00 | 3900.00 | 1742.00 | 5226.00 | 6950.00 | 20850.00 | 3900.00 | MANNU LAL AND SONS
246.00 | Providing and fixing in position of approved quality high pressure rated Gun Metal Float Valve with copper ball float and brass rods of required length suitable for test pressure of not less than 15 Kg/sqcm of the following sizes: 25 mm dia | 2.00 | EA |  | 2100.00 | 4200.00 | 464.00 | 928.00 | 3850.00 | 7700.00 | 928.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
247.00 | Providing & fixing Auto Air vent for cold water supply risers, suitable for pressure not less than 15Kg/Sq.cm. 25 mm dia | 2.00 | EA |  | 2200.00 | 4400.00 | 500.00 | 1000.00 | 2850.00 | 5700.00 | 1000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
248.00 | Providing and fixing G.I. pipes complete with G.I. fittings including trenching and refilling etc, INCLUDING Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality, Providing and fixing G.I. Union in G.I. pipe including cutting and threading the pipe and making long screws etc. complete (New work) :
249.00 | 25 mm nominal dia Pipes | 50.00 | M |  | 500.00 | 25000.00 | 498.00 | 24900.00 | 1535.00 | 76750.00 | 24900.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
250.00 | 32 mm nominal dia Pipes | 50.00 | M |  | 500.00 | 25000.00 | 577.00 | 28850.00 | 1695.00 | 84750.00 | 25000.00 | MANNU LAL AND SONS
251.00 | 40 mm nominal dia Pipes | 50.00 | M |  | 600.00 | 30000.00 | 660.00 | 33000.00 | 1925.00 | 96250.00 | 30000.00 | MANNU LAL AND SONS
252.00 | 50 mm nominal dia Pipes | 200.00 | M |  | 800.00 | 160000.00 | 813.00 | 162600.00 | 1930.00 | 386000.00 | 160000.00 | MANNU LAL AND SONS
253.00 | 65 mm nominal dia Pipes | 100.00 | M |  | 900.00 | 90000.00 | 948.00 | 94800.00 | 1935.00 | 193500.00 | 90000.00 | MANNU LAL AND SONS
254.00 | 80 mm nominal dia Pipes | 10.00 | M |  | 1000.00 | 10000.00 | 1160.00 | 11600.00 | 3850.00 | 38500.00 | 10000.00 | MANNU LAL AND SONS
255.00 | Providing and fixing Connectors for connecting GI Pipe with CPVC pipes complete | 30.00 | NUM |  | 1300.00 | 39000.00 | 500.00 | 15000.00 | 2950.00 | 88500.00 | 15000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
256.00 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete :
257.00 | 20 mm nominal bore | 12.00 | EA |  | 400.00 | 4800.00 | 462.00 | 5544.00 | 1550.00 | 18600.00 | 4800.00 | MANNU LAL AND SONS
258.00 | 25 mm nominal bore | 33.00 | EA |  | 400.00 | 13200.00 | 464.00 | 15312.00 | 1750.00 | 57750.00 | 13200.00 | MANNU LAL AND SONS
259.00 | 32 mm nominal bore | 1.00 | EA |  | 400.00 | 400.00 | 470.00 | 470.00 | 2850.00 | 2850.00 | 400.00 | MANNU LAL AND SONS
260.00 | 40 mm nominal bore | 4.00 | EA |  | 500.00 | 2000.00 | 500.00 | 2000.00 | 5250.00 | 21000.00 | 2000.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
261.00 | 50 mm nominal bore | 1.00 | EA |  | 600.00 | 600.00 | 520.00 | 520.00 | 6450.00 | 6450.00 | 520.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
262.00 | INTERNAL HOT WATER SUPPLY SYSTEM WORK
263.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings INCLUDING bend, elbow, door, tee, Y tee, end cap etc. all complete wherever required with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls
264.00 | 15mm dia nominal bore | 80.00 | M |  | 450.00 | 36000.00 | 497.00 | 39760.00 | 375.00 | 30000.00 | 30000.00 | Innovations Workspace Solutions Pvt. Ltd.
265.00 | 20mm dia nominal bore | 50.00 | M |  | 500.00 | 25000.00 | 537.00 | 26850.00 | 475.00 | 23750.00 | 23750.00 | Innovations Workspace Solutions Pvt. Ltd.
266.00 | 25mm dia nominal bore | 5.00 | M |  | 600.00 | 3000.00 | 627.00 | 3135.00 | 675.00 | 3375.00 | 3000.00 | MANNU LAL AND SONS
267.00 | Providing and fixing nitrle rubber insulation on hot water supply / return pipes.
268.00 | 15 mm dia (9 mm thickness of Insulation) | 80.00 | M |  | 75.00 | 6000.00 | 497.00 | 39760.00 | 95.00 | 7600.00 | 6000.00 | MANNU LAL AND SONS
269.00 | 20 mm dia (9 mm thickness of Insulation) | 50.00 | M |  | 100.00 | 5000.00 | 537.00 | 26850.00 | 125.00 | 6250.00 | 5000.00 | MANNU LAL AND SONS
270.00 | 25 mm dia (9 mm thickness of Insulation) | 5.00 | M |  | 150.00 | 750.00 | 627.00 | 3135.00 | 175.00 | 875.00 | 750.00 | MANNU LAL AND SONS
271.00 | INTERNAL DRAINAGE, SOIL, WASTE & VENT SYSTEM
272.00 | Providing, fixing, jointing, testing and commissioning of UV stabilised UPVC pipes, Type B as per IS:13592 for soil, waste and vent, including all fittings with or without access i.e bends, junctions, cowls, offsets, couplers, connectors, heavy duty Metal pipe clamps with rubber seal/clips//holders etc. and jointing with heavy duty solvent cement, complete as per manufacturer's specifications including cutting holes in walls and floors, wherever required and making good the same, complete as directed by the Engineer-in-Charge. (vertical pipes can be jointed through rubber O rings)
273.00 | 110 mm dia | 600.00 | M |  | 600.00 | 360000.00 | 1151.00 | 690600.00 | 1115.00 | 669000.00 | 360000.00 | MANNU LAL AND SONS
274.00 | 75 mm dia | 130.00 | M |  | 500.00 | 65000.00 | 1044.00 | 135720.00 | 915.00 | 118950.00 | 65000.00 | MANNU LAL AND SONS
275.00 | Providing, fixing, jointing, testing and commissioning of uPVC pipe as per IS 4985, Class-3, 6Kg/cm2 with cement solvent joint, complete with all fittings and clamps etc including cutting and making good the walls and floors for waste pipes from wash basins, urinals and sinks & balcony drainage, as directed by the Engineer-in-charge.
276.00 | 63mm dia | 85.00 | M |  | 475.00 | 40375.00 | 1000.00 | 85000.00 | 2135.00 | 181475.00 | 40375.00 | MANNU LAL AND SONS
277.00 | 40mm dia | 125.00 | M |  | 215.00 | 26875.00 | 950.00 | 118750.00 | 745.00 | 93125.00 | 26875.00 | MANNU LAL AND SONS
278.00 | Providing & fixing in position uPVC full bore P / S trap with 50 mm water seal of following sizes for embedded area, making proper connection with M seal ,including cutting chase / hole in floors /slabs and bringing the same in proper condition and shape after placing the trap in right position complete as required. 100 mm inlet and 100 mm outlet. | 72.00 | EA |  | 600.00 | 43200.00 | 135.00 | 9720.00 | 1250.00 | 90000.00 | 9720.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
279.00 | Providing, fixing, testing and commissioning of uPVC pipe inlet fittings with maximum 3 inlets 40, 50 & 63mm OD size fixed to 'P' traps including Dripseal/Pipe seal/solvent weld joint/rubber ring joint complete . | 72.00 | EA |  | 600.00 | 43200.00 | 150.00 | 10800.00 | 2350.00 | 169200.00 | 10800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
280.00 | Providing and fixing heavy duty S.S. Floor grating (Cockroach proof) with frame of approved design including setting in floor with cement motor to match with floor finish as per architect requirement. Make - Jaquar or equivalent
281.00 | Size 150 mm x 150 mm or 125 mm dia | 72.00 | EA |  | 600.00 | 43200.00 | 2500.00 | 180000.00 | 1050.00 | 75600.00 | 43200.00 | MANNU LAL AND SONS
282.00 | Size 100 mm x 100 mm or 100 mm dia | 40.00 | EA |  | 450.00 | 18000.00 | 2350.00 | 94000.00 | 950.00 | 38000.00 | 18000.00 | MANNU LAL AND SONS
283.00 | Providing and fixing PVC ceiling COP /FCO with suitable insert keys for opening as per approved sample, properly jointed to soil and waste pipe as per requirement, complete as per instructions of the Engineer in charge. For 100 mm dia pipe | 25.00 | EA |  | 400.00 | 10000.00 | 2100.00 | 52500.00 | 1250.00 | 31250.00 | 10000.00 | MANNU LAL AND SONS
284.00 | Rain Water Drainage Providing, fixing, jointing, testing and commissioning uPVC Type B, IS:13592, 6Kg/cm2, Rain water down take pipe conforming to IS:4985 cut to required lengths including all necessary fittings and specials,fixing at wall/ceiling level supported by galvanized steel clamps & hangers, making proper connection with cement solvent joint as per BIS / manufacturer. Cutting, chases / holes in floors / walls / slab.
285.00 | 110 mm diameter | 25.00 | M |  | 900.00 | 22500.00 | 1250.00 | 31250.00 | 2550.00 | 63750.00 | 22500.00 | MANNU LAL AND SONS
286.00 | 160 mm diameter | 175.00 | M |  | 1200.00 | 210000.00 | 1450.00 | 253750.00 | 2600.00 | 455000.00 | 210000.00 | MANNU LAL AND SONS
287.00 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. sheet 1 m x1 m x 400 micron, finished with 12 mm cement plaster 1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete. | 10.00 | EA |  | 300.00 | 3000.00 | 270.00 | 2700.00 | 550.00 | 5500.00 | 2700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
288.00 | SANITARY FIXTURES & FITTINGS:
289.00 | Providing and fixing white vitreous china extended wall mounting water closet of size 770x380x630 mm of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 2 litre/ 4 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete. (JAQUAR Cat No - WHT-353SPPZ or equivalent) | 33.00 | EA |  | 8500.00 | 280500.00 | 7300.00 | 240900.00 | 12250.00 | 404250.00 | 240900.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
290.00 | Providing and fixing Hand shower (health Faucet) with 8mm dia 1.2 Meter long Flexible tube And wall Hook of quality and make as approved by Engineer - in - charge. (JAQUAR Cat No - ALD-CHR-573 or equivalent) | 33.00 | EA |  | 1700.00 | 56100.00 | 1800.00 | 59400.00 | 2450.00 | 80850.00 | 56100.00 | MANNU LAL AND SONS
291.00 | Providing and fixing first quality white vitreous china Under Counter Basin with Fixing Accessories Size: 605x430x200 Mm shape: Oval basin for under counter mounting, specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, waste coupling, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including filling gap between counter and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. (JAQUAR Cat No - CNS-WHT-705 or equivalent) | 34.00 | EA |  | 3685.00 | 125290.00 | 3000.00 | 102000.00 | 6425.00 | 218450.00 | 102000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
292.00 | Providing,fixing and testing of Sensor faucet for wash basin with base flange (battery operated) and easy-to-use of approved quality. (JAQUAR Cat No - SNR-CHR-51011 or equivalent) | 32.00 | EA |  | 13697.00 | 438304.00 | 15000.00 | 480000.00 | 12950.00 | 414400.00 | 414400.00 | Innovations Workspace Solutions Pvt. Ltd.
293.00 | Providing and fixing, testing & commissioning of Single lever basin mixer with or without popup waste system with 450mm long braided hoses complete as required. (JAQUAR Cat No - FLR-CHR-5001B or equivalent) | 2.00 | EA |  | 3500.00 | 7000.00 | 3300.00 | 6600.00 | 3545.00 | 7090.00 | 6600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
294.00 | Providing and fixing white vitreous china Urinal (back inlet) with fixing accessories size: 385x325x635 mm Sensor mini concealed type flushing valve for urinal complete set with installation box (battery operated) battery based infrared sensor operated urinal having pre & post flushing with water (250 ml & 500 ml consumption), having water inlet from back side, including fixing to wall with suitable brackets all as per manufacturers specification and direction of Engineer-in-charge. (JAQUAR Cat No - URS-WHT-13253N or equivalent) (JAQUAR Cat No - SNR-STL-51083 or equivalent) | 30.00 | EA |  | 14866.00 | 445980.00 | 8000.00 | 240000.00 | 16550.00 | 496500.00 | 240000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
295.00 | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink as per IS:13983 with C.I. brackets and stainless steel plug 40 mm,including painting of fittings and brackets, cutting and making good the walls wherever required : 610x510 mm bowl depth 200 mm | 8.00 | EA |  | 6500.00 | 52000.00 | 3890.00 | 31120.00 | 13250.00 | 106000.00 | 31120.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
296.00 | Providing and fixing SS-304. square Towel ring of approved quality. (JAQUAR Cat No - ACN-CHR-1121N or equivalent) | 18.00 | EA |  | 1500.00 | 27000.00 | 1300.00 | 23400.00 | 1260.00 | 22680.00 | 22680.00 | Innovations Workspace Solutions Pvt. Ltd.
297.00 | Providing and fixing Single towel rail 600mm long, stainless steel with PVC rawl plug & C.P. brass screw complete as required. 600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88 mm. (JAQUAR Cat No - ACN-CHR-1111SM or equivalent) | 2.00 | EA |  | 1250.00 | 2500.00 | 1400.00 | 2800.00 | 1395.00 | 2790.00 | 2500.00 | MANNU LAL AND SONS
298.00 | Providing and fixing SS steel toilet paper holder with flap of approved quality: (JAQUAR Cat No - ACN-CHR-1153N or equivalent) | 33.00 | EA |  | 1200.00 | 39600.00 | 1000.00 | 33000.00 | 1265.00 | 41745.00 | 33000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
299.00 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 15mm nominal bore | 100.00 | EA |  | 650.00 | 65000.00 | 574.00 | 57400.00 | 1050.00 | 105000.00 | 57400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
300.00 | Providing and fixing uplasticised PVC connection pipe with brass unions : 45 cm length 15 mm nominal bore | 100.00 | EA |  | 125.00 | 12500.00 | 122.00 | 12200.00 | 350.00 | 35000.00 | 12200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
301.00 | Providing and Fixing SS automatic sensor based liquid soap container with bracket of the same materials with snap fittings of approved quality . (JAQUAR Cat No - SDR-BLC-DJ0160AS or equivalent) | 34.00 | EA |  | 3945.00 | 134130.00 | 6000.00 | 204000.00 | 5750.00 | 195500.00 | 134130.00 | MANNU LAL AND SONS
302.00 | Providing & fixing 6mm thick beveled edge Looking mirror of Make: Modiguard/ Saint Gobain with 12mm thick BWP plywood in back & 75 x 50mm size frame of Teak Wood on perimeter of mirror & 10’’ x 2’’ size designer moulding as per drawing on top of Mirror including Melamine polish on wood frame & designer moulding, fixing with necessary screws etc. all complete as per directions by Engineer-in-charge. | 100.00 | M2 |  | 4300.00 | 430000.00 | 2000.00 | 200000.00 | 5150.00 | 515000.00 | 200000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
303.00 | Providing and fixing C.P. brass bib cock of approved quality conforming to IS:8931 : (JAQUAR Cat No - CHR-5047N or equivalent) 15 mm nominal bore | 35.00 | EA |  | 1915.00 | 67025.00 | 1800.00 | 63000.00 | 1675.00 | 58625.00 | 58625.00 | Innovations Workspace Solutions Pvt. Ltd.
304.00 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete. Flexible pipe 40 mm dia | 8.00 | EA |  | 150.00 | 1200.00 | 119.00 | 952.00 | 350.00 | 2800.00 | 952.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
305.00 | Providing and Fixing stainless steel twin coat hook complete as required. (JAQUAR Cat No - ACN-CHR-1161N or equivalent) | 33.00 | EA |  | 685.00 | 22605.00 | 400.00 | 13200.00 | 375.00 | 12375.00 | 12375.00 | Innovations Workspace Solutions Pvt. Ltd.
306.00 | Providing and fixing first quality white vitreous china Under Counter Basin for handicapped toilet with Fixing Accessories Size: 605x430x200 Mm shape: Oval basin for under counter mounting, specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, waste coupling, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including filling gap between counter and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. (JAQUAR Cat No - CNS-WHT-705 or equivalent) | 7.00 | EA |  | 3685.00 | 25795.00 | 2500.00 | 17500.00 | 7150.00 | 50050.00 | 17500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
307.00 | Providing and Fixing 2 Nos. support arms and backrest to mounted on the track (vertically and laterally) for handicap toilet complete as required. (JAQUAR Cat No - CHR-1507 or equivalent) (JAQUAR Cat No - WAC-WHT-0800 or equivalent) | 7.00 | EA |  | 16000.00 | 112000.00 | 1500.00 | 10500.00 | 18750.00 | 131250.00 | 10500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
308.00 | Providing and fixing white vitreous china extended wall mounting water closet of size 770x380x630 mm for handicapped toilet of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 2 litre/ 4 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete. (JAQUAR Cat No - WHT-353SPPZ or equivalent) | 7.00 | EA |  | 9200.00 | 64400.00 | 7200.00 | 50400.00 | 14950.00 | 104650.00 | 50400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
309.00 | Providing and fixing stainless steel 450 mm long and 32 mm diameter Straight Grab Bar (1 nos.) with 2 nos CP brass wall flange including cutting & making good the walls wherever required complete in all respect as per direction of engineer - in - charge . (Make - Jaquar, Euronics or equivalent) | 7.00 | EA |  | 4000.00 | 28000.00 | 2000.00 | 14000.00 | 16450.00 | 115150.00 | 14000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
310.00 | Providing and fixing stainless steel Horizontally and Vertically Movable Swing Disabled Grab Bar of 32 mm diameter (1 nos.)with necessary fittings including cutting & making good the walls wherever required complete in all respect as per direction of engineer - in - charge. (Make - Jaquar, Euronics or equivalent) | 7.00 | EA |  | 6000.00 | 42000.00 | 2500.00 | 17500.00 | 16450.00 | 115150.00 | 17500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
311.00 | Providing and Fixing, testing and commissioning of C.P. brass wall / counter mounted sink mixer with C.P. wall flange, overhead swinging spout complete as required and making good. (JAQUAR Cat No - CHR-5309 or equivalent) | 8.00 | EA |  | 6000.00 | 48000.00 | 4000.00 | 32000.00 | 4250.00 | 34000.00 | 32000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
312.00 | Providing and Fixing fully automatic stainless steel "NO TOUCH" hand drier suitable to operate on 220 volts, single phase 50 Hz, A.C power supply and directly plugged to power point complete. (JAQUAR Cat No - HDR-SSF-AK2803D or equivalent) | 23.00 | EA |  | 9000.00 | 207000.00 | 8500.00 | 195500.00 | 8250.00 | 189750.00 | 189750.00 | Innovations Workspace Solutions Pvt. Ltd.
313.00 | Providing, fixing and testing & Commissioning of storage type water heater of approved shade with copper container, glasswool insulation,stove enamelled MS jacket, thermostatically controlled inner heater with pilot neon lamps,complete as required.
314.00 | 10 Liters (JAQUAR Cat No - ELM-WHT-V010 or equivalent) | 9.00 | EA |  | 8400.00 | 75600.00 | 9500.00 | 85500.00 | 11450.00 | 103050.00 | 75600.00 | MANNU LAL AND SONS
315.00 | 25 Liters (JAQUAR Cat No - ELM-WHT-V025 or equivalent) | 1.00 | EA |  | 11000.00 | 11000.00 | 9000.00 | 9000.00 | 17500.00 | 17500.00 | 9000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
316.00 | Providing, fixing and testing & Commissioning of storage type solar water heater/ geyser system including piping and connections all of complete as required. The solar water heating system shall be designed according to the following design criterion and shall conform to the following technical specifications. 1. Design criterion:- a. Capacity : 300 LPD x 1 No. b. Output water temperature : 60 deg C c. Collector Type : Evacuated tube collector d. System Type :Non-Pressurized e. Application : Cooking/washing f. Circulation : Thermosyphon | 1.00 | EA |  | 145000.00 | 145000.00 | 13000.00 | 13000.00 | 124500.00 | 124500.00 | 13000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
317.00 | Evacuated Tube shall meet the following specifications Diameter of Tube:58mm (OD) Length of the tube: 1800mm Thickness of glass tube: 1.6mm Glass material:Borosilicate No: of tubes: 100 Absorber coating: 3 layer selective coating Absorption efficiency: >90% Emittance: <8% Vacuum: P<3x10-3 Pa
318.00 | The tank shall be non pressure type and made of stainless steel of grade X04Cr19Ni9 or X07Cr18Ni9 of IS 1570 part 5 – 1985, TIG welded. All sockets and internal fittings of the tanks should of stainless steel. The tank shall be insulated with Polyurethanefoam 50 mm thick duly formed with injunction in a machine and cladding of GI precoated sheet. All sockets and internal fittings of the tanks should be of stainless steel. External of the tank should be properly insulated so that hot water temperature does not decrease by more than 5 deg. C in about 16 hrs. Make: - Racold/ Sudarshan Saur/ Nuetech/ Sunrise
319.00 | Providing and fixing ECO365 X22 Dual Flow Chrome Finish Jet And Eco Flow Aerator of stainless steel and of inner thread diameter 22 mm and outer thread diamter 24 mm complete for all taps, faucet, etc. complete as required. | 100.00 | EA |  | 650.00 | 65000.00 | 1200.00 | 120000.00 | 250.00 | 25000.00 | 25000.00 | Innovations Workspace Solutions Pvt. Ltd.
320.00 | Providing & fixing white vitreous china water less urinal of size 600 x 330 x 315 mm having antibacterial /germs free ceramic surface, fixed with cartridge having debris catcher and hygiene seal. | 2.00 | EA |  | 15000.00 | 30000.00 | 18088.00 | 36176.00 | 45000.00 | 90000.00 | 30000.00 | MANNU LAL AND SONS
321.00 | EXTERNAL SEWRAGE,STORM WATER DRAINAGE,& WATER SUPPLY SYSTEM :
322.00 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, for all depth, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, for all leads All kind of soil Pipes, cables etc, exceeding 80mm dia but not exeeding 300 mm dia | 80.00 | M |  | 400.00 | 32000.00 | 350.00 | 28000.00 | 345.00 | 27600.00 | 27600.00 | Innovations Workspace Solutions Pvt. Ltd.
323.00 | Providing and fixing square-mouth S.W. gully trap class SP-1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design: 150x100 mm size P type With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5.00 | EA |  | 2500.00 | 12500.00 | 2500.00 | 12500.00 | 7750.00 | 38750.00 | 12500.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
324.00 | Constructing brick masonry road gully chamber 50x45x60 cm with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) including 500x450 mm pre-cast R.C.C. horizontal grating with frame complete as per standard design : with common burnt clay F.P.S.(non modular) bricks of class designation 7.5 | 2.00 | EA |  | 5200.00 | 10400.00 | 5957.00 | 11914.00 | 9950.00 | 19900.00 | 10400.00 | MANNU LAL AND SONS
325.00 | Constructing brick masonry rectangular type manhole with 75 class designation bricks in cement mortar 1:4 (1 cement : 4 coarse sand), RCC top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size), inside and outside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement inside and rough plaster on outside and making channels in cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), neatly finished complete as per standard design including excavation, refilling and disposal of surplus earth as per instructions of the Engineer-in-charge. Inside size 600x600mm and 600mm deep including S.F.R.C Perforated cover and frame (medium duty MD-10 grade designation) 455x610mm internal dimensions. | 2.00 | EA |  | 8000.00 | 16000.00 | 4500.00 | 9000.00 | 7750.00 | 15500.00 | 9000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
326.00 | Constructing brick masonry circular type manhole 0.91 m internal dia at bottom and 0.56m dia at top in cement mortar 1:4 (1 cement : 4 coarse sand), in side cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement, foundation concrete 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size), and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement, all complete as per standard design : 0.91 mm deep with SFRC Cover and frame (heavy duty , HD- 20 grade designation) 560 mm internal dia confirming of to I.S 12592 total weight of cover and frame not less than 182.Kg. fixied in cement concrete 1:2:4 (1 cement :2 coarse sand : 4 graded stone agggregate 20 mm nominal size ) including centering shutering all complete.(Excavation,foot rest and 12 mm thick plaster at the external surface shall be paid for separately) with common burnt clay F.P.S.(non module) brick of class designation 7.5 | 4.00 | EA |  | 12000.00 | 48000.00 | 5400.00 | 21600.00 | 8950.00 | 35800.00 | 21600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
327.00 | Extra depth for circular type manhole 0.91m internal dia (at bottom) beyond 0.91 m to 1.67 m. With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 10.00 | M |  | 6400.00 | 64000.00 | 1500.00 | 15000.00 | 4350.00 | 43500.00 | 15000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
328.00 | Constructing brick masonry circular manhole 1.22 m internal dia at bottom and 0.56 m dia at top in cement mortar 1:4 (1 cement :4 coarse sand) inside cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement foundation concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement, all complete as per standard design : 1.68 m deep with SFRC Cover and frame (heavy duty HD20 grade designation) 560 mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182 kg. fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including centering, shuttering all complete.(Excavation,foot rests and 12 mm thick cement plaster at the external surface shall be paid for separately) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2.00 | EA |  | 25000.00 | 50000.00 | 4200.00 | 8400.00 | 17250.00 | 34500.00 | 8400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
329.00 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910, on 12 mm dia steel bar conforming to IS: 1786, having minimum cross section as 23 mmx25 mm and over all minimum length 263 mm and width as 165 mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. | 20.00 | EA |  | 500.00 | 10000.00 | 6500.00 | 130000.00 | 650.00 | 13000.00 | 10000.00 | MANNU LAL AND SONS
330.00 | Providing, Laying, jointing and testing socket and spigot RCC pipes (NP2 class) conforming to IS:458 with stiff mixture of cement mortar in the proporation of 1:2 (1 cement : 2 find sand) laid to correct levels below ground in trenches upto required depth including excavation in all kind of soil (hard / soft), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. The quoted price shall be inclusive of providing protection to pipe all round / haunches as per specification.
331.00 | 300 mm dia | 11.00 | M |  | 1200.00 | 13200.00 | 2100.00 | 23100.00 | 2275.00 | 25025.00 | 13200.00 | MANNU LAL AND SONS
332.00 | 250 mm dia | 22.00 | M |  | 950.00 | 20900.00 | 2000.00 | 44000.00 | 1650.00 | 36300.00 | 20900.00 | MANNU LAL AND SONS
333.00 | 200 mm dia | 22.00 | M |  | 850.00 | 18700.00 | 1850.00 | 40700.00 | 1375.00 | 30250.00 | 18700.00 | MANNU LAL AND SONS
334.00 | 150 mm dia | 22.00 | M |  | 650.00 | 14300.00 | 1780.00 | 39160.00 | 1275.00 | 28050.00 | 14300.00 | MANNU LAL AND SONS
335.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
336.00 | 25 mm nominal bore | 2.00 | EA |  | 500.00 | 1000.00 | 1500.00 | 3000.00 | 1650.00 | 3300.00 | 1000.00 | MANNU LAL AND SONS
337.00 | 50 mm nominal bore | 3.00 | EA |  | 800.00 | 2400.00 | 4000.00 | 12000.00 | 2550.00 | 7650.00 | 2400.00 | MANNU LAL AND SONS
338.00 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve, with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design : With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 | 2.00 | EA |  | 10000.00 | 20000.00 | 4500.00 | 9000.00 | 7750.00 | 15500.00 | 9000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
339.00 | Constructing masonry Chamber 60x45x50 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for water meter complete with C.I. double flap surface box 400x200x200 mm (inside) with locking arrangement and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) , i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement : 5 fine sand:10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design : With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 | 1.00 | EA |  | 9000.00 | 9000.00 | 4500.00 | 4500.00 | 5950.00 | 5950.00 | 4500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
340.00 | Constructing masonry Chamber 30x30x50 cm inside, in brick work in cement mortar 1:4 (1 cement :4 coarse sand) for stop cock, with C. I. surface box 100x100 x75 mm (inside) with hinged cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size ) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12mm thick, finished with a floating coat of neat cement complete as per standard design : With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 | 2.00 | EA |  | 1600.00 | 3200.00 | 2500.00 | 5000.00 | 3150.00 | 6300.00 | 3200.00 | MANNU LAL AND SONS
341.00 | Providing, fixing,Testing and commissioning water meter with totaliser and direct reading Dial in KL with necessary fitting such as threaded Pieces, union pressure gauge and isolation cock, flanges/union complete with all necessary testing charge and obtaining Test Certificate from Municipal Authorities, on following size pipe line with 3 Nos. valve with by pass arragement with 1 no. strainer shall be provided at inlet and cost shall be inclusive for the same. (sample of water mater to be approved from Client and manufacturers/performance guarantee to be submitted to Client). 50 mm dia | 1.00 | M |  | 25000.00 | 25000.00 | 6500.00 | 6500.00 | 21000.00 | 21000.00 | 6500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
342.00 | Constructing recharge pit size 3 m Dia. 3 m deep (effective depth below inlet) in brick masonry in cement mortar 1:6 (1 cement : 6 coarse sand), including necessary earth work in excavation in all kinds of soil, disposal of surplus excavated earth, malba for all leads, returning the earth in layers surrounding brick work/ pipes ramming and watering etc., laying 150 mm thick plain cement concrete 1:4:8 (1 cement: 4 coarse sand: 8 graded stone aggregate 40 mm nominal size) in base, 150 mm thick RCC top slab, RCC columns and beams in cement concrete 1:2:4 (1 cement 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) if required as per structural requirements, including steel work welded in built-up sections/framed work, cutting hoisting and fixing in position required for gratings, frames, guard bars, ladders, brackets etc. and applying a priming coat of approved steel primer with two or more coats of synthetic enamel paint. (Shop drawing to be got approved before execution) | 6.00 | EA |  | 215000.00 | 1290000.00 | 15500.00 | 93000.00 | 142500.00 | 855000.00 | 93000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
343.00 | Boring 300mm dia- 1 Nos. bore (Min 25 m depth or at least 5M above water table) with calyx machine or as required, including the cost of transportation of boring macine to site and taking back after completion of work, providing and fixing a) 160 O.D. uPVC pipe (class 6 Kg/cm2) with fittings in bore b) 160 O.D. uPVC slotted (Supreme/Finolex class 6 Kg/cm2) with fittings in bore , as per site conditions. Providing and fixing bail plug and well cap for 160 OD pipe, supplying and filling 300 mm thick round Boulders (50-200 mm size) in first layer, 300 mm thick Gravels (5-10 mm size) in second layer, 300 mm thick Coarse Sand/fine gravel (1.5 to 2 mm size), Pea gravel packing between bore and pipe 3-6 mm size, 2 nos. 560 mm dia M.S. MH cover heavy duty fixing in top slab. Complete in all respects as per drawings enclosed. | 6.00 | EA |  | 81000.00 | 486000.00 | 120000.00 | 720000.00 | 149500.00 | 897000.00 | 486000.00 | MANNU LAL AND SONS
344.00 | De-Silting Chamber: Construction of brick masonry desilting chamber of size 2000x1500x750mm (effective depth) before recharge well with 75 class designation bricks in cement mortar 1:4 (1 cement : 4 coarse sand) , foundation concrete 1:4:8 mix (1 cement : 4 coarse sand; 8 graded stone aggregate 40mm nominal size), inside and outside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement inside and rough plaster on outside, including fixing of grating, neatly finished complete in all respects including neccessary excavation, refilling and disposal of surplus earth, complete. | 6.00 | EA |  | 30000.00 | 180000.00 | 85000.00 | 510000.00 | 34950.00 | 209700.00 | 180000.00 | MANNU LAL AND SONS
345.00 | Providing and fixing G.I. pipes complete with G.I. fittings including trenching and refilling etc. (External work) 50 mm nominal outer dia Pipes | 80.00 | M |  | 600.00 | 48000.00 | 1850.00 | 148000.00 | 2495.00 | 199600.00 | 48000.00 | MANNU LAL AND SONS
346.00 | Providing and fixing polyshield outer mechanical protection on nitrile rubber insulation comprising of wrapping with poly glass tape helically wound and subsequently applying 2 coats of polyshield material (resin & hardner) for external water pipes as per manufacturers specification. 50 mm dia (13 mm thickness of insulation) | 80.00 | M |  | 200.00 | 16000.00 | 3200.00 | 256000.00 | 450.00 | 36000.00 | 16000.00 | MANNU LAL AND SONS
347.00 | Supplying & installation of automatic type switching submersible pump set for DEWATERING at trenches, etc. directly coupled with 5 HP motor nominal speed 2900 RPM suitable for operation on 3-phase, 50 cycles, 400 + 5% volts A.C. power supply including MCC/ Control panels with level controller, auto control, NRV and to give yield of 5000 LPH at a head of 50 mtrs. Rate to be quoted complete for pump including all cabling, starter, gauge, NRV, inlet outlet valve, flanges and gauge, etc. complete in all respect. Total head = 50 Mt Flow rate = 9000 LPH H P = Minimum 5 HP (Or as per site condition) | 1.00 | SET |  | 120000.00 | 120000.00 | 85000.00 | 85000.00 | 84500.00 | 84500.00 | 84500.00 | Innovations Workspace Solutions Pvt. Ltd.
348.00 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, IS : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. (L means Litre here) | 2000.00 | L |  | 10.50 | 21000.00 | 11.00 | 22000.00 | 15.00 | 30000.00 | 21000.00 | MANNU LAL AND SONS
349.00 | BOREWELL WORKS
350.00 | Boring/drilling bore well of required dia for casing/ strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer –in-charge, upto 90 metre depth below ground level. All types of soil 300 mm dia | 100.00 | M |  | 600.00 | 60000.00 | 1800.00 | 180000.00 | 461.64 | 46164.00 | 46164.00 | Innovations Workspace Solutions Pvt. Ltd.
351.00 | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge. 200 mm nominal size dia | 50.00 | M |  | 1200.00 | 60000.00 | 1750.00 | 87500.00 | 1023.47 | 51173.50 | 51173.50 | Innovations Workspace Solutions Pvt. Ltd.
352.00 | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC medium well Casing (CM) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge. 200 mm nominal size dia | 50.00 | M |  | 1050.00 | 52500.00 | 1750.00 | 87500.00 | 960.62 | 48031.00 | 48031.00 | Innovations Workspace Solutions Pvt. Ltd.
353.00 | Gravel packing in tubewell construction in accordance with IS: 4097, including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 6.00 | M3 |  | 1500.00 | 9000.00 | 5500.00 | 33000.00 | 1349.58 | 8097.48 | 8097.48 | Innovations Workspace Solutions Pvt. Ltd.
355.00 | Providing and fixing suitable size threaded mild steel cap or spot welded plate to the top of bore well housing/ casing pipe, removable as per requirement, all complete for borewell of: 200 mm dia | 1.00 | EA |  | 800.00 | 16000.00 | 7500.00 | 150000.00 | 772.79 | 15455.80 | 15455.80 | Innovations Workspace Solutions Pvt. Ltd.
356.00 | Providing and fixing M.S. clamp of required dia to the top of casing/ housing pipe of tubewell as per IS: 2800 (part I), including necessary bolts & nuts of required size complete. 200 mm clamp | 1.00 | EA |  | 300.00 | 300.00 | 2000.00 | 2000.00 | 253.16 | 253.16 | 253.16 | Innovations Workspace Solutions Pvt. Ltd.
357.00 | Providing and fixing Bail plug/ Bottom plug of required dia to the bottom of pipe assembly of tubewell as per IS:2800 (part I). 200 mm dia | 1.00 | EA |  | 1600.00 | 1600.00 | 2000.00 | 2000.00 | 1523.90 | 1523.90 | 1523.90 | Innovations Workspace Solutions Pvt. Ltd.
358.00 | Providing and fixing factory made precast RCC perforated drain covers, having concrete of strength not less than M-25, of size 1000 x 450x50 mm, reinforced with 8 mm dia four nos longitudinal & 9 nos cross sectional T.M.T. hoop bars, including providing 50 mm dia perforations @ 100 to 125 mm c/c, including providing edge binding with M.S. flats of size 50 mmmm x 1.6 mm complete, all as per direction of Engineer-in-charge. | 1.00 | EA |  | 300.00 | 300.00 | 3500.00 | 3500.00 | 277.31 | 277.31 | 277.31 | Innovations Workspace Solutions Pvt. Ltd.
359.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 50 mm nominal bore | 1.00 | EA |  | 1200.00 | 1200.00 | 1450.00 | 1450.00 | 1091.10 | 1091.10 | 1091.10 | Innovations Workspace Solutions Pvt. Ltd.
360.00 | Providing and fixing gun metal non- return valve of approved quality (screwed end) : 50 mm nominal bore | 1.00 | EA |  | 850.00 | 850.00 | 1500.00 | 1500.00 | 783.24 | 783.24 | 783.24 | Innovations Workspace Solutions Pvt. Ltd.
361.00 | Providing and fixing G.I. pipes complete with G.I. fittings including trenching and refilling etc.
362.00 | 65 mm dia nominal bore | 30.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
363.00 | 80 mm dia nominal bore | 10.00 | M |  | 700.00 | 21000.00 | 2500.00 | 75000.00 | 645.19 | 19355.70 | 19355.70 | Innovations Workspace Solutions Pvt. Ltd.
364.00 | Supplying & installation of submersible pump set directly coupled with 5 HP motor nominal speed 2900 RPM suitable for operation on 3-phase, 50 cycles, 400 + 5% volts A.C. power supply to give yield of 5000 LPH at a head of 50 mtrs. Total head = 50 Mt Flow rate = 9000 LPH H P = Minimum 5 HP (Or as per site condition) | 1.00 | SET |  | 850.00 | 8500.00 | 3000.00 | 30000.00 | 780.71 | 7807.10 | 7807.10 | Innovations Workspace Solutions Pvt. Ltd.
365.00 | Providing, laying, testing & commissioning of 'C' class heavy duty G.I. pipe conforming to IS 1239 including welding, fittings like elbows, tees, flanges, tapers, nuts, bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 80 mm dia (coloumn pipe) | 50.00 | M |  | 155000.00 | 155000.00 | 55000.00 | 55000.00 | 144968.64 | 144968.64 | 55000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
366.00 | STP AND WTP WORK
367.00 | STP AND WTP WORK
368.00 | Supply, installation, testing & commissioning of Chlorine dosing system comprising of 100 ltrs HDPE tank with 0-12 lph electronic metering type pump. | 2.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
369.00 | ELECTRICAL WORK
370.00 | WIRING
371.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C (P means POINT here) | 900.00 | P |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
372.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
373.00 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 12800.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
374.00 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 16500.00 | M |  | 246.00 | 3148800.00 | 302.00 | 3865600.00 | 150.00 | 1920000.00 | 1920000.00 | Innovations Workspace Solutions Pvt. Ltd.
375.00 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | 30.00 | M |  | 298.00 | 4917000.00 | 365.00 | 6022500.00 | 180.00 | 2970000.00 | 2970000.00 | Innovations Workspace Solutions Pvt. Ltd.
376.00 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 125.00 | M |  | 393.00 | 11790.00 | 470.00 | 14100.00 | 225.00 | 6750.00 | 6750.00 | Innovations Workspace Solutions Pvt. Ltd.
377.00 | 4 X 16 sq. mm + 2 X 6 sq. mm earth wire | 110.00 | M |  | 673.00 | 84125.00 | 780.00 | 97500.00 | 355.03 | 44378.75 | 44378.75 | Innovations Workspace Solutions Pvt. Ltd.
378.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required
379.00 | 20mm | 120.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
380.00 | 25mm | 135.00 | M |  | 80.00 | 9600.00 | 128.00 | 15360.00 | 125.00 | 15000.00 | 9600.00 | MANNU LAL AND SONS
381.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 25.00 | EA |  | 100.00 | 13500.00 | 150.00 | 20250.00 | 265.00 | 35775.00 | 13500.00 | MANNU LAL AND SONS
382.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | 300.00 | EA |  | 36.00 | 900.00 | 45.00 | 1125.00 | 28.84 | 721.00 | 721.00 | Innovations Workspace Solutions Pvt. Ltd.
383.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 260.00 | EA |  | 426.00 | 127800.00 | 490.00 | 147000.00 | 380.00 | 114000.00 | 114000.00 | Innovations Workspace Solutions Pvt. Ltd.
384.00 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required | 14.00 | EA |  | 523.00 | 135980.00 | 595.00 | 154700.00 | 455.00 | 118300.00 | 118300.00 | Innovations Workspace Solutions Pvt. Ltd.
385.00 | Supplying and fixing brass batten/ angle holder including connection etc. as required. | 12.00 | EA |  | 78.00 | 1092.00 | 90.00 | 1260.00 | 280.00 | 3920.00 | 1092.00 | MANNU LAL AND SONS
386.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providng and fixing 2 nos. 3 pin 5/6 A modular socket outlet and 2 nos. 5/6 A modular switch, connections etc. as required. (For light plugs to be used in non residential buildings | 300.00 | EA |  | 117.00 | 1404.00 | 160.00 | 1920.00 | 275.00 | 3300.00 | 1404.00 | MANNU LAL AND SONS
387.00 | Supplying & fixing suitable size GI box wih modular plate and cover in front on surface or in recess including providing and fixing 25 A modular socket outlet and 25 A modular SP MCB, "C" curve including connections, painting etc. as required | 4.00 | EA |  | 604.00 | 181200.00 | 780.00 | 234000.00 | 610.00 | 183000.00 | 181200.00 | MANNU LAL AND SONS
388.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the FLOOR and making good the same in case of recessed conduit as required. 25 mm | 940.00 | M |  | 649.00 | 2596.00 | 830.00 | 3320.00 | 575.81 | 2303.24 | 2303.24 | Innovations Workspace Solutions Pvt. Ltd.
389.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed PVC conduit, and earthing the pointwith 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group – C (P means POINT here) | 1000.00 | P |  | 229.00 | 215260.00 | 270.00 | 253800.00 | 194.76 | 183074.40 | 183074.40 | Innovations Workspace Solutions Pvt. Ltd.
390.00 | Supplying and fixing of following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
391.00 | 1 or 2 module (75mmx 75mm) | 20.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
392.00 | 3 module (100mmx 75mm) | 3.00 | EA |  | 266.00 | 5320.00 | 310.00 | 6200.00 | 298.00 | 5960.00 | 5320.00 | MANNU LAL AND SONS
393.00 | 6 module (200mmx 75mm) | 5.00 | EA |  | 292.00 | 876.00 | 350.00 | 1050.00 | 185.00 | 555.00 | 555.00 | Innovations Workspace Solutions Pvt. Ltd.
394.00 | LIGHTS AND FAN FIXTURES
395.00 | Installation ,Testing, Commissioning of wall bracket /ceiling fittings with chain of all sizes and shapes containing upto two GLS/CFL/LED lamps per fitting, complete with all accessories including connections etc. as required | 1600.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
396.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 45 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable, including providing and fixing phenolic laminated sheet cover on the fan box etc. as required | 1.00 | EA |  | 125.00 | 200000.00 | 130.00 | 208000.00 | 225.00 | 360000.00 | 200000.00 | MANNU LAL AND SONS
397.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required Upto 450 mm sweep | 1.00 | EA |  | 500.00 | 500.00 | 300.00 | 300.00 | 450.00 | 450.00 | 300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
398.00 | Supply of lighting fixtures
399.00 | Pendant luminaire Alcove with LED (Light Emitting Diode), system power 18W, luminous flux of luminaire 1980 lm, direct light emission CRI>80, colour temperature of 4000K, Neutral white, 230V constant current driver, 70% of luminous flux after 50,000 operating hours, energy efficient LEDs, luminaire profile in aluminium, Plastic moulded end caps, Polyester powder Aluminium white coloured coat applied over a 5- stage pre-treatment, high efficiency glare-free snap fit micro-prismatic diffuser for homogeneous light distribution, ZHLS (Zero Halogen Low Smoke) internal wiring, integral electronic control gear, adjustable suspender, Protection class I, IP20, L = 1199 mm, B = 75 mm, H = 90 mm, PL max = 1500 mm Regent Model No. 7027 or equivalent in Philips/ Wipro | 45.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
400.00 | COB based LED recessed directional downlight Zena, with HPE (High-Performance Efficiency), with system power: 12 W, Luminous flux of luminaire 1200 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours; energy-efficient LEDs, direct light emission, housing in die-cast aluminium, Polyester powder-white coloured coat applied over a 5-stage pre-treatment ceiling trim, Clear glass cover with aluminium reflector and a beam angle of 36°, ZHLS (ZERO HALOGEN LOW SMOKE) wiring, electronic control gear, Protection class II, IP 20, Ø = 114 mm, DA(Ø) = 108 mm, H = 110 mm. Regent Model No.0032 or equivalent in Philips/ Wipro | 115.00 | NUM |  | 3500.00 | 157500.00 | 5200.00 | 234000.00 | 3935.00 | 177075.00 | 157500.00 | MANNU LAL AND SONS
401.00 | COB based LED recessed directional downlight Zena, with HPE (High-Performance Efficiency), with system power: 15 W, Luminous flux of luminaire 1500 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours; energy-efficient LEDs, direct light emission, housing in die-cast aluminium, Polyester powder-white coloured coat applied over a 5-stage pre-treatment ceiling trim, Clear glass cover with aluminium reflector and a beam angle of 36°, ZHLS (ZERO HALOGEN LOW SMOKE) wiring, electronic control gear, Protection class II, IP 20, Ø = 114 mm, DA(Ø) = 108 mm, H = 110 mm. Regent Model No. 0032 or equivalent in Philips/ Wipro | 160.00 | NUM |  | 1813.00 | 208495.00 | 1700.00 | 195500.00 | 835.00 | 96025.00 | 96025.00 | Innovations Workspace Solutions Pvt. Ltd.
402.00 | Recessed luminaire Casella with LED (Light Emitting Diode) system power: 32 W, Luminous flux of luminaire 3200 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, 1.4 mm thick extruded aluminium profile with Polyester powder white coloured coat applied over a 5- stage pre-treatment, Protruded opal diffuser for glare-free uniform illumination, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Protection class I, IP 40, L = 595 mm, B = 595 mm, H = 75 mm, A = 14 mm. Regent Model No. 0701 or equivalent in Philips/ Wipro | 130.00 | NUM |  | 2188.00 | 350080.00 | 2420.00 | 387200.00 | 925.00 | 148000.00 | 148000.00 | Innovations Workspace Solutions Pvt. Ltd.
403.00 | LED recessed luminaire Zen22 - SM with LED(Light Emitting Diode) system power: 32W, colour temperature of 4000K, 230V constant current driver, 70% of luminous flux after 50,000 operating hours, energy efficient LEDs, CRI>80, luminous flux of 3200 lm,direct light emission, Sheet Metal frame, polyester white powder coat applied over a 5-stage pre-treatment, Opal diffuser for glare-free uniform light, electronic control gear, Protection class I, IP40, MacAdam 3, T.H.D≤ 10%, driver efficiency ≥ 88%, surge protection of 2.5kV, L = 595mm, B = 595mm, H = 70mm Regent Model No. 0820 or equivalent in Philips/ Wipro | 130.00 | NUM |  | 2000.00 | 260000.00 | 7000.00 | 910000.00 | 1505.00 | 195650.00 | 195650.00 | Innovations Workspace Solutions Pvt. Ltd.
404.00 | Pendant luminaire Hexel with LED (Light Emitting Diode) system power: 18 W, luminous flux of luminaire 1800 lm, 4000 K, Neutral white, CRI>80, 230 V constant current driver, direct light emission, aluminium profile polyester powder coated black applied over a 5-stage pre-treatment, prismatic diffuser for homogeneous light distribution, Electronic control gear, Protection class I, IP 20, L = 400 mm, B = 350 mm, H = 67 mm, PL max 1500 mm Regent Model No. 0814 or equivalent in Philips/ Wipro | 20.00 | NUM |  | 2000.00 | 260000.00 | 7100.00 | 923000.00 | 1505.00 | 195650.00 | 195650.00 | Innovations Workspace Solutions Pvt. Ltd.
405.00 | Pendant luminaire Solo slim with HPE (High-Performance Efficiency) LED (Light Emitting Diode) system power: 26 W luminous flux of luminaire 2600 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, luminaire housing in aluminium, Polyester powder white coloured coat applied over a 5- stage pre-treatment, pre-wired backplate luminaire, Prismatic diffuser for homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Pendent tube with a ball joint, for self-levelling (+/-20°). Protection class I, IP20, Ø = 530 mm, H = 70 mm, PL = 900 mm. Regent Model No. 0116 or equivalent in Philips/ Wipro | 10.00 | NUM |  | 12000.00 | 240000.00 | 4050.00 | 81000.00 | 26600.00 | 532000.00 | 81000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
406.00 | Recessed luminaire shopping with 2 spotlights, system power: 2 x 6 W, luminous flux of luminaire 1200 lm, colour temperature of 4000K, CRI>90, 230V constant current driver, 70% of luminous flux after 50,000 operating hours, direct light emission, sheet metal housing with luminaire part in aluminium, polyester black powder coat applied over a 5-stage pre-treatment, with reflector, beam angle of 38°, Electronic control gear,Protection class II, IP20, L = 265 mm, B = 145 mm, H = 155 mm, cutout = 248 mm x 128 mm Regent Model No. 2728 or equivalent in Philips/ Wipro | 6.00 | NUM |  | 15725.00 | 157250.00 | 7900.00 | 79000.00 | 9720.00 | 97200.00 | 79000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
407.00 | Pendant luminaire Groove 2 with with HPE (High Performance Efficiency) LED (Light Emitting Diode), system power: 18 W, luminous flux of luminaire 1890 lm, Colour temperature of 4000 K, neutral white, CRI > 80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire housing in aluminium, Polyester powder black coloured coat applied over a 5- stage pre-treatment, Opal diffuser for a homogenous light distribution ZHLS (Zero Halogen Low Smoke) internal wiring, Electronic control gear, Protection class I, IP 20, Ø = 427 mm, H = 227 mm PL =1500 mm. Regent Model No. 6128 or equivalent in Philips/ Wipro | 4.00 | NUM |  | 5400.00 | 32400.00 | 4200.00 | 25200.00 | 7980.00 | 47880.00 | 25200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
408.00 | Recessed luminaire Zen 14 SM with LED (Light Emitting Diode), system power: 36 W, luminous flux of 3600 lm, colour temperature of 4000 K, Neutral white, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours, energy-efficient LEDs, CRI > 80, direct light emission, Luminaire housing in CRCA, polyester white powder coat applied over a 5-stage pre-treatment, Opal diffuser for glare-free uniform light, integral electronic control gear, Protection class I, IP40, L = 1195 mm, B = 295 mm, H = 70 mm Regent Model No. 0820 or equivalent in Philips/ Wipro | 300.00 | NUM |  | 11800.00 | 47200.00 | 7600.00 | 30400.00 | 8160.00 | 32640.00 | 30400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
409.00 | LED recessed mounted downlight BLAIRE with LED (Light Emitting Diode) for system power 10W, luminous flux of 1000 lm, CRI> 80, 230V constant current driver, colour temperature of 4000K, direct light emission, white housing with ceiling trim, in die-cast aluminium, polyester powder coat applied over a 5-stage pre-treatment, deep white satin diffuser, passive cooling, electronic control gear, Protection class II , IP 40 Ø = 140, DA(ø) = 125mm, HT = 56 mm Regent Model No. 3445 or equivalent in Philips/ Wipro | 170.00 | NUM |  | 2437.00 | 731100.00 | 4500.00 | 1350000.00 | 2310.00 | 693000.00 | 693000.00 | Innovations Workspace Solutions Pvt. Ltd.
410.00 | Wall / Surface / Ceiling Mounted luminaire Vela with HPE (High Performance Efficiency) LED (Light Emitting Diode) system power: 36 W, Luminous flux of luminaire 4680 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire profile in anodised aluminium, snap fit linear prismatic diffuser for a homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Protection class I, IP 40, L = 1188 mm, B = 65 mm, H = 42 mm Regent Model No. 6667 or equivalent in Philips/ Wipro | 55.00 | NUM |  | 950.00 | 161500.00 | 1600.00 | 272000.00 | 1775.00 | 301750.00 | 161500.00 | MANNU LAL AND SONS
411.00 | COB based recessed spotlight Aston for 12W LED, luminous flux of luminaire 1260lm, CRI>80, 230V, 4000K constant current driver, direct light emission, aluminium housing thermo painted silver with white trim, clear acrylic, high quality reflector with 38° beam angle, electronic control gear, Protection class II, IP40, Φ= 136mm, DA(Φ) = 125mm, H = 150, Regent Model No. 3138 or equivalent in Philips/ Wipro | 290.00 | NUM |  | 1900.00 | 104500.00 | 3990.00 | 219450.00 | 5395.00 | 296725.00 | 104500.00 | MANNU LAL AND SONS
412.00 | Pendant luminaire Victor with LED (Light Emitting Diode), system power: 64 W (36UP, 28DN), luminous flux of luminaire 7360 lm, colour temperature of 4000K, neutral white, CRI >80, 230V constant current driver, direct-indirect light emission, 48% UP, 52% DN aluminium housing, polyester powder coated white applied over a 5 stage pre-treatment, Opal diffuser, electronic control gear, Protection class I, IP20 L = 1186 mm, B = 220 mm, H = 105 mm Regent Model No. 0945 or equivalent in Philips/ Wipro | 20.00 | NUM |  | 1000.00 | 290000.00 | 1950.00 | 565500.00 | 835.00 | 242150.00 | 242150.00 | Innovations Workspace Solutions Pvt. Ltd.
413.00 | Pendant luminaire Alcove with LED (Light Emitting Diode), system power 28W (14W up, 14W dn), luminous flux of luminaire 3335 lm, direct-indirect light emission, CRI > 80, 4000K, neutral white, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours, energy-efficient LED's, luminaire profile in aluminium, Plastic moulded end caps, Polyester powder Aluminium white coloured coat applied over a 5- stage pre-treatment, snap-fit prismatic diffuser for homogeneous light distribution, ZHLS (Zero Halogen Low Smoke) internal wiring, integral Electronic control gear, with bluetooth controller, adjustable suspender, Protection class I, IP 20, L = 1199 mm, B = 75 mm, H = 90 mm, PL max = 1500 mm. Regent Model No. 7047 or equivalent in Philips/ Wipro | 45.00 | NUM |  | 12400.00 | 248000.00 | 12020.00 | 240400.00 | 18450.00 | 369000.00 | 240400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
414.00 | Pendant luminaire Ring with HPE (High Performance Efficiency) LED (Light Emitting Diode) system power: 60 W, Luminous flux of luminaire 5400 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire profile in aluminium, Polyester powder black coloured coat applied over a 5- stage pre-treatment, Prismatic diffuser for a homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Protection class I, IP20, Ø = 980 mm, W = 100 mm, H =67 mm, PL = 1500 mm Regent Model No. 0115 or equivalent in Philips/ Wipro | 8.00 | NUM |  | 5000.00 | 225000.00 | 920.00 | 41400.00 | 5525.00 | 248625.00 | 41400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
415.00 | Pendant luminaire Ring with HPE (High Performance Efficiency) LED (Light Emitting Diode) system power: 85 W, Luminous flux of luminaire 7650 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire profile in aluminium, Polyester powder black coloured coat applied over a 5- stage pre-treatment, Prismatic diffuser for a homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Protection class I, IP20, Ø = 1200 mm, W = 100 mm, H =67 mm, PL = 1500 mm Regent Model No. 0115 or equivalent in Philips/ Wipro | 5.00 | NUM |  | 30625.00 | 245000.00 | 23420.00 | 187360.00 | 49750.00 | 398000.00 | 187360.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
416.00 | Pendant luminaire Lightup Direct with LED(Light Emitting Diode), system power: 28W/4feet, luminous flux of luminare 3080 lm, colour temperature of 4000K, neutral white, 230V constant current driver, 70% of luminous ï¬‚ux after 50,000 operating hours, energy eï¬ƒcient LEDs, CRI>80, luminaire profile in aluminium, polyester powder coated white applied over a 5 stage pre-treatment, dual optics of lens + raster with dual asymmetric lens, ZHLS(ZERO HALOGEN LOW SMOKE) internal wiring, electronic control gear, sliding fixing wire suspension, Protection class I, IP40, L = 5190 mmX 900mm, B = 68 mm, H = 60 mm, max.PL = 1500mm Regent Model No. 0593 or equivalent in Philips/ Wipro | 3.00 | NUM |  | 39000.00 | 195000.00 | 32100.00 | 160500.00 | 66400.00 | 332000.00 | 160500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
417.00 | Pendant luminaire Lightup Direct with LED(Light Emitting Diode), system power: 28W/4feet, luminous flux of luminare 3080 lm, colour temperature of 4000K, neutral white, 230V constant current driver, 70% of luminous ï¬‚ux after 50,000 operating hours, energy eï¬ƒcient LEDs, CRI>80, luminaire profile in aluminium, polyester powder coated white applied over a 5 stage pre-treatment, dual optics of lens + raster with dual asymmetric lens, ZHLS(ZERO HALOGEN LOW SMOKE) internal wiring, electronic control gear, sliding fixing wire suspension, Protection class I, IP40, L = 6000 mmX 900mm, B = 68 mm, H = 60 mm, max.PL = 1500mm Regent Model No. 0593 or equivalent in Philips/ Wipro | 1.00 | NUM |  | 128000.00 | 384000.00 | 8570.00 | 25710.00 | 131670.00 | 395010.00 | 25710.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
418.00 | COB based pendant downlight luminaire Rea 100 with system power: 15 W, Luminous flux of luminaire 1500 lm, Colour temperature of 3000 K, warm white, SDCM 3, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire housing in aluminium, Polyester powder black coloured coat applied over a 5- stage pre-treatment, Clear glass cover, beam angle of 40°, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear,Protection class II, IP 20, Ø = 100 mm, H = 165 mm, PL = 1500 mm. Regent Model No. 3045 or equivalent in Philips/ Wipro | 105.00 | NUM |  | 140000.00 | 140000.00 | 8570.00 | 8570.00 | 152950.00 | 152950.00 | 8570.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
419.00 | Recessed luminaire Slash with HE-High Efficiency LED (Light Emitting Diode) system power: 28W, luminous flux of luminaire 2800lm, colour temperature of 4000K, neutral white, CRI>80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours, energy efficient LEDs, direct light emission, luminaire profile in anodised aluminium, pre-wired batten luminaire, opal APD (Added Performance Diffuser) diffuser for a homogenous light distribution, ZHLS(ZERO HALOGEN LOW SMOKE) internal wiring, integral electronic control gear, Protection class I, IP40 L = 1183 mm, EL = 1195 B = 48 mm, EB = 61mm, H = 70 mm Regent Model No. 0571 or equivalent in Philips/ Wipro | 20.00 | NUM |  | 1000.00 | 105000.00 | 4200.00 | 441000.00 | 2215.00 | 232575.00 | 105000.00 | MANNU LAL AND SONS
420.00 | Ceiling mounted luminaire Slash with HE-High Efficiency LED (Light Emitting Diode) system power: 28W, luminous flux of luminaire 2800lm, colour temperature of 4000K, neutral white, CRI>80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours, energy efficient LEDs, direct light emission, luminaire profile in anodised aluminium, pre-wired batten luminaire, opal APD (Added Performance Diffuser) diffuser for a homogenous light distribution, ZHLS(ZERO HALOGEN LOW SMOKE) internal wiring, integral electronic control gear, Protection class I, IP40L = 1189 mm B = 48 mm H = 70 mm P = max. 1500 mm Regent Model No. 0571 or equivalent in Philips/ Wipro | 20.00 | NUM |  | 4062.00 | 81240.00 | 4800.00 | 96000.00 | 3630.00 | 72600.00 | 72600.00 | Innovations Workspace Solutions Pvt. Ltd.
421.00 | Pendant spotlight luminaire Crest with LED (Light Emitting Diode) system power: 14 W, Luminous flux of luminaire 1120lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230 V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire profile in aluminium, Polyester powder black coloured coat applied over a 5- stage pre-treatment, Clear glass cover with anti - glare dark reflectors and beam angle of 45 degrees, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear,Protection class I, IP 20, L = 1188 mm, B = 55 mm, H = 80 mm, PL = 1500 mm Regent Model No. 7048 or equivalent in Philips/ Wipro | 10.00 | NUM |  | 4062.00 | 81240.00 | 6900.00 | 138000.00 | 3630.00 | 72600.00 | 72600.00 | Innovations Workspace Solutions Pvt. Ltd.
422.00 | LED strip (flexible) with 60 LEDs per meter,10W per Meter, 500lm, 3000K, 2835 SMD package with thermal tape of high thermal convection factor, beam angle of 120°, MacAdum 5, constant voltage driving circuit, L = 1000mm, H = 10mm, B = 1.4mm Regent Model No. 5001 or equivalent in Philips/ Wipro | 900.00 | M |  | 7000.00 | 70000.00 | 3542.00 | 35420.00 | 11970.00 | 119700.00 | 35420.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
423.00 | Pendant luminaire Solo slim with HPE (High-Performance Efficiency) LED (Light Emitting Diode) system power: 26 W luminous flux of luminaire 2600 lm, Colour temperature of 4000 K, Neutral white, CRI > 80, 230V constant current driver, 70% of luminous flux after 50,000 operating hours; Energy efficient LEDs, Direct light emission, luminaire housing in aluminium, Polyester powder white coloured coat applied over a 5- stage pre-treatment, pre-wired backplate luminaire, Prismatic diffuser for homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) internal wiring, Electronic control gear, Pendent tube with a ball joint, for self-levelling (+/-20°). Protection class I, IP20, Ø = 530 mm, H = 70 mm, PL = 900 mm. Regent Model No. 0116 or equivalent in Philips/ Wipro | 15.00 | NUM |  | 300.00 | 270000.00 | 2910.00 | 2619000.00 | 485.00 | 436500.00 | 270000.00 | MANNU LAL AND SONS
424.00 | Supply of ceiling fan 1200 sweep with all accessories.Make -havels or equivalent | 1.00 | EA |  | 13975.00 | 209625.00 | 5200.00 | 78000.00 | 9720.00 | 145800.00 | 78000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
425.00 | Supply of exhaust fan 450 sweep with all accesoroes and louwers | 2.00 | EA |  | 3000.00 | 3000.00 | 2100.00 | 2100.00 | 2060.00 | 2060.00 | 2060.00 | Innovations Workspace Solutions Pvt. Ltd.
426.00 | Supplying,installation,testing and commissioning of Passive Infrared(PIR) technology based occupancy sensor having high preformance, non regulating programmable type, suitable for connected load upto 10Amp , for mounting height up to 2.8 mtr and for 5 m diameter coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required. | 10.00 | EA |  | 2500.00 | 5000.00 | 6500.00 | 13000.00 | 3660.00 | 7320.00 | 5000.00 | MANNU LAL AND SONS
427.00 | Supplying,installation,testing and commissioning of Passive Infrared(PIR) technology based occupancy sensor with day light dimming(lighting level shall be regulated as per availability of natural day light in an area along with occupancy detection.) having high preformance, regulating programmable type, suitable for connected load upto 10Amp , for mounting height up to 2.8 mtr and for 5 m diameter coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required. | 30.00 | EA |  | 2400.00 | 24000.00 | 1100.00 | 11000.00 | 2395.00 | 23950.00 | 11000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
428.00 | DISTRIBUTION BOARD
429.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board (IP Rating - IP52), 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
430.00 | 6 way , Double door | 2.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
431.00 | 8 way , Double door | 11.00 | EA |  | 5598.00 | 11196.00 | 2500.00 | 5000.00 | 1745.00 | 3490.00 | 3490.00 | Innovations Workspace Solutions Pvt. Ltd.
432.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painte including earthing etc. as required. (But without MCB/RCCB/Isolator
433.00 | 6 way (4 + 18), Double door | 3.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
434.00 | 8 way (4 + 18), Double door | 4.00 | EA |  | 4320.00 | 12960.00 | 5100.00 | 15300.00 | 4095.00 | 12285.00 | 12285.00 | Innovations Workspace Solutions Pvt. Ltd.
435.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs ( but without MCBs and incomer )as required . (Note : Vertical type MCB TPDB is normally used 8 way (4 + 24), Double door | 1.00 | EA |  | 5060.00 | 20240.00 | 6300.00 | 25200.00 | 4845.00 | 19380.00 | 19380.00 | Innovations Workspace Solutions Pvt. Ltd.
436.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
437.00 | Single pole and neutral | 760.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
438.00 | Triple pole and neutral | 20.00 | EA |  | 535.00 | 406600.00 | 265.00 | 201400.00 | 225.00 | 171000.00 | 171000.00 | Innovations Workspace Solutions Pvt. Ltd.
439.00 | Supplying and fixing following rating, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required 63 A | 9.00 | EA |  | 1097.00 | 21940.00 | 1405.00 | 28100.00 | 2015.00 | 40300.00 | 21940.00 | MANNU LAL AND SONS
440.00 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 25A | 9.00 | EA |  | 923.00 | 8307.00 | 1200.00 | 10800.00 | 1110.00 | 9990.00 | 8307.00 | MANNU LAL AND SONS
441.00 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
442.00 | 25A | 14.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
443.00 | 63A | 8.00 | EA |  | 2309.00 | 32326.00 | 2812.00 | 39368.00 | 3100.00 | 43400.00 | 32326.00 | MANNU LAL AND SONS
444.00 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | 2.00 | EA |  | 2565.00 | 20520.00 | 3300.00 | 26400.00 | 3415.00 | 27320.00 | 20520.00 | MANNU LAL AND SONS
445.00 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A 415 V "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | 5.00 | EA |  | 1044.00 | 2088.00 | 1250.00 | 2500.00 | 865.00 | 1730.00 | 1730.00 | Innovations Workspace Solutions Pvt. Ltd.
446.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 12 way tpn DB -double door | 14.00 | EA |  | 1422.00 | 7110.00 | 1700.00 | 8500.00 | 865.00 | 4325.00 | 4325.00 | Innovations Workspace Solutions Pvt. Ltd.
447.00 | TRAY, RACEWAYS
448.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
449.00 | 300 mm width X 50 mm depth X 1.6 mm thickness | 65.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
450.00 | 450 mm width X 50 mm depth X 2.0 mm thickness | 32.00 | M |  | 876.00 | 56940.00 | 1050.00 | 68250.00 | 2235.00 | 145275.00 | 56940.00 | MANNU LAL AND SONS
451.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
452.00 | 300 mm width X 50 mm depth X 1.6 mm thickness | 10.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
453.00 | 450 mm width X 50 mm depth X 2.0 mm thickness | 4.00 | EA |  | 1995.00 | 19950.00 | 2000.00 | 20000.00 | 3910.00 | 39100.00 | 19950.00 | MANNU LAL AND SONS
454.00 | Supplyinging, installation, testing & commissioning of GI openable top cover raceway made from 2mm thick pre-galvanized sheets for top, bottom and sides and complete with 2mm thick top cover complete with rubber gasketing. The junction box shall be suitable to accommodate GI raceways specified below. Necessary civil work to support/ clamp from RCC slab/floor need to be included here too.(Junction Box price not included in the item).
455.00 | 300 mm wide x40 mm deep | 30.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
456.00 | 200 mm wide x40 mm deep | 150.00 | M |  | 1460.00 | 43800.00 | 1560.00 | 46800.00 | 4010.00 | 120300.00 | 43800.00 | MANNU LAL AND SONS
457.00 | 150 mm wide x40 mm deep | 70.00 | M |  | 1100.00 | 165000.00 | 1050.00 | 157500.00 | 3050.00 | 457500.00 | 157500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
458.00 | 100 mm wide x40 mm deep | 60.00 | M |  | 880.00 | 61600.00 | 780.00 | 54600.00 | 2370.00 | 165900.00 | 54600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
459.00 | 50 mm wide x40 mm deep | 50.00 | M |  | 680.00 | 40800.00 | 550.00 | 33000.00 | 1790.00 | 107400.00 | 33000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
460.00 | Supplyinging, installation, testing & commissioning of floor/ceiling recessed junction boxes for GI raceway systems fabricated from 3 mm MS sheets finished with pre-galvanized sheets, including 2 nos. GI strip at side for earthing, with 1, 2 or 3 nos "+", "I", ''L' shaped support in the centre in case required with 3 mm thick neoprene gasketted removable cover fixed by counter sunk cadmium plated screws including the cost of earth links at all joints to ensure earth continuity and including the cost of chasing and making good recess in floor etc complete as required and as below. (in ceiling / Floor)(With Stainless Steel Top Cover Plates .) Thickness 2 mm
461.00 | 350X50mm | 3.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
462.00 | 250X50mm | 8.00 | EA |  | 2530.00 | 7590.00 | 890.00 | 2670.00 | 5300.00 | 15900.00 | 2670.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
463.00 | 200X50mm | 2.00 | EA |  | 1390.00 | 11120.00 | 750.00 | 6000.00 | 3630.00 | 29040.00 | 6000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
464.00 | 150X50mm | 6.00 | EA |  | 930.00 | 1860.00 | 650.00 | 1300.00 | 2890.00 | 5780.00 | 1300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
465.00 | 100X50mm | 4.00 | EA |  | 560.00 | 3360.00 | 400.00 | 2400.00 | 2205.00 | 13230.00 | 2400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
466.00 | CABLE WORKS
467.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required Upto 35 sq. mm (clamped with 1mm thick saddle
468.00 | 4CX 16SQMM | 280.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
469.00 | 4CX10SQMM | 200.00 | M |  | 25.00 | 7000.00 | 52.00 | 14560.00 | 75.00 | 21000.00 | 7000.00 | MANNU LAL AND SONS
470.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
471.00 | 4CX10SQMM | 10.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
472.00 | 4CX 16SQMM | 8.00 | EA |  | 350.00 | 3500.00 | 280.00 | 2800.00 | 680.00 | 6800.00 | 2800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
473.00 | Supply of PVC insulated and PVC sheathed PVC/ XLPE insulated Aluminum/copper conductor power multicore armoured cable of 1.1 KV grade
474.00 | 4CORE X 16 SQMM | 145.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
475.00 | 4CORE X 10 SQMM | 110.00 | M |  | 360.00 | 52200.00 | 298.00 | 43210.00 | 175.00 | 25375.00 | 25375.00 | Innovations Workspace Solutions Pvt. Ltd.
476.00 | 4CORE X 25 SQMM | 25.00 | M |  | 595.00 | 65450.00 | 255.00 | 28050.00 | 145.00 | 15950.00 | 15950.00 | Innovations Workspace Solutions Pvt. Ltd.
477.00 | 4CORE X 6 SQMM | 40.00 | M |  | 1335.00 | 33375.00 | 373.00 | 9325.00 | 215.00 | 5375.00 | 5375.00 | Innovations Workspace Solutions Pvt. Ltd.
478.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
479.00 | 3½ X 185 sq. mm | 10.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
480.00 | 3½ X 240 sq. mm | 20.00 | EA |  | 1250.00 | 12500.00 | 900.00 | 9000.00 | 1935.00 | 19350.00 | 9000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
481.00 | 3½ X 300 sq. mm | 16.00 | EA |  | 1350.00 | 27000.00 | 1150.00 | 23000.00 | 2920.00 | 58400.00 | 23000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
482.00 | 4CX10SQMM | 10.00 | EA |  | 1550.00 | 24800.00 | 1300.00 | 20800.00 | 3435.00 | 54960.00 | 20800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
483.00 | 4CX 16SQMM | 8.00 | EA |  | 350.00 | 3500.00 | 280.00 | 2800.00 | 420.00 | 4200.00 | 2800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
484.00 | 4 X 25 sq. mm | 14.00 | EA |  | 450.00 | 3600.00 | 350.00 | 2800.00 | 545.00 | 4360.00 | 2800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
485.00 | 3½ X 50 sq. mm | 6.00 | EA |  | 650.00 | 9100.00 | 400.00 | 5600.00 | 550.00 | 7700.00 | 5600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
486.00 | 3½ X 70 sq. mm | 8.00 | EA |  | 850.00 | 5100.00 | 550.00 | 3300.00 | 980.00 | 5880.00 | 3300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
487.00 | 3½ X 95 sq. mm | 4.00 | EA |  | 950.00 | 7600.00 | 480.00 | 3840.00 | 1190.00 | 9520.00 | 3840.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
488.00 | 3½ X 120 sq. mm | 10.00 | EA |  | 1050.00 | 4200.00 | 610.00 | 2440.00 | 1420.00 | 5680.00 | 2440.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
489.00 | 3½ X 150 sq. mm | 6.00 | EA |  | 1150.00 | 11500.00 | 700.00 | 7000.00 | 1675.00 | 16750.00 | 7000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
490.00 | 2 X 6 sq. mm | 12.00 | EA |  | 1225.00 | 7350.00 | 900.00 | 5400.00 | 1675.00 | 10050.00 | 5400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
491.00 | 2 X 10 sq. mm | 2.00 | EA |  | 250.00 | 3000.00 | 250.00 | 3000.00 | 420.00 | 5040.00 | 3000.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
492.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
493.00 | Upto 35 sq. mm | 200.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
494.00 | Above 35 sq. mm and upto 95 sq. mm | 20.00 | M |  | 387.00 | 77400.00 | 400.00 | 80000.00 | 305.00 | 61000.00 | 61000.00 | Innovations Workspace Solutions Pvt. Ltd.
495.00 | Above 95 sq. mm and upto 185 sq. mm | 24.00 | M |  | 405.00 | 8100.00 | 420.00 | 8400.00 | 625.00 | 12500.00 | 8100.00 | MANNU LAL AND SONS
496.00 | Above 185 sq. mm and upto 400 sq. mm | 28.00 | M |  | 422.00 | 10128.00 | 450.00 | 10800.00 | 780.00 | 18720.00 | 10128.00 | MANNU LAL AND SONS
497.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
498.00 | Upto 35 sq. mm | 500.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
499.00 | Above 35 sq. mm and upto 95 sq. mm | 250.00 | M |  | 37.00 | 18500.00 | 42.00 | 21000.00 | 45.00 | 22500.00 | 18500.00 | MANNU LAL AND SONS
500.00 | Above 95 sq. mm and upto 185 sq. mm | 500.00 | M |  | 57.00 | 14250.00 | 62.00 | 15500.00 | 110.00 | 27500.00 | 14250.00 | MANNU LAL AND SONS
501.00 | Above 185 sq. mm and upto 400 sq. mm | 120.00 | M |  | 77.00 | 38500.00 | 82.00 | 41000.00 | 165.00 | 82500.00 | 38500.00 | MANNU LAL AND SONS
502.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
503.00 | Above 35 sq. mm and upto 95 sq. mm | 160.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
504.00 | Above 95 sq. mm and upto 185 sq. mm | 150.00 | M |  | 35.00 | 5600.00 | 52.00 | 8320.00 | 85.00 | 13600.00 | 5600.00 | MANNU LAL AND SONS
505.00 | Above 185 sq. mm and upto 400 sq. mm | 300.00 | M |  | 50.00 | 7500.00 | 71.00 | 10650.00 | 160.00 | 24000.00 | 7500.00 | MANNU LAL AND SONS
506.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
507.00 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 250.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
508.00 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 1600.00 | M |  | 55.00 | 13750.00 | 52.00 | 13000.00 | 45.00 | 11250.00 | 11250.00 | Innovations Workspace Solutions Pvt. Ltd.
509.00 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 200.00 | M |  | 110.00 | 176000.00 | 98.00 | 156800.00 | 180.00 | 288000.00 | 156800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
510.00 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 250.00 | M |  | 153.00 | 30600.00 | 125.00 | 25000.00 | 240.00 | 48000.00 | 25000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
511.00 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 20.00 | EA |  | 226.00 | 56500.00 | 198.00 | 49500.00 | 420.00 | 105000.00 | 49500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
512.00 | Laying of one number XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required. Above 120 sq. mm and upto 400 sq. mm | 15.00 | M |  | 454.00 | 9080.00 | 700.00 | 14000.00 | 510.00 | 10200.00 | 9080.00 | MANNU LAL AND SONS
513.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
514.00 | 3½ X 185 sq. mm (57mm) | 10.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
515.00 | 3½ X 240 sq. mm (62mm) | 20.00 | EA |  | 1200.00 | 12000.00 | 900.00 | 9000.00 | 2295.00 | 22950.00 | 9000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
516.00 | 3½ X 300 sq. mm (70mm) | 15.00 | EA |  | 1300.00 | 26000.00 | 1150.00 | 23000.00 | 2545.00 | 50900.00 | 23000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
517.00 | 4 X 10 sq. mm (25mm) | 10.00 | EA |  | 1500.00 | 22500.00 | 1200.00 | 18000.00 | 8010.00 | 120150.00 | 18000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
518.00 | 4 X 16 sq. mm (28mm) | 20.00 | EA |  | 300.00 | 3000.00 | 280.00 | 2800.00 | 845.00 | 8450.00 | 2800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
519.00 | 4 X 25 sq. mm (28mm) | 15.00 | EA |  | 400.00 | 8000.00 | 350.00 | 7000.00 | 615.00 | 12300.00 | 7000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
520.00 | 3½ X 50 sq. mm (35mm) | 6.00 | EA |  | 450.00 | 6750.00 | 400.00 | 6000.00 | 1095.00 | 16425.00 | 6000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
521.00 | 3½ X 70 sq. mm (38mm) | 8.00 | EA |  | 650.00 | 3900.00 | 550.00 | 3300.00 | 1860.00 | 11160.00 | 3300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
522.00 | 3½ X 95 sq. mm (45mm) | 4.00 | EA |  | 800.00 | 6400.00 | 480.00 | 3840.00 | 1295.00 | 10360.00 | 3840.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
523.00 | 3½ X 120 sq. mm (45mm) | 10.00 | EA |  | 900.00 | 3600.00 | 610.00 | 2440.00 | 1525.00 | 6100.00 | 2440.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
524.00 | 3½ X 150 sq. mm (50mm) | 6.00 | EA |  | 950.00 | 9500.00 | 700.00 | 7000.00 | 1805.00 | 18050.00 | 7000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
525.00 | 2 X 6 sq. mm (19mm) | 12.00 | EA |  | 1050.00 | 6300.00 | 900.00 | 5400.00 | 3110.00 | 18660.00 | 5400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
526.00 | 2 X 10 sq. mm (19mm) | 2.00 | EA |  | 250.00 | 3000.00 | 250.00 | 3000.00 | 820.00 | 9840.00 | 3000.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
527.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required. 300 sq. mm | 4.00 | EA |  | 300.00 | 600.00 | 255.00 | 510.00 | 475.00 | 950.00 | 510.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
528.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required. 300 sq. mm | 1.00 | EA |  | 15000.00 | 60000.00 | 17000.00 | 68000.00 | 15225.00 | 60900.00 | 60000.00 | MANNU LAL AND SONS
529.00 | HT Cable - Supplying of following sizes of XLPE aluminium conductor, corss linked polythylene, individual core screwed, flat steel strip armoured, PVC sheathed cable of 11KV grade (earthed) comforming to IS: 7098 (Part 2),with uptodate ammendment complete as required. 3 C x 300 Sq.mm XLPE HT cable (Earthed) | 160.00 | M |  | 20000.00 | 20000.00 | 25000.00 | 25000.00 | 15950.00 | 15950.00 | 15950.00 | Innovations Workspace Solutions Pvt. Ltd.
530.00 | MV Cable - Supply, following sizes of PVC sheathed PVC/XLPE insulated Aluminium conductor/copper conductor power/ multicore control armoured cable of 1.1 KV grade.
531.00 | 3 ½ C - 300 sq mm Aluminium | 300.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
532.00 | 3 ½ C - 240 sq mm Aluminium | 250.00 | M |  | 1500.00 | 450000.00 | 2570.00 | 771000.00 | 2975.00 | 892500.00 | 450000.00 | MANNU LAL AND SONS
533.00 | 3 ½ C - 185 sq mm Aluminium | 200.00 | M |  | 1300.00 | 325000.00 | 2118.00 | 529500.00 | 1300.00 | 325000.00 | 325000.00 | Innovations Workspace Solutions Pvt. Ltd., MANNU LAL AND SONS
534.00 | 3 ½ C - 150 sq mm Aluminium | 50.00 | M |  | 1200.00 | 240000.00 | 1672.00 | 334400.00 | 1650.00 | 330000.00 | 240000.00 | MANNU LAL AND SONS
535.00 | 3 ½ C - 120 sq mm Aluminium | 60.00 | M |  | 1100.00 | 55000.00 | 1378.00 | 68900.00 | 1635.00 | 81750.00 | 55000.00 | MANNU LAL AND SONS
536.00 | 3 ½ C - 95 sq mm Aluminium | 100.00 | M |  | 950.00 | 57000.00 | 1146.00 | 68760.00 | 815.00 | 48900.00 | 48900.00 | Innovations Workspace Solutions Pvt. Ltd.
537.00 | 3 C - 70 sq mm Aluminium | 20.00 | M |  | 750.00 | 75000.00 | 1129.00 | 112900.00 | 660.00 | 66000.00 | 66000.00 | Innovations Workspace Solutions Pvt. Ltd.
538.00 | 3 ½ C - 50 sq mm Aluminium | 50.00 | M |  | 500.00 | 10000.00 | 751.00 | 15020.00 | 390.00 | 7800.00 | 7800.00 | Innovations Workspace Solutions Pvt. Ltd.
539.00 | 3 ½ C- 35 sq mm Aluminium | 50.00 | M |  | 395.00 | 19750.00 | 568.00 | 28400.00 | 690.00 | 34500.00 | 19750.00 | MANNU LAL AND SONS
540.00 | 4C- 25 sq mm Aluminium | 20.00 | M |  | 300.00 | 15000.00 | 438.00 | 21900.00 | 310.00 | 15500.00 | 15000.00 | MANNU LAL AND SONS
541.00 | 4C- 16 sq mm Aluminium | 160.00 | M |  | 295.00 | 5900.00 | 383.00 | 7660.00 | 435.00 | 8700.00 | 5900.00 | MANNU LAL AND SONS
542.00 | 4C- 10 sq mm Aluminium | 120.00 | M |  | 200.00 | 32000.00 | 298.00 | 47680.00 | 210.00 | 33600.00 | 32000.00 | MANNU LAL AND SONS
543.00 | 4C- 6 sq mm Aluminium | 40.00 | M |  | 195.00 | 23400.00 | 255.00 | 30600.00 | 310.00 | 37200.00 | 23400.00 | MANNU LAL AND SONS
544.00 | 3C- 6 sq mm Aluminium | 40.00 | M |  | 112.00 | 4480.00 | 239.00 | 9560.00 | 150.00 | 6000.00 | 4480.00 | MANNU LAL AND SONS
545.00 | 3C- 10 sq mm Aluminium | 30.00 | M |  | 125.00 | 5000.00 | 189.00 | 7560.00 | 130.00 | 5200.00 | 5000.00 | MANNU LAL AND SONS
546.00 | 2C- 6 sq mm Aluminium | 60.00 | M |  | 165.00 | 4950.00 | 210.00 | 6300.00 | 155.00 | 4650.00 | 4650.00 | Innovations Workspace Solutions Pvt. Ltd.
547.00 | 1C-70 sq mm CU | 500.00 | M |  | 800.00 | 48000.00 | 140.00 | 8400.00 | 200.00 | 12000.00 | 8400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
548.00 | Supply, installation, testing & commissioning of all materials and making terminations of control cable terminations for control cables as per item 7.6 above complete with single brass compression glands, copper lugs etc. as required:
549.00 | 4 C x 2.5 sq.mm control cable | 15.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
550.00 | 12 C x 2.5 sq.mm control cable | 30.00 | NUM |  | 250.00 | 3750.00 | 250.00 | 3750.00 | 365.00 | 5475.00 | 3750.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
551.00 | EARTHING
552.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 12.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
553.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 16.00 | EA |  | 6500.00 | 78000.00 | 6500.00 | 78000.00 | 2500.00 | 30000.00 | 30000.00 | Innovations Workspace Solutions Pvt. Ltd.
554.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | EA |  | 8500.00 | 136000.00 | 11000.00 | 176000.00 | 12310.00 | 196960.00 | 136000.00 | MANNU LAL AND SONS
555.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 100.00 | M |  | 14500.00 | 145000.00 | 16000.00 | 160000.00 | 22680.00 | 226800.00 | 145000.00 | MANNU LAL AND SONS
556.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 125.00 | M |  | 35.00 | 3500.00 | 65.00 | 6500.00 | 30.00 | 3000.00 | 3000.00 | Innovations Workspace Solutions Pvt. Ltd.
557.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 150.00 | M |  | 1240.00 | 155000.00 | 1250.00 | 156250.00 | 150.00 | 18750.00 | 18750.00 | Innovations Workspace Solutions Pvt. Ltd.
558.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe FRLSom earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | M |  | 165.00 | 24750.00 | 200.00 | 30000.00 | 465.00 | 69750.00 | 24750.00 | MANNU LAL AND SONS
559.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | M |  | 1600.00 | 160000.00 | 1700.00 | 170000.00 | 250.00 | 25000.00 | 25000.00 | Innovations Workspace Solutions Pvt. Ltd.
560.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 50.00 | M |  | 600.00 | 60000.00 | 900.00 | 90000.00 | 150.00 | 15000.00 | 15000.00 | Innovations Workspace Solutions Pvt. Ltd.
561.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | M |  | 250.00 | 12500.00 | 370.00 | 18500.00 | 35.00 | 1750.00 | 1750.00 | Innovations Workspace Solutions Pvt. Ltd.
562.00 | Supplying & laying of 25x5 mm size G.I. strips drawn on surface from earth electrode to Electrical switch gears, machineries etc complete with supply of G.I. nuts & bolts, screws etc including riveting, soldering & making necessary connection as approved, specified and directed by the deptt. | 20.00 | M |  | 1240.00 | 24800.00 | 1400.00 | 28000.00 | 1170.00 | 23400.00 | 23400.00 | Innovations Workspace Solutions Pvt. Ltd.
563.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 80.00 | M |  | 165.00 | 3300.00 | 390.00 | 7800.00 | 575.00 | 11500.00 | 3300.00 | MANNU LAL AND SONS
564.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 300.00 | M |  | 165.00 | 13200.00 | 290.00 | 23200.00 | 465.00 | 37200.00 | 13200.00 | MANNU LAL AND SONS
565.00 | LIGHTNING PROTECTION SYSTEM
566.00 | Providing and fixing of lightning conductor finial, made of 25mm dia 300mm long, copper tube, having single prong at top, with 85mm dia 6 mm thick copper base plate including holes etc. complete as required. | 20.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
567.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 65.00 | EA |  | 463.00 | 9260.00 | 715.00 | 14300.00 | 5800.00 | 116000.00 | 9260.00 | MANNU LAL AND SONS
568.00 | Providing and fixing GI tape 20mm x 3mm thick on parapet or surface of wall for lightning conductor as required. (for horizontal run). | 320.00 | M |  | 101.00 | 6565.00 | 250.00 | 16250.00 | 280.00 | 18200.00 | 6565.00 | MANNU LAL AND SONS
569.00 | Providing and fixing G.I. tape 20mm x 3mm thick on parapet or surface of wall for lightning conductor as required. (For vertical run.) | 300.00 | M |  | 113.00 | 36160.00 | 210.00 | 67200.00 | 420.00 | 134400.00 | 36160.00 | MANNU LAL AND SONS
570.00 | Providing and fixing testing joint, made of 20mm x 3mm thick G.I. strip, 125mm long with 4 Nos. of G.I. bolts, nuts, check nuts and spring washers etc. complete as required. | 28.00 | EA |  | 176.00 | 52800.00 | 360.00 | 108000.00 | 420.00 | 126000.00 | 52800.00 | MANNU LAL AND SONS
571.00 | Providing and laying G.I. tape, 32mm x 6mm thick, from earth electrode directly in ground as required. | 75.00 | M |  | 108.00 | 3024.00 | 190.00 | 5320.00 | 605.00 | 16940.00 | 3024.00 | MANNU LAL AND SONS
572.00 | Earthing with G.I. earth pipe 4.5 metre long, 40mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement etc. with charcoal or coke and salt complete as required. | 20.00 | SET |  | 174.00 | 13050.00 | 230.00 | 17250.00 | 335.00 | 25125.00 | 13050.00 | MANNU LAL AND SONS
573.00 | LT PANELS
574.00 | DETAILED TECHNICAL SPECIFICATIONS:
575.00 | The panel will be of low tension, Indoor type, floor mounting, dust and vermin proof with IP42 protection
576.00 | and bus bar of Electro grade Aluminium suitable for 3 phase 4 wire supply. The panel will be designed for
577.00 | front access and cable entry from bottom . Bus bars will be insulated with heat shrinkable PVC colour code sleeves.
578.00 | The panel is made out of 2.0/1.6 mm thk. CRCA sheets, PRE-TREATED and POWDER COATED-
579.00 | with Siemens gray.
580.00 | TESTING :
581.00 | The following tests shall be carried out in presence of your representative at our site.
582.00 | Operational and functional tests
583.00 | Insulation test using 1KV megger
584.00 | H.V. test of 2.5 K.V. for one minute
585.00 | Load test up to rated current with loading transformer
586.00 | COMMON NOTES:-
587.00 | All Control wiring would be 2.5Sq. m.m. copper wires
588.00 | Busbar will be provided with heat shrinkable colour code PVC sleeve.
589.00 | All meters will be of size 96 x 96 mm.
590.00 | Each Compartment will be labelled with aluminium anodised engraved labels as per specifications.
591.00 | MAIN LT PANEL | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
592.00 | INCOMING FROM 1000KVA TRF
593.00 | 1600A 4P 50KA EDO ACB with Microprocessor base O/L, S/C & E/F Protection Release with Communication Port-1
594.00 | ACB Under Voltage Release 220VAC-1
595.00 | 6A SP 10KA MCB-6
596.00 | 6A DP 10KA MCB-2
597.00 | Auxilairy Contactor (4NO+4NC)-5
598.00 | Digital Multifunction Meter with Rs485 Port-1
599.00 | Digital Amp Meter With Selector Switch -1
600.00 | Digital Volt Meter With Selector Switch -1
601.00 | Under Voltage Relay-1
602.00 | Over Voltage Relay-1
603.00 | Master Trip Relay-1
604.00 | Trip Circuit Supervison Relay-1
605.00 | Ristricated Earth Fault Relay-1
606.00 | Breaker Control Switch-1
607.00 | Auto Manual selector switch-1
608.00 | R, Y, B Phase Indicating Lamps-3
609.00 | ON/OFF/Trip Indicating Lamps-3
610.00 | CT's 1600/5A class-1 15VA Cast Resin-3
611.00 | CT's 1600/5A class-1 15VA Cast Resin for CAPACITOR PANEL-1
612.00 | CT's 1600/5A class -PS 15VA -1
613.00 | INCOMING FROM 50KW SOLAR-
614.00 | 125A 4P 50KA MCCB with Microprocessor base Base O/L, S/C & E/F Protection Release-1
615.00 | Extended Rotatory Handle, Spreaders & Auxilary Block-1
616.00 | 125A 4P 4P Power Contactor-1
617.00 | Auxilairy Contactor (4NO+4NC)-5
618.00 | 6A SP 10KA MCB-4
619.00 | R, Y, B Phase Indicating Lamps-3
620.00 | ON/OFF/Trip Indicating Lamps-3
621.00 | Digital Multifunction Meter with RS485 Port-1
622.00 | CT's 150/5A class-1 15VA Cast Resin-3
623.00 | INCOMING FROM 380KVA DG X 1-
624.00 | 800A 4P 50KA EDO ACB with Microprocessor base O/L, S/C & E/F Protection Releasse with Communication Port-1
625.00 | ACB Under Voltage Release 220VAC-1
626.00 | 6A SP 10KA MCB-6
627.00 | 6A DP 10KA MCB-2
628.00 | 16A DP 10KA MCB-1
629.00 | Auxilairy Contactor (4NO+4NC)-5
630.00 | Digital Multifunction Meter with Rs485 Port-1
631.00 | Digital Amp Meter With Selector Switch -1
632.00 | Digital Volt Meter With Selector Switch -1
633.00 | Under Voltage Relay-1
634.00 | Over Voltage Relay-1
635.00 | Reverse Power Relay -1
636.00 | Master Trip Relay-1
637.00 | Trip Circuit Supervison Relay-1
638.00 | Breaker Control Switch-1
639.00 | Auto Manual selector switch-1
640.00 | R, Y, B Phase Indicating Lamps-3
641.00 | ON/OFF/Trip Indicating Lamps-3
642.00 | Start/ Stop Push Button-2
643.00 | Emergency Stop Push Button with Key-1
644.00 | CT's 800/5A class-1 15VA Cast Resin-3
645.00 | CT's 800/5A class-5P10 15VA Cast Resin-3
646.00 | Auxiliary Relay 24VDC-4
647.00 | 0-30A DC Amp Meter-1
648.00 | 0-30V DC Amp Meter-1
649.00 | 16A 24VDC battery Charger-1
650.00 | INCOMING FROM 160KVA DG SET-2-
651.00 | 400A 4P 50KA MCCB with Microprocessor base Base O/L, S/C & E/F Protection Release-1
652.00 | Extended Rotatory Handle, Spreaders & Auxilary Block-1
653.00 | 400A 4P 4P Power Contactor-1
654.00 | Auxilairy Contactor (4NO+4NC)-5
655.00 | 6A SP 10KA MCB-6
656.00 | 6A DP 10KA MCB-2
657.00 | 16A DP 10KA MCB-1
658.00 | Auxilairy Contactor (4NO+4NC)-5
659.00 | Digital Multifunction Meter with Rs485 Port-1
660.00 | Digital Amp Meter With Selector Switch -1
661.00 | Digital Volt Meter With Selector Switch -1
662.00 | Under Voltage Relay-1
663.00 | Over Voltage Relay-1
664.00 | Reverse Power Relay -1
665.00 | Master Trip Relay-1
666.00 | Trip Circuit Supervison Relay-1
667.00 | Auto Manual selector switch-1
668.00 | R, Y, B Phase Indicating Lamps-3
669.00 | ON/OFF/Trip Indicating Lamps-3
670.00 | Start/ Stop Push Button-4
671.00 | Emergency Stop Push Button with Key-1
672.00 | CT's 400/5A class-1 15VA Cast Resin-3
673.00 | CT's 400/5A class-5P10 15VA Cast Resin-3
674.00 | Auxiliary Relay 24VDC-4
675.00 | 0-30A DC Amp Meter-1
676.00 | 0-30V DC Amp Meter-1
677.00 | 16A 24VDC battery Charger-1
678.00 | BUS COUPLER-
679.00 | 1000A 4P 50KA EDO ACB without Protection Releasse -1
680.00 | ACB Under Voltage Release 220VAC-1
681.00 | 6A SP 10KA MCB-6
682.00 | 6A DP 10KA MCB-2
683.00 | Auxilairy Contactor (4NO+4NC)-5
684.00 | Breaker Control Switch-1
685.00 | Auto Manual selector -1
686.00 | ON/OFF Indicating Lamps-2
687.00 | PLC INTERLOCKING & D.G. AMF-
688.00 | PLC with IOS -1
689.00 | PLC Power Supply 220VAC/24VDC 10A-2
690.00 | Power Pack -1
691.00 | 1KVA Online UPS-1
692.00 | DC Auxilairy Realy Card -4
693.00 | DC Auxilairy Contactor 24VDC-30
694.00 | PLC Auto /Manual Selector Switch-1
695.00 | PLC Fault Indicating Lamps-1
696.00 | PLC Reset Push Button-1
697.00 | 6A Piano Type Switch Socket-2
698.00 | Inspection Lamps with Door Switch-2
699.00 | BUS BAR-
700.00 | 2000A/1000A TPN 415V 50Hz ALUMINIUM BUS BAR-
701.00 | OUTGOING SECTION-1-
702.00 | 800A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-1
703.00 | Extended Rotatory Handle, Spreaders -1
704.00 | 6A SP 10KA MCB-4
705.00 | Digital Multifunction Meter with RS485 Port-1
706.00 | R, Y, B Phase Indicating Lamps-3
707.00 | CT's 800/5A class-1 15VA Cast Resin-3
708.00 | 630A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-1
709.00 | Extended Rotatory Handle, Spreaders -1
710.00 | 6A SP 10KA MCB-4
711.00 | Digital Multifunction Meter with RS485 Port-1
712.00 | R, Y, B Phase Indicating Lamps-3
713.00 | CT's 600/5A class-1 15VA Cast Resin-3
714.00 | 250A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-2
715.00 | Extended Rotatory Handle, Spreaders-2
716.00 | 6A SP 10KA MCB-8
717.00 | Digital Multifunction Meter with RS485 Port-2
718.00 | R, Y, B Phase Indicating Lamps-6
719.00 | CT's 250/5A class-1 10VA Cast Resin-6
720.00 | 125A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-7
721.00 | Extended Rotatory Handle, Spreaders -7
722.00 | 6A SP 10KA MCB-28
723.00 | Digital Multifunction Meter with RS485 Port-7
724.00 | R, Y, B Phase Indicating Lamps-21
725.00 | CT's 150/5A class-1 10VA Cast Resin-21
726.00 | 63A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-1
727.00 | Extended Rotatory Handle, Spreaders-1
728.00 | 6A SP 10KA MCB-4
729.00 | Digital Multifunction Meter with RS485 Port-1
730.00 | R, Y, B Phase Indicating Lamps-3
731.00 | CT's 150/5A class-1 10VA Cast Resin-3
732.00 | OUTGOING SECTION-2-
733.00 | 630A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-1
734.00 | Extended Rotatory Handle, Spreaders -1
735.00 | 6A SP 10KA MCB-4
736.00 | Digital Multifunction Meter with RS485 Port-1
737.00 | R, Y, B Phase Indicating Lamps-3
738.00 | CT's 600/5A class-1 15VA Cast Resin-3
739.00 | 250A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-3
740.00 | Extended Rotatory Handle, Spreaders -3
741.00 | 6A SP 10KA MCB-12
742.00 | Digital Multifunction Meter with RS485 Port-3
743.00 | R, Y, B Phase Indicating Lamps-9
744.00 | CT's 250/5A class-1 10VA Cast Resin-9
745.00 | 200A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-2
746.00 | Extended Rotatory Handle, Spreaders -2
747.00 | 6A SP 10KA MCB-8
748.00 | Digital Multifunction Meter with RS485 Port-2
749.00 | R, Y, B Phase Indicating Lamps-6
750.00 | CT's 200/5A class-1 10VA Cast Resin-6
751.00 | 125A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-3
752.00 | Extended Rotatory Handle, Spreaders -3
753.00 | 6A SP 10KA MCB-12
754.00 | Digital Multifunction Meter with RS485 Port-3
755.00 | R, Y, B Phase Indicating Lamps-9
756.00 | CT's 150/5A class-1 10VA Cast Resin-9
757.00 | 100A TPN 36KA MCCB with Thermal Magnetic Base O/L, S/C Protection Release-1
758.00 | Extended Rotatory Handle, Spreaders -1
759.00 | 6A SP 10KA MCB-4
760.00 | Digital Multifunction Meter with RS485 Port-1
761.00 | R, Y, B Phase Indicating Lamps-3
762.00 | CT's 100/5A class-1 5VA Cast Resin-3
763.00 | Inspection Lamps with Door Switch-8
764.00 | Space Heater with Thermostate-8
765.00 | 330 KVAR APFC PANEL | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
766.00 | INCOMER
767.00 | 800A TPN 50KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
768.00 | Extended Rotatory Handle, Spreaders-1
769.00 | 6A SP 10KA MCB -4
770.00 | Digital VAF Meter -1
771.00 | Auxiliary Contactor with 4NO+4NC-5
772.00 | APFC Relay 12-Stage-1
773.00 | Auto /Manual Selector Switch-1
774.00 | R,Y,B Phase Indicating Lamps-3
775.00 | CT's 600/5A class-1 15VA Cast Resin-3
776.00 | Axial Fan with Filter-6
777.00 | BUS BAR-
778.00 | 700A TPN ALUMINIUM BUS BAR-
779.00 | OUTGOING-
780.00 | 50KVAR Capacitor Bank × 3-
781.00 | 125A 3P 36KA MCCB with Thermal Magnetic Trip-3
782.00 | Spreaders-3
783.00 | 50KVAR Switching Thyristor-3
784.00 | 50KVAR 7% Detuned Reactor-3
785.00 | 50KVAR MPP Type 480V Heavy Duty Capacitor -3
786.00 | Auxilary Relay 12VDC-3
787.00 | ON/OFF Indicating Lamps-6
788.00 | Start/Stop Push Button-6
789.00 | 25KVAR Capacitor Bank × 4-
790.00 | 63A 3P 36KA MCCB with Thermal Magnetic Trip-4
791.00 | 25KVAR Switching Thyristor-4
792.00 | 25KVAR 7% Detuned Reactor-4
793.00 | 25KVAR MPP Type 480V Heavy Duty Capacitor -4
794.00 | Auxilary Relay 12VDC-4
795.00 | ON/OFF Indicating Lamps-8
796.00 | Start/Stop Push Button-8
797.00 | 15KVAR Capacitor Bank × 4-
798.00 | 40A 3P 36KA MCCB with Thermal Magnetic Trip-2
799.00 | 15KVAR Switching Thyristor-2
800.00 | 15KVAR 7% Detuned Reactor-2
801.00 | 15KVAR MPP Type 480V Heavy Duty Capacitor -2
802.00 | Auxilary Relay 12VDC-2
803.00 | ON/OFF Indicating Lamps-4
804.00 | Start/Stop Push Button-4
805.00 | 10KVAR Capacitor Bank × 1-
806.00 | 32A 3P 36KA MCCB with Thermal Magnetic Trip-1
807.00 | 10KVAR Switching Thyristor-1
808.00 | 10KVAR 7% Detuned Reactor-1
809.00 | 10KVAR MPP Type 480V Heavy Duty Capacitor -1
810.00 | Auxilary Relay 12VDC-1
811.00 | ON/OFF Indicating Lamps-2
812.00 | Start/Stop Push Button-2
813.00 | 5KVAR Capacitor Bank × 2-
814.00 | 20A 3P 36KA MCCB with Thermal Magnetic Trip-2
815.00 | 5KVAR Switching Thyristor-2
816.00 | 5KVAR 7% Detuned Reactor-2
817.00 | 5KVAR MPP Type 480V Heavy Duty Capacitor -2
818.00 | Auxilary Relay 12VDC-2
819.00 | ON/OFF Indicating Lamps-4
820.00 | Start/Stop Push Button-4
821.00 | MAIN DISTRIBUTION PANEL - GROUND FLOOR | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
822.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
823.00 | Extended Rotatory Handle, Spreaders-1
824.00 | Auxilary & Trip Alarm Contact-1
825.00 | 6A SP 10KA MCB -4
826.00 | Digital Multifunction Meter with Rs485 Port -1
827.00 | R,Y,B Phase Indicating Lamps-3
828.00 | CT's 150/5A class-1 5VA -3
829.00 | BUS BAR-
830.00 | 150A TPN ALUMINIUM BUS BAR-
831.00 | OUTGOING-
832.00 | 63A 4P 10KA MCB-2
833.00 | 32A 4P 10KA MCB-4
834.00 | MAIN DISTRIBUTION PANEL - FIRST FLOOR- | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
835.00 | INCOMER-
836.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
837.00 | Extended Rotatory Handle, Spreaders-1
838.00 | Auxilary & Trip Alarm Contact-1
839.00 | 6A SP 10KA MCB -4
840.00 | Digital Multifunction Meter with Rs485 Port -1
841.00 | R,Y,B Phase Indicating Lamps-3
842.00 | CT's 150/5A class-1 5VA -3
843.00 | BUS BAR-
844.00 | 150A TPN ALUMINIUM BUS BAR-
845.00 | OUTGOING-
846.00 | 63A 4P 10KA MCB-2
847.00 | 32A 4P 10KA MCB-4
848.00 | MAIN DISTRIBUTION PANEL - SECOND FLOOR- | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
849.00 | INCOMER-
850.00 | 250A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
851.00 | Extended Rotatory Handle, Spreaders-1
852.00 | Auxilary & Trip Alarm Contact-1
853.00 | 6A SP 10KA MCB -4
854.00 | Digital Multifunction Meter with Rs485 Port -1
855.00 | R,Y,B Phase Indicating Lamps-3
856.00 | CT's 250/5A class-1 5VA -3
857.00 | BUS BAR-
858.00 | 300A TPN ALUMINIUM BUS BAR-
859.00 | OUTGOING-
860.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-2
861.00 | Extended Rotatory Handle, Spreaders-2
862.00 | 63A 4P 10KA MCB-2
863.00 | 32A 4P 10KA MCB-4
864.00 | MAIN DISTRIBUTION PANEL - THIRD FLOOR- | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
865.00 | INCOMER-
866.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
867.00 | Extended Rotatory Handle, Spreaders-1
868.00 | Auxilary & Trip Alarm Contact-1
869.00 | 6A SP 10KA MCB -4
870.00 | Digital Multifunction Meter with Rs485 Port -1
871.00 | R,Y,B Phase Indicating Lamps-3
872.00 | CT's 150/5A class-1 5VA -3
873.00 | BUS BAR-
874.00 | 150A TPN ALUMINIUM BUS BAR-
875.00 | OUTGOING-
876.00 | 63A 4P 10KA MCB-2
877.00 | 32A 4P 10KA MCB-4
878.00 | MAIN DISTRIBUTION PANEL - FOURTH FLOOR- | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
879.00 | INCOMER-
880.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
881.00 | Extended Rotatory Handle, Spreaders-1
882.00 | Auxilary & Trip Alarm Contact-1
883.00 | 6A SP 10KA MCB -4
884.00 | Digital Multifunction Meter with Rs485 Port -1
885.00 | R,Y,B Phase Indicating Lamps-3
886.00 | CT's 150/5A class-1 5VA -3
887.00 | BUS BAR-
888.00 | 150A TPN ALUMINIUM BUS BAR-
889.00 | OUTGOING-
890.00 | 63A 4P 10KA MCB-2
891.00 | 32A 4P 10KA MCB-4
892.00 | MAIN DISTRIBUTION PANEL - FIFTH FLOOR- | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
893.00 | INCOMER-
894.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
895.00 | Extended Rotatory Handle, Spreaders-1
896.00 | Auxilary & Trip Alarm Contact-1
897.00 | 6A SP 10KA MCB -4
898.00 | Digital Multifunction Meter with Rs485 Port -1
899.00 | R,Y,B Phase Indicating Lamps-3
900.00 | CT's 150/5A class-1 5VA -3
901.00 | BUS BAR-
902.00 | 150A TPN ALUMINIUM BUS BAR-
903.00 | OUTGOING-
904.00 | 63A 4P 10KA MCB-2
905.00 | 32A 4P 10KA MCB-4
906.00 | MAIN DISTRIBUTION PANEL - SIXTH FLOOR | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
907.00 | INCOMER
908.00 | 125A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release
909.00 | Extended Rotatory Handle, Spreaders
910.00 | Auxilary & Trip Alarm Contact
911.00 | 6A SP 10KA MCB
912.00 | Digital Multifunction Meter with Rs485 Port
913.00 | R,Y,B Phase Indicating Lamps
914.00 | CT's 150/5A class-1 5VA
915.00 | BUS BAR
916.00 | 150A TPN ALUMINIUM BUS BAR
917.00 | OUTGOING
918.00 | 63A 4P 10KA MCB
919.00 | 32A 4P 10KA MCB
920.00 | UPS INPUT PANEL - | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
921.00 | INCOMER-
922.00 | 250A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-2
923.00 | Extended Rotatory Handle, Spreaders-2
924.00 | Auxilary & Trip Alarm Contact-2
925.00 | 250A 4P Power Contactor for electrial & machenical Interlocking -2
926.00 | 6A SP 10KA MCB -8
927.00 | Digital Multifunction Meter with Rs485 Port -2
928.00 | R,Y,B Phase Indicating Lamps-6
929.00 | CT's 250/5A class-1 10VA -6
930.00 | BUS BAR-
931.00 | 300A TPN ALUMINIUM BUS BAR-
932.00 | OUTGOING-
933.00 | 160A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-2
934.00 | Extended Rotatory Handle, Spreaders-2
935.00 | 6A SP 10KA MCB -3
936.00 | Digital Amp Meter with builtin selector switch-2
937.00 | CT's 200/5A class-1 10VA -6
938.00 | 32A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
939.00 | Extended Rotatory Handle, Spreaders-1
940.00 | 6A SP 10KA MCB -1
941.00 | Digital Amp Meter with builtin selector switch-1
942.00 | CT's 30/5A class-1, 5VA -3
943.00 | UPS OUTPUT PANEL - | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
944.00 | INCOMER-
945.00 | 160A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-
946.00 | Extended Rotatory Handle, Spreaders-
947.00 | Auxilary & Trip Alarm Contact-
948.00 | 160A 4P Power Contactor for electrial & machenical Interlocking -
949.00 | 6A SP 10KA MCB -
950.00 | Digital Multifunction Meter with Rs485 Port -
951.00 | R,Y,B Phase Indicating Lamps-
952.00 | ON/OFF/ Trip Indicating Lamps-
953.00 | Start/ Stop Push Button-
954.00 | Auto manual selector switch-
955.00 | CT's 200/5A class-1 10VA -
956.00 | 160A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-
957.00 | Extended Rotatory Handle, Spreaders-
958.00 | Auxilary & Trip Alarm Contact-
959.00 | 160A 4P Power Contactor for electrial & machenical Interlocking -
960.00 | 6A SP 10KA MCB -
961.00 | 6A DP 10KA MCB -
962.00 | On Delay Timer-
963.00 | ON/OFF Indicating Lamps-
964.00 | Start/ Stop Push Button-
965.00 | Auto manual selector switch-
966.00 | BUS BAR-
967.00 | 300A TPN ALUMINIUM BUS BAR-
968.00 | OUTGOING SECTION-1-
969.00 | 63A 4P 10KA MCB-
970.00 | 40A 4P 10KA MCB-
971.00 | 40A DP 10KA MCB-
972.00 | OUTGOING SECTION-2-
973.00 | 63A 4P 10KA MCB-
974.00 | 40A 4P 10KA MCB-
975.00 | 40A DP 10KA MCB-
976.00 | PRESSURIZATION PANEL - | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
977.00 | INCOMER-
978.00 | 160A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
979.00 | Extended Rotatory Handle, Spreaders-1
980.00 | Auxilary & Trip Alarm Contact-1
981.00 | 6A SP 10KA MCB -4
982.00 | Digital Multifunction Meter with Rs485 Port -1
983.00 | R,Y,B Phase Indicating Lamps-3
984.00 | CT's 200/5A class-1 10VA -3
985.00 | BUS BAR-
986.00 | 200A TPN ALUMINIUM BUS BAR-
987.00 | OUTGOING-
988.00 | 63A TPN 10KA MCB-8
989.00 | 40A TPN 10KA MCB-1
990.00 | 32A TPN 10KA MCB-2
991.00 | SMOKE EXHAUST PANEL - | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
992.00 | INCOMER-
993.00 | 250A 4P ATS-1
994.00 | 250A 4P 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
995.00 | Extended Rotatory Handle, Spreaders-1
996.00 | Auxilary & Trip Alarm Contact-1
997.00 | 6A SP 10KA MCB -8
998.00 | Auxilary Contactor with 2NO+2NC 230VAC-2
999.00 | Digital Multifunction Meter with Rs485 Port -1
1000.00 | On Delay Timer-2
1001.00 | Voltage Monitoring Relay-2
1002.00 | R,Y,B Phase Indicating Lamps-3
1003.00 | CT's 250/5A class-1 10VA -3
1004.00 | BUS BAR-
1005.00 | 300A TPN ALUMINIUM BUS BAR-
1006.00 | OUTGOING-
1007.00 | 160A TPN 25KA MCCB With Thermal Magnetic Base O/L, S/C Protection Release-1
1008.00 | Extended Rotatory Handle, Spreaders-1
1009.00 | 63A TPN 10KA MCB-1
1010.00 | 32A TPN10KA MCB-16
1011.00 | UPS
1012.00 | Supply, installation, testing & commissioning of One Set of 1 Nos., 80 KVA UPS. Each UPS of 80 KVA should have following specifications in addition to tender requirements : (i) True online double conversions, IGBT Rectifier & inverter based UPS. (ii) Three phases Input/ three phase output (Input Line Voltage: 340 - 478 Volt, 3 phase, Output Line Voltage 400 volt, 3 phase) (iii) SMF batteries complete with MS Fabricated battery rack to accomodate the complete battery system. (iv) Suitable for 30 Min backup on Full load at 0.8 Load P.F., with required nos. of Battery with each UPS. (v) Output THD is less than 3% for full linear load & Less than 5 % for nonlinear load. (vi) Crest factor 3:1 (vii) over load 125% for 10 min, 150% for 1 min and should be able to operate continuously at 115% load on bypass mode. (viii) Battery type should be Valve regulated lead-acid (VRLA). | 2.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1013.00 | (ix) Inbuilt Delta - Star Input Isolation Transformer, parallel communication port, RS232, USB, EPO and SNMP interface, BMS interface. (x) Dust Filter at Air Inlet point are required. (xi) UPS should be provided with environment monitoring probe to measure temperature and humidity of UPS room on SNMP card software. (xii) LCD Display indicating all important parameters. (xiii) UPS shall be provided with Temperature and Humidity Sensors to monitor Temperature and Humidity over LAN. (xiv) Battery open rack with top cover, battery interlinks and battery breaker. (xv) Battery to UPS cable as required should be provided with UPS systems. (xvi) UPS system shall be parallelable upto 6 units in case required in future. (xvii) Each UPS shall be compatible for working in parallel redundant mode with other. MAKE-EMERSON, UNILINE, 3EM (Testing will be as per IEC 62040)
1014.00 | Supply, installation, testing & commissioning of One Set of 1 Nos., 5 KVA UPS. Each UPS of 5 KVA should have following specifications in addition to tender requirements : (i) True online double conversions, IGBT Rectifier & inverter based UPS. (ii) Three phases Input/ three phase output (Input Line Voltage: 340 - 478 Volt, 3 phase, Output Line Voltage 400 volt, 3 phase) (iii) SMF batteries complete with MS Fabricated battery rack to accomodate the complete battery system. (iv) Suitable for 30 Min backup on Full load at 0.8 Load P.F., with required nos. of Battery with each UPS. (v) Output THD is less than 3% for full linear load & Less than 5 % for nonlinear load. (vi) Crest factor 3:1 (vii) over load 125% for 10 min, 150% for 1 min and should be able to operate continuously at 115% load on bypass mode. (viii) Battery type should be Valve regulated lead-acid (VRLA). | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1015.00 | (ix) Inbuilt Delta - Star Input Isolation Transformer, parallel communication port, RS232, USB, EPO and SNMP interface, BMS interface. (x) Dust Filter at Air Inlet point are required. (xi) UPS should be provided with environment monitoring probe to measure temperature and humidity of UPS room on SNMP card software. (xii) LCD Display indicating all important parameters. (xiii) UPS shall be provided with Temperature and Humidity Sensors to monitor Temperature and Humidity over LAN. (xiv) Battery open rack with top cover, battery interlinks and battery breaker. (xv) Battery to UPS cable as required should be provided with UPS systems. (xvi) UPS system shall be parallelable upto 6 units in case required in future. (xvii) Each UPS shall be compatible for working in parallel redundant mode with other. MAKE-EMERSON, UNILINE, 3EM (Testing will be as per IEC 62040)
1016.00 | MISCELLANEOUS ITEMS
1017.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 7.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1018.00 | Supply and fixing glass framed shock treatment chart.900mm x 600mm high, printed preferably in three languages i.e. Hindi, English & local language; | 1.00 | EA |  | 450.00 | 3150.00 | 100.00 | 700.00 | 550.00 | 3850.00 | 700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1019.00 | Supplying and fixing of high voltage insulation mat of class B having 1.1 KV dielectric strength, 1000mm width and thickness of 2.0 mm ISI approved as required including cutting to required lengths. | 7.00 | M2 |  | 2500.00 | 2500.00 | 1500.00 | 1500.00 | 2650.00 | 2650.00 | 1500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1020.00 | Supply and installation of DCP type fire extinguisher of capacity 5 kg with upright operation conforming to IS:2171 having a jet length of 8m with discharge time of 10 sec including all accessories. | 7.00 | EA |  | 1500.00 | 10500.00 | 1200.00 | 8400.00 | 1950.00 | 13650.00 | 8400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1021.00 | Standard first aid box - prescribed by St.John Ambulance brigade or India Red Cross shall be provided (First aid box should be of 18 gauge M.S sheet of size 14" x 17" x 5"):- | 2.00 | EA |  | 6800.00 | 47600.00 | 4500.00 | 31500.00 | 2883.05 | 20181.35 | 20181.35 | Innovations Workspace Solutions Pvt. Ltd.
1022.00 | 11 KV, 3 Phase Overhead HT Line work comprising of following:- | 500.00 | M |  | 2500.00 | 5000.00 | 7000.00 | 14000.00 | 5500.00 | 11000.00 | 5000.00 | MANNU LAL AND SONS
1023.00 | A. Supplying & Fixing 11kV Pin / Disc insulators confirming to IS-731 / 1971 & IS 2486 (Part-II)/1989 on existing structure / pole etc. as required along with complete accessories including Cross arms, Top Clamps, Guarding Cross arms, etc. (M/s. JSI / BHEL / HTIF / Punjab Ceramic / W S Ind. / Allied Ceramic / India Potteries / or any reputed make)
1024.00 | B. Supplying and laying of A.C.S.R. weasel conductor confirming to IS-398 (Part-I & II) / 1996 of overall dia. of 7.77mm on the existing pole on insulators including binding, testing, commissioning etc.
1025.00 | C. The 11KV guarding cross arm is to be fitted on the pole( which are already erected, and if any extra pole is to be installed the same shall be apid seperately) as per standard engineering practice for guarding the line with 8 SWG GI wire as guard wire and 10 SWG GI wire for lacing. Guarding cross arm made of 75x40x6 mm angle 5 feet long should be clamped at 300mm below the bottom arm of ‘V’ cross arm.
1026.00 | D. ANTI-CLIMBING DEVICE: Barbed wire weighing 3.5 Kg per pole should be wrapped at a height of 3000 mm above ground level stretching in 900 mm length. Both ends of barbed should be clamped suitably to avoid coming down from its location.
1027.00 | E. DANGER BOARD: Danger Board for 11KV voltage and danger mark conforming to IS:2551-1963 should be fixed on each location.
1028.00 | F. GUYS: The guys shall consist of anchor plate, stay rod with bow and ratchet assembly, thimbles stay wires, stay grips and stay clamps. All iron fittings of stay shall be painted with Red Oxide paint. The minimum size of stay wire shall be 7/4.0 mm with and ultimate breaking strength of 6450 Kg. The stay rod shall be 20 mm dia 2 meters long fitted with bow and ratchets assembly having ultimate tensile strength of 8000 Kg. The anchor plate shall not be less than 300 x 300 x 6 mm size made up of mild steel. Turnbuckles with 20 mm dia. screw shall have ultimate breaking strength of 8000 kg.
1029.00 | Supply,installation,testing and commissioning of Metering cubicle as per local electric authority norms including providing required CT and PT complete as required.dust, damp and vermin proof, cubicle HT. Metering Panel made out of 14 gauge CRCA sheet steel complete with 5 Amp electronic trivector meter, C.T.'s of 20/10/5 Amp, 0.5 Class, 15 VA Burden, and P.T's of 11 KV / √3, 110V / √3, 100 VA conforming to relevant IS Standards and complete as required. H.T. Metering cubicle along with C.T.'s, P.T.'s and trivector meter shall be got tested and approved from local electricity supply authority. The GA drawing shall be got approved from the local statutory authorities before fabrication.Note: The contractor shall ensure that the above panel meets the requirement as insisted by local electricity authorities for satisfactory operation and as per the Drawings | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1030.00 | 250 KVA DG Set Equipment With AMF Panel Providing, Installing, Testing and Commissioning of 250 KVA Continuous rating ‘Silent Type (Prime rating)’ raditor cooled Diesel Generating set along with complete fuel oil piping, antivirbation mounts, base frame, required hardware, Batteries, Engine control panel with accessories, residential silencer, flexible connection, bellow/ expansion joints, etc. complete with all associated equipement/ work as per specifications or requirements as per site having Prime Power Rating, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor and consisting of the followings including making necessary civil foundation etc. complete as required (Factory test or load test as per ISO3046 & ISO8528) | 1.00 | SET |  | 155000.00 | 155000.00 | 700000.00 | 700000.00 | 300000.00 | 300000.00 | 155000.00 | MANNU LAL AND SONS
1031.00 | Diesel Engines:
1032.00 | Diesel engine 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for delivering required output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories.
1033.00 | Engine mounted Instrument Panel fitted with and having digital display for following:
1034.00 | DG set shall be supplied with built in acoustic enclosure as per pollution control board norms and as per specification complete in all respect.
1035.00 | The DG Set shall be complete with PCC (Power Command Control) or equivalent DG Controller module suitable for AMF (auto-mains failure), Auto Load Sharing & Interface with PLC mounted in the LT panel for ACB/MCCB switching and Auto load sensing and Auto load Management, including communication card and networking gateway and software as required.
1036.00 | Note: Item rate shall be include 1st time filling of Lube oil & diesel and also include the cable termination box suitable for termination of 4 Runs 3.5 C X 300 Sqmm. XLPE AL cables at alternator.
1037.00 | Battery charger for 1X250 KVA DG sets
1038.00 | Supply, installation, testing & commissioning of Battery Charger as described in Specifications and described below:
1039.00 | Rating
1040.00 | AC Input: 230 V + 10% AC 50 Hz single phase.
1041.00 | DC Output: To float / boost charge the batteries (with required AH as per D.G. rating) and also supply a continuous load or as per offered DG set requirement.
1042.00 | Current Rating: 30 A
1043.00 | Float Mode: 27.0 V nominal (Adjustable) between 24-28.0 V.
1044.00 | Boost Mode: 29.0 V nominal (Adjustable) between 24-32.0 V
1045.00 | Voltage Regulation:+ 2% for AC input variation of 230 V + 10%. Frequency Variation of 50 Hz + 5% and DC load variation 0-100%
1046.00 | Ripple:Less than 5%
1047.00 | Alternator :
1048.00 | Synchronous alternator rated at 250KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class-F/H insulation.
1049.00 | Base Frame & Foundation:
1050.00 | Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer.
1051.00 | Fuel Tank:
1052.00 | Daily service fuel tank of 990 liters capacity respectively fabricated out of 2 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class ‘C’ pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications.
1053.00 | Oil Piping
1054.00 | Supply, installation, testing & commissioning of the following MS class ‘C’ pipes cut to required lengths and installed with all welded joints. Providing the necessary fittings like elbows, tees and reducers, sockets, hot dip galvanized supports and accessories including ceiling Hanger, Hardware complete as per site requirement.
1055.00 | 25 mm dia MS pipes of required length as directed by Engineer-In-Charge
1056.00 | 25 mm dia. ball valves of required numbers as directed by Engineer-In-Charge
1057.00 | Exhaust System:
1058.00 | Dry exhaust manifold with hospital exhaust silencer and catalytic convertor.
1059.00 | Starting System:
1060.00 | 24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries (180 AH capacity lead acid type) as required as per specifications.
1061.00 | Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications, For in house power Generation for Emergency loads suitable for 250KVA
1062.00 | Supplying and fixing Exhaust gas piping of 1x100 dia. welded black MS, B Class pipe conforming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, insulation of exhaust system with mineral wool/ Rockwool, 50 mm thick wire mesh & aluminum cladding etc., as required as per specifications. The height will be goverened by existing structures nearby and as per norms and bye-laws (if any) and/or as per design requirement as per the decision of Engineer-In-Charge. Cost of framing and all supports complete in all respect is included. | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1063.00 | Supply, installation, testing & commissioning of MS class-C exhaust pipe as per IS 1239 and all fixing accessories and hardwares. The exhaust pipes shall be insulated with 75 mm thick mineral wool (density 150 kg/m3) insulation wrapped in chicken mesh and clad with 26 gauge aluminium sheet including all hot dip galvanized support structural as required.
1064.00 | 125 mm dia MS class-C pipe & 75mm thick mineral wool insulation as per description given above of required length as directed by Engineer-In-Charge
1065.00 | 100 mm dia MS class-C pipe & 75mm thick mineral wool insulation as per description given above of required length as directed by Engineer-In-Charge
1066.00 | Contractor should furnish calculation for exhaust piping size for approval by the Consultant. The system should meet the performance of the engine without exceeding the back pressure limit prescribed by engine supplier.
1067.00 | Support Structure
1068.00 | Supply, installation, testing & commissioning of miscellaneous structural support (MS angle iron / MS Plates / MS Channel etc.) for horizontal/vertical exhaust piping at suitable interval as per approved Shop drawing including fabrication, hardwares / flanges and painting (2 coats of primer and 2 coats of enamel paint) complete in all respect.
1069.00 | Additional Material Required
1070.00 | Supply, installation, testing & commissioning of 125 mm dia Flexible Bellows of required numbers as directed by Engineer-In-Charge
1071.00 | Supply, installation, testing & commissioning of 100 mm dia Flexible Bellows of required numbers as directed by Engineer-In-Charge
1072.00 | Supply, installation, testing & commissioning of Thermal Cladding of Silencers of required numbers as directed by Engineer-In-Charge
1073.00 | Supply, installation, testing & commissioning of following 1100 volt grade XLPE PVC insulated sheathed copper conductor armoured cable including supplying of bimettalic crimping lugs, double compression glands with earthing. as per specification.
1074.00 | 4 C x 2.5 sq.mm control cable of required length as directed by Engineer-In-Charge
1075.00 | 12 C x 2.5 sq.mm control cable of required length as directed by Engineer-In-Charge
1076.00 | AMF PANEL - Fabricating , supplying, installation, testing and commissioning of Automatic Mains Failure Control (AMF panel) including auto by-pass panel, suitable for 250 KVA, silent type DG set complete with relay, timers, set of CTs for metering & protection and enery analyser to indicate currents, phase and line voltage, frequency, power factor, KWH, KVARH and provision for overload, short circuit, restricted earth fault , under frequency, control cabling from AMF panel to diesel engine and elsewhere if required, all complete and inter locking including the following: | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1077.00 | (a) 1 No. 400 AMP., 4 Pole motorised molded case circuit breaker.
1078.00 | (b) Auto/Manual/Test/Off selector switch
1079.00 | (c ) 2 Nos. over voltage relay, 2 nos.reverse power relay and 2 nos. under voltage relay
1080.00 | (d) 3 Sets of Current Transformer 15P 10 accuracy for protection and 15 VA class-I for metering
1081.00 | (e )Energy analyzer unit to indicate current voltage frequency power factor and KWH
1082.00 | (f) indication lamps for load on mains and load on set
1083.00 | (g) fuse for instruments
1084.00 | (h) Battery charger, complete with transformer/ rectifier, D.C voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment.
1085.00 | (i) Main supply failure monitor
1086.00 | (j) Supply failure timer
1087.00 | (k) Restoration timer
1088.00 | (l) Control unit with three impulse automatic engine start/stop and failure to start lockout.
1089.00 | (m) Impulse counter with locking and reset facility.
1090.00 | (n) ON/OFF/Control circuit switch with indicator
1091.00 | (o) Audio/Video annunciation for
1092.00 | (i) High water temperature (ii) Low lubricating oil pressure (iii) Engine over speed (iv) Engine fails to start (v) Full load/maximum load warning
1093.00 | SOLAR SYSTEM 50KW
1094.00 | Supply, Installation, Testing and Commissioning of ongrid Solar Photovoltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono/Poly Crystalline silicon solar cells, net metering facility, necessary protections, earthing, mounted on Aluminium/GI structure of suitable strength with following components complete as required:- a) Solar Photovoltaic Module of capacity 330 Wp or above, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants/ systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. b) Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. c) Data Monitoring System complete with accessories. d) Fixing of Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. (KWH means KWP here) | 50.00 | KWH |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1095.00 | LV WORK
1096.00 | FIRE AND PUBLIC ADDRESS SYSTEM
1097.00 | FIRE ALARM SYSTEM
1098.00 | Supplying, installation, testing and commissioning of microprocessor based intelligent addressable main fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5% V, 50 hz), 48 hrs back-up with 24 volt sealedmaintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol BACnet/ Modbus over IP complete as per specifications. 8 loop | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1099.00 | Supply,installation testing and commissioning of Integrated facilities monitoring network Work station with GUI based main network software capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems; and / or sensors’ locations. The Work station shall be located in control room in one of the blocks and shall monitor all the blocks panel connected with each other. The software shall be capable of monitoring 100 Nodes with 100 MB baud transmission rate on Fibre Optics network and 12 MB baud transmission on cable or more. The software shall provide the facility to monitor, control all the 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal. | 1.00 | NUM |  | 523000.00 | 523000.00 | 400000.00 | 400000.00 | 615090.00 | 615090.00 | 400000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1100.00 | Supply, Installation, Testing & commissioing of Bacnet/Modbus Card for integration of 8 Loop panel with BMS system etc. As required.(compile with UL listed 9th Edition). | 8.00 | NUM |  | 135000.00 | 135000.00 | 235000.00 | 235000.00 | 181250.00 | 181250.00 | 135000.00 | MANNU LAL AND SONS
1101.00 | Supplying ,installation testing and commissioning of Repeater Panel/Annunciators with suitable character LCD display .The annunciator shall have Four Status Queues with selector switches and LEDs for Alarm, Supervisory, Trouble and Monitor to sort events etc. as required.Mounting options include an annunciator box, and blank modules are required for mounting etc. as required.(UL Listed). | 7.00 | NUM |  | 115850.00 | 926800.00 | 32000.00 | 256000.00 | 87500.00 | 700000.00 | 256000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1102.00 | Supplying, installation, testing & commissioning of intelligent analog addressable Photothermal/Multicriteria Detector detector complete with mounting base complete as required. | 573.00 | NUM |  | 92000.00 | 644000.00 | 55000.00 | 385000.00 | 93750.00 | 656250.00 | 385000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1103.00 | Supplying, installation, testing & commissioning of intelligent addressable Thermal/Heat Detector with rate of rise cum fixed tempreature thermistor complete with base as required. | 7.00 | NUM |  | 2360.00 | 1352280.00 | 2800.00 | 1604400.00 | 2850.00 | 1633050.00 | 1352280.00 | MANNU LAL AND SONS
1104.00 | Supplying, installation, testing & commissioning of addressable manual call point complete as required. | 16.00 | NUM |  | 2940.00 | 20580.00 | 2900.00 | 20300.00 | 3450.00 | 24150.00 | 20300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1105.00 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required. | 16.00 | NUM |  | 4032.00 | 64512.00 | 4200.00 | 67200.00 | 5200.00 | 83200.00 | 64512.00 | MANNU LAL AND SONS
1106.00 | Supplying, installation, testing & commissioning of addressable Beam Detector complete as required. | 12.00 | NUM |  | 6496.00 | 103936.00 | 5200.00 | 83200.00 | 4850.00 | 77600.00 | 77600.00 | Innovations Workspace Solutions Pvt. Ltd.
1107.00 | Supplying, installation, testing & commissioning of fire fighter phone jack complete as required. | 16.00 | NUM |  | 61600.00 | 739200.00 | 32000.00 | 384000.00 | 33565.00 | 402780.00 | 384000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1108.00 | Supplying, installation, testing & commissioning of fire fighter telephone handset complete as required. | 7.00 | NUM |  | 2520.00 | 40320.00 | 3200.00 | 51200.00 | 2615.00 | 41840.00 | 40320.00 | MANNU LAL AND SONS
1109.00 | Supplying, installation, testing & commissioning of addressable fire control module complete as required. (For AHU, Ventilation and pressurization fans ) | 39.00 | NUM |  | 6048.00 | 42336.00 | 6500.00 | 45500.00 | 8875.00 | 62125.00 | 42336.00 | MANNU LAL AND SONS
1110.00 | Supplying, installation, testing & commissioning of addressable fire Control/Monitor module complete as required. | 28.00 | NUM |  | 2632.00 | 102648.00 | 6500.00 | 253500.00 | 3450.00 | 134550.00 | 102648.00 | MANNU LAL AND SONS
1111.00 | Supplying, installation, testing & commissioning of response indicator on surface/recessed MS Box having two LED, metallic cover complete with all connections etc as required. | 289.00 | NUM |  | 2632.00 | 73696.00 | 3600.00 | 100800.00 | 3450.00 | 96600.00 | 73696.00 | MANNU LAL AND SONS
1112.00 | Supplying, installation, testing & commissioning of fault isolator complete with base as required. | 50.00 | NUM |  | 201.00 | 58089.00 | 160.00 | 46240.00 | 225.00 | 65025.00 | 46240.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1113.00 | Supplying and installation of photo luminescent safety signage made up of LED based exit signage with 90 min. battery backup as per NBC including arrangement for fixing on wall / ceiling etc. complete as required (single sided) (size 150 mm x 300 mm) Exit Sign and Internal Hydrant illuminated Sign. | 22.00 | NUM |  | 2632.00 | 131600.00 | 3400.00 | 170000.00 | 3250.00 | 162500.00 | 131600.00 | MANNU LAL AND SONS
1114.00 | Supply, Installation, Testing and Commissioning of UL Listed Fire Alarm Hooter (sound output of minimum 90 dB upto a distance of 30 meters) cum Strobe (Selectable 15, 30, 75, or 110 cd), made Addressable with the help of Intelligent Addressable Signal Module (cost of the Module to be included), capable of being addressed electronically. Manual Addressing (Dip/ Rotary Switches) not acceptable, with seperate power supply arrangement complete as required. Approved Makes : Ansul/ Edwards/Notifier/Wissenschaftler/Rux | 2.00 | EA |  | 4080.00 | 89760.00 | 2800.00 | 61600.00 | 3850.00 | 84700.00 | 61600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1115.00 | PUBLIC ADDRESS SYSTEM
1116.00 | Supplying, installation, testing & commissioning of 6 zone, voice alarm controller with USB, MP3 player (including 6 zone button paging station) with seamless integration facility with main fire alarm panel for voice evacuation complete as required | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1117.00 | Supplying, installation, testing & commissioning of Voice command keypad 6 zone, with microphone assembly complete as required | 1.00 | SET |  | 128800.00 | 128800.00 | 120000.00 | 120000.00 | 105000.00 | 105000.00 | 105000.00 | Innovations Workspace Solutions Pvt. Ltd.
1118.00 | Supplying, installation, testing & commissioning of 1.5/3/6W ceiling speaker complete as required | 266.00 | NUM |  | 36960.00 | 36960.00 | 65000.00 | 65000.00 | 17340.00 | 17340.00 | 17340.00 | Innovations Workspace Solutions Pvt. Ltd.
1119.00 | Supplying, installation, testing & commissioning of 10W wall mount speaker complete as required | 11.00 | NUM |  | 896.00 | 238336.00 | 1050.00 | 279300.00 | 1050.00 | 279300.00 | 238336.00 | MANNU LAL AND SONS
1120.00 | Supplying, installation, testing & commissioning of digital audio amplifier 240Watt, 25V rms operating at 240 Volt AC Supply complete as required | 7.00 | NUM |  | 1512.00 | 16632.00 | 1460.00 | 16060.00 | 2880.00 | 31680.00 | 16060.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1121.00 | SITC of 2x1.5sqmm speaker cable | 1500.00 | M |  | 40320.00 | 282240.00 | 85000.00 | 595000.00 | 35000.00 | 245000.00 | 245000.00 | Innovations Workspace Solutions Pvt. Ltd.
1122.00 | SITC of cat6 cable for Microphone | 50.00 | M |  | 68.00 | 102000.00 | 45.00 | 67500.00 | 45.00 | 67500.00 | 67500.00 | Innovations Workspace Solutions Pvt. Ltd., RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1123.00 | SITC of 19-inch Equipment Rack with standardized frame or enclosure for mounting multiple PA controllers, CD player, FM sources, Amplifiers etc modules. Size 24U | 1.00 | NUM |  | 40.00 | 2000.00 | 42.00 | 2100.00 | 35.00 | 1750.00 | 1750.00 | Innovations Workspace Solutions Pvt. Ltd.
1124.00 | CONDUITS AND CABLES
1125.00 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required 2 x 1.5 sq.mm | 8500.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1126.00 | Supplying and fixing 25 mm dia MS flexible pipe with PVC coating along with all ancillaries and accessories like coupler etc. as required. | 1500.00 | M |  | 168.00 | 1428000.00 | 135.00 | 1147500.00 | 110.00 | 935000.00 | 935000.00 | Innovations Workspace Solutions Pvt. Ltd.
1127.00 | ACCESS CONTROL SYSTEM
1128.00 | Supply, Installation, testing and commissioning of Surface mounted Networkable multiprocessor controlled 4 reader controller capable of controlling multiple readers (IN/OUT) alongwith TCP/IP connectivity complete as per specifications. Control panel housed in MS Powder Coated Cabinet with Tamper Switch, Complete with power supply unit for Controllers & Magnetic Locks as per specification Make-DDS/SoftwareHouse/Continuum | 10.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1129.00 | Supply, Installation, testing and commissioning of Surface mounted Networkable multiprocessor controlled 2 reader controller capable of controlling multiple readers (IN/OUT) alongwith TCP/IP connectivity complete as per specifications. Control panel housed in MS Powder Coated Cabinet with Tamper Switch, Complete with power supply unit for Controllers & Magnetic Locks as per specification Make-DDS/SoftwareHouse/Continuum | 4.00 | NUM |  | 91840.00 | 918400.00 | 42350.00 | 423500.00 | 106800.00 | 1068000.00 | 423500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1130.00 | Supply, installation, testing and commissioning of UL Listed Smart Card Reader fwith compatible support of weigand output, 13.56 MHz technology platform and complies with the ISO 15693 / 14443A standard for contact less smart card technology. Card reader must be configurable to read encrypted ISO14443A sectors using standard or custom read keys for Sign OUT Terminal. should be compatible with HID format cards.Encryption,All RF data transmission between the card and reader should be encrypted using a secure algorithm. Industry-standard encryption techniques and advanced key management systems should be used to avoid the risk of compromised data or duplicated cards.The reader should have audio transducer to provide various tone sequences to signify access granted, access denied, power up and diagnostics. Visually impaired cardholders can easily distinguish between access granted and access denied. High-intensity light bar should provide a clear visual status indication in red, green or amber, even in bright sunlight. Make-HID/Morpho/Tyco | 45.00 | NUM |  | 63280.00 | 253120.00 | 39665.00 | 158660.00 | 74715.00 | 298860.00 | 158660.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1131.00 | Supply Installation testing and Commissioning of Biometric Attendance Device fingerprint technology inside 1:10,000 user identification in 1 second,Anti-fraud features,Fake finger detection, duress finger, timed anti-pass back,Tough design,CPU: ARM® Cortex™-A9 core 1GHz.Linux Operating System, 1:N mode: 10,000 user (*3 templates each, including 1 duress),1:1 mode: 250,000 user IDs,1 Million transaction logs.Inputs/outputs: Wiegand In & Out,as per technical specification. Make-Morpho/HID/Tyco | 2.00 | NUM |  | 14560.00 | 655200.00 | 12895.00 | 580275.00 | 13500.00 | 607500.00 | 580275.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1132.00 | Supply, installation, testing and commissioning of biometric USB devices High performance sensor: 500 dpi, 256 grey levels ,Biometric Feature Extraction to generate templates Feature Extractor is MINEX/FIPS 201 compliant Proprietary, ISO 19794-2 or ANSI 378 template formats available Templates can be stored in the internal database (up to 10 000 templates) | 1.00 | NUM |  | 25760.00 | 51520.00 | 32445.00 | 64890.00 | 28800.00 | 57600.00 | 51520.00 | MANNU LAL AND SONS
1133.00 | Supply, testing and commissioning of 16K chip memory Read/Write contact less non-propritory smart card. Make-HID/Morpho/Tyco | 500.00 | NUM |  | 14000.00 | 14000.00 | 28445.00 | 28445.00 | 5400.00 | 5400.00 | 5400.00 | Innovations Workspace Solutions Pvt. Ltd.
1134.00 | Supply, installation, testing and commissioning of Access Control Application Software for 128 Reader Capacity, and 5000 Card Holder Capacity, Basic GUI , TA Module with Alarm Module, T+Module for using SQL DB , -MULTI Site Module. Make-DDS/SoftwareHouse/Continuum | 1.00 | NUM |  | 280.00 | 140000.00 | 85.00 | 42500.00 | 325.00 | 162500.00 | 42500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1135.00 | Supply, installation, testing and commissioning of Access Control client workstation license. Make-DDS/ SoftwareHouse/ Continuum. | 2.00 | NUM |  | 325000.00 | 325000.00 | 135445.00 | 135445.00 | 138840.00 | 138840.00 | 135445.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1136.00 | Supply, installation, testing and commissioning of Visitor Management system Software with required hardware. | 1.00 | NUM |  | 173600.00 | 347200.00 | 45365.00 | 90730.00 | 102000.00 | 204000.00 | 90730.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1137.00 | Supply, installation, testing and commissioning of Server with minimum specification of Mount Intel® Xeon® processor/ equivalent / latest generation, 2 X 8 core 2.6Hz or heigher CPUs, Support to at least 30 VM, Memory : 64 GB ECC DDR4 upgradable to 100 GB, Graphics NVIDIA (4 GB dedicated) With 2-DVI/HMI output with Dual Screen card & associate Software of operation, Internal Storage of 2TB 7.5K or heigher rpm SATA hard disk along with Dual 10G-Gigabit Ethernet ports, PS/2 / USP Compatible, High –Efficiency, Hot-plug, redundant power supplied, hot-plug drives bays; dual internal SD support; hot-plug, redundant fan. Cost should be With Life time license for Operating System : Microsoft® Windows Server® latest software, & SQL Database . The software & Workstation should be FCC & UL listed | 1.00 | NUM |  | 80000.00 | 80000.00 | 85342.00 | 85342.00 | 102000.00 | 102000.00 | 80000.00 | MANNU LAL AND SONS
1138.00 | Supply, installation, testing and commissioning of Intel Core i5 Quad Core @ 3.3 GHz or Latest, 8GB dual channel DDR3 1333/1600,Graphics NVIDIA (2 GB dedicated) With 2-DVI/HMI output with Dual/Quad Screen card & associate Software of operation,, 2TB 7.5K rpm SATA hard disk, PS/2 Compatible, Dual Gigabit Ethernet, power supply provisions Cost should be With Life time license for Windows 8 enterprise/professional or latest software compatible MacAfee /Symantec Anti virus & All other related software such MS office with liscesenced. The required operation & CCTV remote software etc. & Workstation should be FCC & UL listed | 2.00 | NUM |  | 252000.00 | 252000.00 | 285346.00 | 285346.00 | 296400.00 | 296400.00 | 252000.00 | MANNU LAL AND SONS
1139.00 | Supply, installation, testing and commissioning of Single Leaf Electro Magnetic Lock of Suitable Capacity (Min 600 lbs). Make-Bel/Ncom/Algatech | 40.00 | EA |  | 84000.00 | 168000.00 | 78433.00 | 156866.00 | 96600.00 | 193200.00 | 156866.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1140.00 | Supply, installation, testing and commissioning of Double Leaf Electro Magnetic Lock of Suitable Capacity(Min 1200 lbs). Make-Bel/Ncom/Algatech | 3.00 | EA |  | 1904.00 | 76160.00 | 2855.00 | 114200.00 | 2500.00 | 100000.00 | 76160.00 | MANNU LAL AND SONS
1141.00 | Supply and Fixing of ''U/L'' Bracket with Accessories. Make-Bel/Ncom/Algatech | 43.00 | EA |  | 3696.00 | 11088.00 | 3455.00 | 10365.00 | 5500.00 | 16500.00 | 10365.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1142.00 | Supply and Fixing of Door Positioning sensor with Accessories. Make-Bel/Algatech/Honeywell | 43.00 | EA |  | 1512.00 | 65016.00 | 658.00 | 28294.00 | 750.00 | 32250.00 | 28294.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1143.00 | Supply, Fixing and Laying of 8 Core multi strand, copper, unarmoured Cable (between the every readers & the access controllers). Make-Vimco/Finolex/Polycab | 3000.00 | M |  | 265.00 | 11395.00 | 1435.00 | 61705.00 | 450.00 | 19350.00 | 11395.00 | MANNU LAL AND SONS
1144.00 | Supply, Fixing and Laying of 2 Core x 1.5 Sq mm, multi strand, copper, unarmoured cable (between the controller and EM Lock/Request to exit button). Make-Vimco/Finolex/Polycab | 3000.00 | M |  | 105.00 | 315000.00 | 255.00 | 765000.00 | 135.00 | 405000.00 | 315000.00 | MANNU LAL AND SONS
1145.00 | Enclosure: 42 U Floor Standing Rack & Modular Construction of the rack made of 4 vertical, 4 horizontal & 4 depth aluminum/MS bolted and joined together with Links and Corner Block. Enough support channel to equate the load evenly and castor provision at bottom side, Degree of Protection: The unit should have a minimum of IP 20, Compliance with standards: UL, IEC, Earthing: All cabinet components (doors, side panels, top panels, 19” rails, pdu brackets) shall be grounded directly to the frame using Dual Copper plated earth stud of suitable rating on main Metal parts for better electrical continuity, Weight Capacity: Load Capacity of minimum 1200 Kg, Coating: Powder coated black with fine texture – 60 to 80 uM, Corrosion Resistance:Salt spray test resist upto 500 Hrs, Top and Bottom: Top cover consist of Fire Retardant Brushes and Fire retardant ABS plastic / MS frame for cable and fiber entry to rack from fiber runner and copper cable pathway system. This consists of Brush with 2 line of brush system UL Certified Fire Retardant Brushes and Fire retardant ABS plastic / MS frame, Mounting Angle: 19"Upright adjustable in depth, equipment mounting angles with square slots to accommodate M6 cage nuts, powder coated texture finish. It contains U printing pattern which can be read from down to up and vice versa, Mounting Angle: 19"Upright adjustable in depth, equipment mounting angles with square slots to accommodate M6 cage nuts, powder coated texture finish. It contains U printing pattern which can be read from down to up and vice versa, Castor: Set of 4 castors with levelling feet, 2 brakes on front side and 2 without brakes, Mounting Hardware Packets with set of M 6 screw, Cage Nuts and Washer set of 10 or 20, Network Rack: 42U 800W x 1200D (Height x Width x Depth) ,Single Honeycomb/ Perforated door (Front Side), Double Honeycomb/ Perforated door (Rear Side), Zero U tool-less mounting PDU. 2 no PDU, 230 V AC-2 no. for each PDU, 18 no of 6 AMP socket(c13 type);6 no of 16Amp socket(c19 type) with 2 no of MCB 16/32 Amp. PDU of standard make like APC, Schnider, 4 no of cooling fan. Make: APW/Wellrack/Rittle | 2.00 | NUM |  | 75.00 | 225000.00 | 56.00 | 168000.00 | 115.00 | 345000.00 | 168000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1146.00 | DATA AND TELEPHONE NETWORK
1147.00 | Supply, Installation, testing and commissioning of Cat6A Tool less Information outlet for Data & Voice. Cat6A U/UTP built in crimping mechanism with capability of retermination without refreshing the wires. LCS2 Toolless RJ45 Information outlet with insertion cycle (in & out) should be 2500 times (I/O) along with front side Label holder and transparent shutter. The Information Outlet connector shall be of gold/nickel, thickness of gold > 0.8 μm.The connectors shall be compatible as per IEEE 802.3af standard for POE application. Make-Siemon/Panduit/Legrand/ Schneider/AMP . | 1010.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1148.00 | SITC of Double port Face Plate : Polycarbonate Hi-Grade Plastic FR Grade & UV Resistant 850 degree C/ Glow Wire Test. The face plate should be compatible for Cat5e, Cat6 range of RJ45 and AV connectors.The face plate Size should be of minimum 86x86mm. Make-Siemon/Panduit/Legrand . | 350.00 | NUM |  | 445.00 | 449450.00 | 385.00 | 388850.00 | 650.00 | 656500.00 | 388850.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1149.00 | SITC of Quard port Face Plate : Polycarbonate Hi-Grade Plastic FR Grade & UV Resistant 850 degree C/ Glow Wire Test. The face plate should be compatible for Cat5e, Cat6 range of RJ45 and AV connectors.The face plate Size should be of minimum 86x86mm Make-Siemon/Panduit/Legrand . | 245.00 | NUM |  | 110.00 | 38500.00 | 95.00 | 33250.00 | 250.00 | 87500.00 | 33250.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1150.00 | Supply, Installation, testing and commissioning of 24 port Cat 6A 19" Modular Toolless Patch Panel (loaded) enable all possible combinations of the various types of cable. mounted on the same panel by using various toolless connector blocks/modules. Have a metal structure enabling them to be durably fixed to the uprights of the 19” chassis and assuring automatic grounding between toolless RJ-45 connectors, the panel, and the 19” uprights of the enclosure. Include rear cable support with plastic cable guides to hold cable without need for cable ties. Include quick mounting system to mount the panel into the 19” rails without use of cage-nuts. Front Removal IO's option for maintenance and trouble shooting with 6 Different Colours Labels for Labelling & Identification of Individual Ports. Tested and guaranteed under dual circuit IEEE PoE+ up to 50W for up to 2500 on-load connections / disconnections. Make-Siemon/Panduit/Legrand . | 44.00 | NUM |  | 125.00 | 30625.00 | 145.00 | 35525.00 | 350.00 | 85750.00 | 30625.00 | MANNU LAL AND SONS
1151.00 | Supply and drawing of UTP 4 pair 23 AWG CAT 6A LSZH Cable in the existing surface/ recessed steel/ PVC conduit as required conforming to the following standards like ANSI/TIA 568 C.2, IEC 60332-1, IEC 60754-1. Cable Dia 8.0 mm with beneding radius -4 X Cable Diameter Operates at frequency of 500 Mhz . Make-Siemon/Panduit/Legrand | 54300.00 | M |  | 11144.00 | 490336.00 | 11548.00 | 508112.00 | 27500.00 | 1210000.00 | 490336.00 | MANNU LAL AND SONS
1152.00 | Supply, Installation, testing and commissioning of CAT6A UTP 24 AWG Patch Cord - 1 mtr with cross separator , Manufactured from stranded wires for longer flex-life , Minimum length of 1m, and maximum length of 5m Conforming to the following standards like EN 50173, ISO/IEC 60603-7 & 11801/IEC 60332-1, UL VW-1 Make-Siemon/Panduit/Legrand . | 1010.00 | NUM |  | 60.00 | 3258000.00 | 56.00 | 3040800.00 | 83.00 | 4506900.00 | 3040800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1153.00 | Supply, Installation, testing and commissioning of CAT6A UTP 24 AWG Patch Cord - 2 mtr with cross separator , Manufactured from stranded wires for longer flex-life , Minimum length of 1m, and maximum length of 5m Conforming to the following standards like EN 50173, ISO/IEC 60603-7 & 11801/IEC 60332-1, UL VW-1 Make-Siemon/Panduit/Legrand . | 500.00 | NUM |  | 314.00 | 317140.00 | 245.00 | 247450.00 | 645.00 | 651450.00 | 247450.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1154.00 | Supplying & Fixing of Fiber Optic LC style fully loaded Patch Panel (FOPP), 19" Rack Mount ,Shall have all accessories including coupler plates pre loaded with 24 Nos of LC couplers (OM3) with all accessories complete in all respect. Pigtails Should Complie to ITU-G657.B-Bend insestive fiber. Make-Siemon/Panduit/Legrand . | 4.00 | NUM |  | 325.00 | 162500.00 | 315.00 | 157500.00 | 655.00 | 327500.00 | 157500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1155.00 | Supplying & Fixing of Fiber Optic LC style fully loaded Patch Panel (FOPP), 19" Rack Mount ,Shall have all accessories including coupler plates pre loaded with 12 Nos of LC couplers (OM3) with all accessories complete in all respect. Pigtails Should Complie to ITU-G657.B-Bend insestive fiber. Make-Siemon/Panduit/Legrand . | 7.00 | NUM |  | 13500.00 | 54000.00 | 16548.00 | 66192.00 | 43825.00 | 175300.00 | 54000.00 | MANNU LAL AND SONS
1156.00 | Supplying & Fixing of Fiber Optic Patch Cable (LC-LC), 3 Mtrs. Long, ISO/IEC-11801-OM3 50μ Duplex, LSZH,All patch cords shall conform to EIA/TIA-568C.3 and ISO/IEC-11801,Shall be Duplex Multi Mode Fiber Optic Patch Cords OM3 50μ,Shall support network line speeds up to 10 Gbps.Shall have LC-LC Connector connectors at the ends complete in all respect.Make-Siemon/Panduit/Legrand | 56.00 | NUM |  | 11200.00 | 78400.00 | 12346.00 | 86422.00 | 26875.00 | 188125.00 | 78400.00 | MANNU LAL AND SONS
1157.00 | Supply & Fixing of OM3 50/125μ Type Pigtails of ISO/IEC-11801-OM3 Pigtails with LC Type Connectors,pigtails for terminating fibers on the FOPP complete in all respect. Make-Siemon/Panduit/Legrand | 336.00 | NUM |  | 2576.00 | 144256.00 | 1834.00 | 102704.00 | 3170.00 | 177520.00 | 102704.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1158.00 | Supplying, Installation, Testing & Commissioning of 50μ, 6-core Multi mode OM3 metallic armored Fiber cable as per ISO/IEC-11801, Shall be able to meet Gigabit & 10 Gigabit Ethernet performance up to 300 meters requirement specified by IEEE 802.3z (1000 Base-X) & IEEE 802.3ae (10G Base-X) Tensile load should be 4000 Newton or higher and crush resistance should be 4000 Newton or higher ,The attenuation @ 850 nm should be ≤ 2.7 (Max) db/Km and @ 1300 nm should be ≤ 0.7 (Max) dB/Km, the fiber construction can be unitube or multitube, but tensile and crush resistance parameters should be matched, the jacket shall be FRLSZH complete in all respect. Make-Siemon/Panduit/Legrand . | 2000.00 | M |  | 280.00 | 94080.00 | 455.00 | 152880.00 | 345.00 | 115920.00 | 94080.00 | MANNU LAL AND SONS
1159.00 | Supplying, Installation, Testing & Commissioning of 24 port 10/100/1000BASE-T PoE+ ports and four GbE/10GbE SFP/SFP+ uplink ports layer3 and layer 2 from day1 having static & RIP , should support at least 8 switches stack, should support redundant power supply and fan , 3 Year OEM On site NBD warranty. Please refer tender for detailed Tech Specifications. Make: Juniper/Cisco/Extreme | 32.00 | NUM |  | 146.00 | 292000.00 | 214.00 | 428000.00 | 195.00 | 390000.00 | 292000.00 | MANNU LAL AND SONS
1160.00 | Supplying, Installation, Testing & Commissioning of 24 port 10/100/1000BASE-T ports and four GbE/10GbE SFP/SFP+ uplink ports layer3 and layer 2 from day1 having static & RIP , should support at least 8 switches stack, should support redundant power supply and fan , 3 Year OEM On site NBD warranty. Please refer tender for detailed Tech Specifications. Make: Juniper/Cisco/Extreme | 16.00 | NUM |  | 156800.00 | 5017600.00 | 215240.00 | 6887680.00 | 192500.00 | 6160000.00 | 5017600.00 | MANNU LAL AND SONS
1161.00 | Supplying Installation testing and Commissioning of Small Form Factor Pluggable 1 Gigabit Ethernet (SFP+) SR Optics 3 Year OEM On site warranty. Make: Juniper/Cisco/Extreme | 56.00 | NUM |  | 145600.00 | 2329600.00 | 165424.00 | 2646784.00 | 178750.00 | 2860000.00 | 2329600.00 | MANNU LAL AND SONS
1162.00 | Supply, installation, testing & commissioning of 10 GBase-T Gigabit Ethernet Transceiver SFP 3 Year OEM On site warranty - Make: Juniper/Cisco/Extreme | 4.00 | NUM |  | 9520.00 | 533120.00 | 13566.00 | 759696.00 | 11690.00 | 654640.00 | 533120.00 | MANNU LAL AND SONS
1163.00 | Supplying Installation testing and Commissioning of SFP+ 10 Gigabit Ethernet Direct Attach Copper (twinax copper cable) 1m in length complete in all3 Year OEM On site warranty respect. Make: Juniper/Cisco/Extreme | 43.00 | NUM |  | 24640.00 | 98560.00 | 24678.00 | 98712.00 | 38500.00 | 154000.00 | 98560.00 | MANNU LAL AND SONS
1164.00 | Supplying Installation testing and Commissioning of 32 Port Fiber Switch 10/100/1000BASE-T ports, with up to 4X 10GbE uplinks and 2X 40GbE uplinks, Switch should support stacking bandwidth of minimum 160gbps, Modular operating system, 32 1 Gig SFP port with additional 4 no. of 10g SFP+PORT, redundant power supply, layer3 switch, each switch should be provided with stacking port/cable complete in all respect. Make-Juniper/Cisco/Extreme | 2.00 | NUM |  | 7280.00 | 313040.00 | 4500.00 | 193500.00 | 8875.00 | 381625.00 | 193500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1165.00 | Enclosure: 24 U Floor Standing Rack & Modular Construction of the rack made of 4 vertical, 4 horizontal & 4 depth aluminum/MS bolted and joined together with Links and Corner Block. Enough support channel to equate the load evenly and castor provision at bottom side, Degree of Protection: The unit should have a minimum of IP 20, Compliance with standards: UL, IEC, Earthing: All cabinet components (doors, side panels, top panels, 19” rails, pdu brackets) shall be grounded directly to the frame using Dual Copper plated earth stud of suitable rating on main Metal parts for better electrical continuity, Weight Capacity: Load Capacity of minimum 1200 Kg, Coating: Powder coated black with fine texture – 60 to 80 uM, Corrosion Resistance:Salt spray test resist upto 500 Hrs, Top and Bottom: Top cover consist of Fire Retardant Brushes and Fire retardant ABS plastic / MS frame for cable and fiber entry to rack from fiber runner and copper cable pathway system. This consists of Brush with 2 line of brush system UL Certified Fire Retardant Brushes and Fire retardant ABS plastic / MS frame, Mounting Angle: 19"Upright adjustable in depth, equipment mounting angles with square slots to accommodate M6 cage nuts, powder coated texture finish. It contains U printing pattern which can be read from down to up and vice versa, Mounting Angle: 19"Upright adjustable in depth, equipment mounting angles with square slots to accommodate M6 cage nuts, powder coated texture finish. It contains U printing pattern which can be read from down to up and vice versa, Castor: Set of 4 castors with levelling feet, 2 brakes on front side and 2 without brakes, Mounting Hardware Packets with set of M 6 screw, Cage Nuts and Washer set of 10 or 20, Network Rack: 24U 800W x 1200D (Height x Width x Depth) ,Single Honeycomb/ Perforated door (Front Side), Double Honeycomb/ Perforated door (Rear Side), Zero U tool-less mounting PDU. 2 no PDU, 230 V AC-2 no. for each PDU, 18 no of 6 AMP socket(c13 type);6 no of 16Amp socket(c19 type) with 2 no of MCB 16/32 Amp. PDU of standard make like APC, Schnider, 4 no of cooling fan. Make: APW/Wellrack/Rittle | 7.00 | NUM |  | 633248.00 | 1266496.00 | 615444.00 | 1230888.00 | 656250.00 | 1312500.00 | 1230888.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1166.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm dia.- ISI MARK | 300.00 | M |  | 40320.00 | 282240.00 | 65440.00 | 458080.00 | 45000.00 | 315000.00 | 282240.00 | MANNU LAL AND SONS
1167.00 | Supply , Installtion , Testing and comissioning of 1, 2 and 4 port face plate white for I/O fixing at user side For Data ,Voice Make: Legrand/Siemon/Panduit | 25.00 | NUM |  | 50.00 | 15000.00 | 165.00 | 49500.00 | 60.00 | 18000.00 | 15000.00 | MANNU LAL AND SONS
1168.00 | SITC of 50 Pair Krone Module | 2.00 | NUM |  | 150.00 | 3750.00 | 95.00 | 2375.00 | 80.00 | 2000.00 | 2000.00 | Innovations Workspace Solutions Pvt. Ltd.
1169.00 | Supplying, installing, testing and commissioning of Cat 6 RJ45 Modular Jack, Min. 600Mhz ETL Tested (Enclose Test Report), Encapsulated Lead Frame technology (Without PCB), 1000 Front Mating Cycles, 4.8 Gbps Supported for Wave 2 Devies for 100MT Channel, 25 Years Performance Warranty, UL Listed, RoHS Certified, UL 1863, IEC 60603-7, FCC part 68-F, Storage Temperature -40°C to +70°C, Without Spring Shutter as it malfunctioned, Technical Datasheet should have Worst Case Performance Values of IL <=0.31dB, NEXT Min. 44 dB, FEXT Min. 37 dB, RL Min. 18 dB & Balanced TCL Min. 22 dB @ 300 Mhz. Safety Listing of ACA and Bi-national standard listed, Cable Pairs Crimped & Cut together via Tool to avoid manual termination issues Make: Legrand/Siemon/Panduit | 50.00 | NUM |  | 4032.00 | 8064.00 | 14555.00 | 29110.00 | 4000.00 | 8000.00 | 8000.00 | Innovations Workspace Solutions Pvt. Ltd.
1170.00 | WiFi System
1171.00 | Supply, installation, testing & commissioning of Dual-band 802.11abgn/ac Wireless Access Point, 2x2:2 streams, 1 ports, 802.3af PoE support. Does not include power adapter or PoE injector.should Includes Limited Lifetime Warranty and Mounting Kit complet in all respect. Make-Aruba/Ruckus/Juniper | 14.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1172.00 | Supply, installation, testing & commissioning of Wi-Fi Controller with 4 Gig Ports, with 100 APs license, Power Supply and HA mode alongwith 3 year support. Make-Aruba/Ruckus/Juniper | 1.00 | NUM |  | 35200.00 | 492800.00 | 48655.00 | 681170.00 | 35000.00 | 490000.00 | 490000.00 | Innovations Workspace Solutions Pvt. Ltd.
1173.00 | IP EPABX System
1174.00 | Supply Installation, Testing and Commissioning of Server Based EPABX Fully Computerized IP System, SIP Compliant. Multi slot 19: U Rack Mountable 2U Rack Expandable upto 900 Ports Presently Configuration as Below CO Line 08 Nos. PRI(30 Channel) 04 Nos. SIP Extension 64 Nos IP Extension Circuits 375 Nos. Analog Extension Circuits 64 Nos. Make-Cisco/Alcatel/Progility(Seimens) | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1175.00 | Supply Installation and Commissioning of centralized Operator Console with all dignostic Software of IP EPABX System .Make-Cisco/Alcatel/Progility(Seimens) | 1.00 | SET |  | 1517500.00 | 1517500.00 | 3255240.00 | 3255240.00 | 1872375.00 | 1872375.00 | 1517500.00 | MANNU LAL AND SONS
1176.00 | Supply Installation, Testing and Commissioning of 4 Level IVR software with 6 different languages and 4 time schedule | 1.00 | SET |  | 46200.00 | 46200.00 | 164555.00 | 164555.00 | 57500.00 | 57500.00 | 46200.00 | MANNU LAL AND SONS
1177.00 | Supply Installation Testing and Commissioning of Call Billing Software with PC | 1.00 | SET |  | 46200.00 | 46200.00 | 35444.00 | 35444.00 | 57500.00 | 57500.00 | 35444.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1178.00 | Supply Installation Testing and Commissioning of IP Phone (24Key) Backlit keypad Hands-free, full duplex ,Headset support Easy to use soft keys/LCD prompts,Directory dialling,Navigation wheel,Call history,Wall mountable,Backlit LCD screen,Security lock key open interface complete in all respect.Make-Cisco/Alcatel/Progility(Seimens) | 25.00 | EA |  | 107800.00 | 107800.00 | 85235.00 | 85235.00 | 75000.00 | 75000.00 | 75000.00 | Innovations Workspace Solutions Pvt. Ltd.
1179.00 | Supply Installation Testing and Commissioning of IP Phone (12Key)Backlit keypad Hands-free, full duplex Headset support Easy to use soft keys/LCD prompts Directory dialling Navigation wheel Call history Wall mountable Backlit LCD screen Security lock key XML open interface complete in all respect. Make-Cisco/Alcatel/Progility(Seimens) | 50.00 | EA |  | 24200.00 | 605000.00 | 24355.00 | 608875.00 | 7500.00 | 187500.00 | 187500.00 | Innovations Workspace Solutions Pvt. Ltd.
1180.00 | Supply Installation Testing and Commissioning of IP Phone (6Key)Backlit keypad Hands-free, full duplex Headset support Easy to use soft keys/LCD prompts Directory dialling Navigation wheel Call history Wall mountable Backlit LCD screen Security lock key XML open interface complete in all respect.Make-Cisco/Alcatel/Progility(Seimens) | 100.00 | EA |  | 13200.00 | 660000.00 | 18535.00 | 926750.00 | 5000.00 | 250000.00 | 250000.00 | Innovations Workspace Solutions Pvt. Ltd.
1181.00 | Supply Installation Testing and Commissioning of Analog Speaker phone With CLI and handset | 50.00 | EA |  | 10780.00 | 1078000.00 | 9544.00 | 954400.00 | 3125.00 | 312500.00 | 312500.00 | Innovations Workspace Solutions Pvt. Ltd.
1182.00 | Video Surveillance System(IP CCTV)
1183.00 | Supplying, installation, testing and commissioning of 2 megapixels resolution Network Dome Camera for true HD quality images,2.8 – 12 mm varifocal lens,True Day/Night (TDN) functionality for true color image ,Motion Detection 4 Zones, Multi- Level Sensitivity Privacy Zones 4 Zones,Snapshoot Support JPEG format Password Protection Support Character Display Support(Channel /Date) ONVIF Yes,IR Illumination20-30M IR illuminators for clear images in low light conditions Wide Dynamic Range 3D noise reduction for sharper images and lower bandwidth use in low light ONVIF compliant complete in all respect. Make-Hanwha/Mobotix/Pelco/Tyco | 10.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1184.00 | Supply, installation, testing and commissioning of 2 megapixels resolution Network Bullet camera camera,Imager 1/2.8”SONY 2.43 mega low illumination CMOS,Video Compression. .H.264/MJPEG,Day/Night .Mechanical ICR,Minimum Illumination-0Lux/F1.4(IR ON) IR Illumination-40-50M,,Electronic Shutter-Auto/Manual(1/25~1/10000) Lens 2.8 – 12 mm varifocal lens,Resolution Main-stream:D1/Q1080P(960*540)/HD720P/ HD1080P 1-25/30fps,Digital Noise Reduction-3D,Wide Dynamic Range-Digital WDR Motion Detection -4 Zones, Multi- Level Sensitivity,Privacy Zones-4 Zones,Snapshoot-Support JPEG format,Password Protection-Support,Character Display-Support(Channel /Date).Regulatory Emissions-FCC Part 15 CE: EN55022,Immunity -CE: EN50130-4,IP Rating- IP66 rated enclosure to protect against dust and water damage ONVIF compliant. Make-Hanwha/Mobotix/Pelco/Tyco | 10.00 | EA |  | 13822.00 | 138220.00 | 32455.00 | 324550.00 | 15000.00 | 150000.00 | 138220.00 | MANNU LAL AND SONS
1185.00 | Supplying of 1/2.8’’ Progressive Scan CMOS PTZ Dome Camera with laser IR,Compression- H.264/MJPEG/MPEG4,Focal Length - 4.3-129mm, Optical zoom 30x and digital zoom 16x,Max. Image Resolution-1920×1080,Frame Rate 50Hz: 25fps(1920×1080) 360° endless pan range and -2°-90° tilt range,240°/s Pan Preset Speed and 200°/s Tilt Preset Speed,0.1°-160°/s Manual Pan Speed and 1°- 120°/s Manual Tilt Speed,256 presets programmable; preset image freezing capability ,8 patrols, up to 32 presets per patrol 4 patterns, with the recording time not less than 10 minutes per pattern,SD/SDHC card local storage Support up to 8 NAS storage; Edge recording (transmit the videos from SD card to the NAS after network resumed) High performance Laser IR LED covering up to 150m (IR) distance 3D intelligent positioning function,3D DNR,Protection Level-IP66 standard,TVS 6,000V lightning protection, surge protection and voltage transient protection. Make-Hanwha/Mobotix/Pelco/Tyco | 2.00 | EA |  | 14850.00 | 148500.00 | 32455.00 | 324550.00 | 16500.00 | 165000.00 | 148500.00 | MANNU LAL AND SONS
1186.00 | Supply, installation, testing and commissioning of 2U Rack mount single chassis Network Video Recorder with dual Gb NIC, 1 DVI-I + HDMI + 1 Display Port, max 2 simultaneous monitors, RS-232/485 serial port, DVD, Server Operating System-Windows 10,Ubuntu Linux 16.04, Processor-Gen 4 Intel Core i3, Local Client Display Rate (FPS)Windows – 700 FPS (HD)Linux – 900 FPS (HD),High Performance, High Reliability IP Recorder. — Continuously records 300Mbps (Windows) & 450 Mbps (Linux)of video while hosting a local client, multiple remote clients and the web server on a single server,RAM-4 GB, 8 GB, 12 GB (Optional)solid-state operating system drive,USB-6 x USB 2.0, 2 x USB 3.0 high air flow cooling and hardware monitoring features ensure maximum uptime. keyboard and mouse, Professional Grade client and server software pre-installed and software updates. Access live and recorded video on multiple client PCs with free Windows, Mac or Linux client application. web server application is pre-installed on the server to access video through a web browser or free Mobile iPhone / iPad and Android apps. Maximum Storage Capacity 30TB & Maximum Hard Drive 3 Slot(Up to 10TB) Support Up to 64 IP Camera. Make-Tyco/Mobotix/Pelco/Tyco | 1.00 | EA |  | 126500.00 | 253000.00 | 215440.00 | 430880.00 | 105000.00 | 210000.00 | 210000.00 | Innovations Workspace Solutions Pvt. Ltd.
1187.00 | Supply, installation, testing and commissioning of 10TB HDD. Make-WD/Seagate | 3.00 | EA |  | 357500.00 | 357500.00 | 345500.00 | 345500.00 | 72000.00 | 72000.00 | 72000.00 | Innovations Workspace Solutions Pvt. Ltd.
1188.00 | Supply, installation, testing and commissioning of Video Management System (VMS) software shall be used to view live and recorded video from capture cards and IP devices connected to local and wide area networks. The VMS software shall have a client/server-based architecture that can be configured as a standalone VMS system with the client software running on the server hardware and/or the client running on any network-connected TCP/IP workstation. Multiple client workstations shall be capable of simultaneously viewing live and/or recorded video from one or more servers. Multiple servers shall also be able to simultaneously provide live and/or recorded video to one or more workstations. The VMS server software shall also have the ability to be installed on an IP edge device—such as an IP camera or encoder that allows for 3rd party applications—allowing the device to serve as both a server and IP video recording device.The VMS shall not charge for the number of concurrent clients (min. 50 thick clients and 16 mobile clients to be provided along with VMS). Make-Tyco/Mobotix/Pelco | 32.00 | EA |  | 30800.00 | 92400.00 | 25645.00 | 76935.00 | 24000.00 | 72000.00 | 72000.00 | Innovations Workspace Solutions Pvt. Ltd.
1189.00 | Supply, Installation, Testing and Commissioning of Workstation PC: Intel(R) Core(TM) i7-3770 Processor (8M Cache, up to 3.90 GHz); Memory: 4GB, NON-ECC, 1600MHZ; RAM: 4GB (1x4GB) Non-ECC DDR3 1600MHz SDRAM Memory; Keyboard: 12 function keys; Chassis: Tower/Workstation; DVD: 8X Slimline DVD+/-RW, Data Only; 20" TFT Monitor; Dual Graphics Card; Network interface card: Integrated Intel(R) 82579LM Gigabit1 Ethernet LAN 10/100/1000; Hard disk: 250GB, 7200 RPM 3.5" SATA 6Gb/s Hard Drive; Operating system: Windows 7 Professional 64 Bit. Make: HP/DELL/ASUS | 2.00 | EA |  | 7150.00 | 228800.00 | 8444.00 | 270208.00 | 6000.00 | 192000.00 | 192000.00 | Innovations Workspace Solutions Pvt. Ltd.
1190.00 | Supply , Installation,testing and commissioning of 55" LED TV- LED TV should be Professional and HDMI Ports - 55 inches UHD 3840 x 2160 (16:9) Direct-lit LED Display with brightness of 500 nits, viewing angle of 178° h/v. Display should be supplied with necessary mounting bracket as required. Make: Sony, LG, Samsung | 2.00 | NUM |  | 137500.00 | 275000.00 | 95345.00 | 190690.00 | 72000.00 | 144000.00 | 144000.00 | Innovations Workspace Solutions Pvt. Ltd.
1191.00 | Audio Visual System in Board Room
1192.00 | Supply Installation Testing and commissioning of 120'' LED TV Ultra HD LED Full array (Direct LED) Audio Codec - Dolby Digital / DTS, IP Control,Input Terminals - DisplayPort 1.2 in x 1, DisplayPort out, HDMI 2.0 x 2 (HDCP 2.2), HDMI 1.4 x 2, OPS x 1, USB X 1, Component x 1, Composite x 2, D-Sub x 1 ,Output Terminals-Optical, RCA L/R,Wake on LAN,Input/Output Terminals-RS23SC X 1 , LAN X 1,Public Mode / Hotel Mode,MediaPlex Plus Processing,Bezel Size-10-20mm, Power Consumption 300-450 W.Viewing Angle (H/V)- 176°/176° (CR ≥ 10) complete in all respects. Make-Sony/LG/Samsung | 1.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1193.00 | Supply, Installation, testing and commissioning of two-way, thin edge ceiling speaker with back can, built in cone driver, Line Transformer Tappings : 60watt - 30watt, Sensitivity : 86dB, Sound Pressure : 106dB, Dispersion Conical : 145° or more, Frequency Response : 90 Hz - 20 kHz, Frequency range : 65 Hz - 20 kHz etc complete required as per specifcations. Make: OSL/OHM/ British Acoustics/ LAcoustics | 6.00 | EA |  | 508500.00 | 508500.00 | 65445.00 | 65445.00 | 2277000.00 | 2277000.00 | 65445.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1194.00 | Supply, Installation, testing and commissioning of digital power amplifier, class-D, RMS power : 2 X 240watt, Frequency Response : 50 Hz - 22 kHz, Signal / Noise : > 100 dB, THD+N : < 0.3%, Crosstalk : < 80 dB, Power Supply : Switching mode, Common mode rejection ratio : 70dB, Protection : DC Short circuit; Over heating; Over load; Signal limiting, built in temperature controlled fan etc complete required as per specifications. Make: OSL/OHM/ British Acoustics/ LAcoustics | 1.00 | EA |  | 9020.00 | 54120.00 | 4533.00 | 27198.00 | 11770.00 | 70620.00 | 27198.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1195.00 | SITC of 12x8 Audio Digital Signal Processor dante built in with minimum 9 or more channel of AEC, Matrix switching, Phantom Power supply. 20Hz to 20 KHz or Frequency response, AEC taillength: >200msec or better etc as required, A/D & D/A conversion: 24 bit, 48 kHz sampling etc as required at site. Make : Sennheiser /BSS / Xylica. | 1.00 | EA |  | 66000.00 | 66000.00 | 48555.00 | 48555.00 | 20425.00 | 20425.00 | 20425.00 | Innovations Workspace Solutions Pvt. Ltd.
1196.00 | Supply of Chairman Unit with LED screen, 4 types of operation modes-vote initiation, master mute, accepting applications, Output frequency response 40-16000Hz, Earphone load >16 Ω, Earphone volume 10 mV, Earphone output φ 3.5mm stereo jack, Max. power consumption 1.65W, Microphone Type Uni-directional electret condenser microphone, connection 7P-DIN dedicated cable with buckle. Make: OSL/Beyerdynamic/ Shure/Nuemann | 1.00 | EA |  | 297000.00 | 297000.00 | 215344.00 | 215344.00 | 386400.00 | 386400.00 | 215344.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1197.00 | Supply of Digital Conference Control Unit - Wired ,Supply voltage AC110Vor AC220V (default settings), Number of connectable conference units ≤254, Frequency response 40-16000Hz, Signal-to-noise ratio >80dBA, Dynamic range >85dB, Total harmonic distortion <0.05% Original input: 6.3 mm balanced Signal strength: 0.775 V, Audio crosstalk >70dB Make: OSL/Beyerdynamic/ Shure/Nuemann | 1.00 | EA |  | 44000.00 | 44000.00 | 45665.00 | 45665.00 | 201250.00 | 201250.00 | 44000.00 | MANNU LAL AND SONS
1198.00 | Supply & fixing of Molded CAT-5/6 Patch Cords for loop in loop out 3 mtr length. Make: OSL/Beyerdynamic/ Shure/Nuemann | 31.00 | EA |  | 115500.00 | 115500.00 | 215600.00 | 215600.00 | 253000.00 | 253000.00 | 115500.00 | MANNU LAL AND SONS
1199.00 | Supply & fixing of Molded CAT-5/6 Patch Cords for loop in loop out 20 mtr length.Make: OSL/Beyerdynamic/ Shure/Nuemann | 2.00 | EA |  | 4000.00 | 124000.00 | 210.00 | 6510.00 | 3590.00 | 111290.00 | 6510.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1200.00 | SITC of Logitech Group Video Conferencing Bundle with Expansion Mics HD 1080p Camera Speakerphone of minimum dimensions (LxWxH) ‎24.1 x 24.1 x 6.4 Centimeters complete in all respect. | 2.00 | EA |  | 9000.00 | 18000.00 | 35435.00 | 70870.00 | 36570.00 | 73140.00 | 18000.00 | MANNU LAL AND SONS
1201.00 | SITC of Wireless presentation device which supports video resolution upto 1080p (Full HD), with 1xHDMI / DVI/ DP output, PoE enabled Ethernet port, 1xUSB port for data sharing , Supports Windows laptops and MAC, as well as iOS, Windows and Android mobile operating systems, display minimum 2 users screen simultaneously on a single display through hardware dongle/ software app. Supports DHCP, Audio out. Support 32 or more concurrent users. Support Full HD video of 1080p @ 30fps or more etc as required at site. | 1.00 | EA |  | 165000.00 | 330000.00 | 35435.00 | 70870.00 | 145410.00 | 290820.00 | 70870.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1202.00 | Supply, Installation, testing and commissioning of of Cable Manager with 1 no. multiregion AC Power socket, 1x USB power, Black anodised /brushed aluminium finish,Tilt up lid with pass through holes for 1 HDMI, 1 VGA with audio, 1x LAN complete etc. as required. Make-Crestron/Satellier/RG Spectrum | 6.00 | EA |  | 135000.00 | 135000.00 | 65345.00 | 65345.00 | 248400.00 | 248400.00 | 65345.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1203.00 | Supply lnstatlation Testing & Commissioning of 8 x 8 HDMI Matrix Switcher with HDCP Compliant, HDMI and HDCP as per technical specification. Input and Output: supporting 8 signal input and 8 signal outputs simultaneously. Make-Crestron/Satellier/RG Spectrum | 1.00 | EA |  | 13000.00 | 78000.00 | 22500.00 | 135000.00 | 19320.00 | 115920.00 | 78000.00 | MANNU LAL AND SONS
1204.00 | Supply, Installation, testing and commissioning of of HDMI & Control twisted pair Scaling receiver with 1x Twisted pair/HDbaseT input on RJ45, Output: 1x HDMI, 1x RS232/IR(Controls), supporting reception of audio,video, controls and power upto minimum 100mtrs or more. 4K resolution support & should be able to do scaling upto 4K resolution. HDCP 2.2 compliant & EDID. as per specifications & Compatible to the Modular Digital Matrix Switcher complete etc. as required. Make-Crestron/Satellier/RG Spectrum | 2.00 | EA |  | 324500.00 | 324500.00 | 35400.00 | 35400.00 | 331200.00 | 331200.00 | 35400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1205.00 | Supply, Installation, testing and commissioning of of HDMI & Control twisted pair Transmitter with Input: 1x HDMI, 1x RS232/IR(Controls) , Output: 1x Twisted pair/HD base T input on RJ45, supporting transmission of audio,video, controls and power upto minimum 70 mtrs or more. Upto 4K resolution support at various distance, remote powering feature, HDCP 2.2 compliant & EDID as per specifications complete etc. as required. Make-Crestron/Satellier/RG Spectrum | 2.00 | EA |  | 65000.00 | 130000.00 | 38400.00 | 76800.00 | 39400.00 | 78800.00 | 76800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1206.00 | Supply, Installation, testing and commissioning of HDMI & Control twisted pair Receiver with Input:1x Twisted pair/HDbaseT input on RJ45, Output:1x HDMI, 1x RS232/IR(Controls) , supporting reception of audio,video, controls and power upto minimum 70mtrs or more. Upto 4K resolution support at various distance ,remote powering feature,HDCP 2.2 compliant & EDID. as per specifications complete etc. as required. Make-Crestron/Satellier/RG Spectrum | 1.00 | EA |  | 58000.00 | 116000.00 | 36400.00 | 72800.00 | 39400.00 | 78800.00 | 72800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1207.00 | Supply, Installation, testing and commissioning of Touch Panel Control System should be equipped with at least 8 bidirectional RS-232 serial ports (Internal /external module acceptable), at least 8 IR/Serial ports, at least 4or more Digital I/O ports, at least 4 or more low voltage relays for controlling room functions, at least 1 Ethernet monitoring and control port, Memory: 512MB SDRAM, 4 GB Flash or more etc.as required. | 1.00 | EA |  | 58000.00 | 58000.00 | 36400.00 | 36400.00 | 39400.00 | 39400.00 | 36400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1208.00 | Supply, Installation, testing and commissioning of 9.7" Wireless Touch panel, screen resolution 2048x1536 pixels, 32 GB with Should have appropriate app for controlling the Devices etc.as required. | 1.00 | EA |  | 155000.00 | 155000.00 | 55345.00 | 55345.00 | 39400.00 | 39400.00 | 39400.00 | Innovations Workspace Solutions Pvt. Ltd.
1209.00 | Supply, Installation, testing and commissioning of Wifi router with 8 port Switch etc complete as required. | 1.00 | EA |  | 44000.00 | 44000.00 | 68345.00 | 68345.00 | 41400.00 | 41400.00 | 41400.00 | Innovations Workspace Solutions Pvt. Ltd.
1210.00 | Supply and Laying of 2.5 Metres HDMI patch cord with connectors in existing conduit i/c testing etc. as required. Make-Crestron/Satellier/RG Spectrum | 2.00 | EA |  | 3850.00 | 3850.00 | 4500.00 | 4500.00 | 24840.00 | 24840.00 | 3850.00 | MANNU LAL AND SONS
1211.00 | Supply and Laying of 1.5 Metres HDMI patch cord with connectors in existing conduit i/c testing etc. as required. Make-Crestron/Satellier/RG Spectrum | 16.00 | EA |  | 2000.00 | 4000.00 | 1250.00 | 2500.00 | 3035.00 | 6070.00 | 2500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1212.00 | Supply and Laying of 16 AWG 2 core speaker cable with connectors in existing conduit i/c testing etc. as required. | 150.00 | M |  | 1800.00 | 28800.00 | 950.00 | 15200.00 | 2210.00 | 35360.00 | 15200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1213.00 | Supply and Laying of 24 AWG or better shielded CAT 6 cable with suitable connectors in existing conduit i/c testing etc. as required. | 500.00 | M |  | 98.00 | 14700.00 | 135.00 | 20250.00 | 145.00 | 21750.00 | 14700.00 | MANNU LAL AND SONS
1214.00 | S/F of network rack of size 19"having 42U for supporting equiments pertaining to sound system with front/rear lockable doors i/c providing caster wheels and all other accessories for easy storation and movement etc. complete as required. | 1.00 | EA |  | 45.00 | 22500.00 | 45.00 | 22500.00 | 130.00 | 65000.00 | 22500.00 | MANNU LAL AND SONS, RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1215.00 | SITC of Soundstation SIP-based IP conference phone of tentative dimensions - 36.8 x 31.1 x 6.4 cm (L x W x H) with two (2) Number of microphone of cisco make or equivalent with power of IEEE 802.3af Power over Ethernet (built in), Optional external universal AC power supply: 100-240V, 0.4A, 48V/19W. Display of Size (pixels): 248 x 68 (W x H), White LED backlight with custom intensity control. Keypad - Standard 12-key keypad, Context-dependent soft keys: 3, On-hook/Off-hook, redial, mute, volume up/ down. Audio features Loudspeaker Frequency: 220-14,000 Hz Volume: Adjustable to 86 dB at 1/2 meter peak volume Individual volume settings with visual feedback for each audio path Voice activity detection Comfort noise fill DTMF tone generation / DTMF event RTP payload Low-delay audio packet transmission Adaptive jitter buffers Packet loss concealment Acoustic echo cancellation Background noise suppression Supported Codecs G.711 (A-law and Mu-law) G.729a (Annex B) G.722, G.722.1 G.722.1C Siren 14 complete in all repsect and as directed by Engineer-In-Charge. | 3.00 | NUM |  | 54000.00 | 54000.00 | 65000.00 | 65000.00 | 38640.00 | 38640.00 | 38640.00 | Innovations Workspace Solutions Pvt. Ltd.
1216.00 | Supplying and laying of RG6 Cable in the existing surface/ recessed steel/ PVC conduit as required. | 100.00 | M |  | 39000.00 | 117000.00 | 78500.00 | 235500.00 | 48875.00 | 146625.00 | 117000.00 | MANNU LAL AND SONS
1217.00 | Audio Visual System in Meeting Room
1218.00 | Supply Installation Testing and commissioning of 85'' LED TV Ultra HD LED Full array (Direct LED) Audio Codec - Dolby Digital / DTS, IP Control,Input Terminals - DisplayPort 1.2 in x 1, DisplayPort out, HDMI 2.0 x 2 (HDCP 2.2), HDMI 1.4 x 2, OPS x 1, USB X 1, Component x 1, Composite x 2, D-Sub x 1 ,Output Terminals-Optical, RCA L/R,Wake on LAN,Input/Output Terminals-RS23SC X 1 , LAN X 1,Public Mode / Hotel Mode,MediaPlex Plus Processing,Bezel Size-10-20mm, Power Consumption 300-450 W.Viewing Angle (H/V)- 176°/176° (CR ≥ 10) complete in all respects. Make-Sony/LG/Samsung | 6.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1219.00 | Supply, Installation, testing and commissioning of two-way, thin edge ceiling speaker with back can, built in cone driver, Line Transformer Tappings : 60watt - 30watt, Sensitivity : 86dB, Sound Pressure : 106dB, Dispersion Conical : 145° or more, Frequency Response : 90 Hz - 20 kHz, Frequency range : 65 Hz - 20 kHz etc complete required as per specifcations. Make: OSL/OHM/ British Acoustics/ LAcoustics | 22.00 | EA |  | 325000.00 | 1950000.00 | 245600.00 | 1473600.00 | 370125.00 | 2220750.00 | 1473600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1220.00 | Supply, Installation, testing and commissioning of digital power amplifier, class-D, RMS power : 2 X 120watt, Frequency Response : 50 Hz - 22 kHz, Signal / Noise : > 100 dB, THD+N : < 0.3%, Crosstalk : < 80 dB, Power Supply : Switching mode, Common mode rejection ratio : 70dB, Protection : DC Short circuit; Over heating; Over load; Signal limiting, built in temperature controlled fan etc complete required as per specifications. Make: OSL/OHM/ British Acoustics/ LAcoustics | 5.00 | EA |  | 9680.00 | 212960.00 | 5645.00 | 124190.00 | 11770.00 | 258940.00 | 124190.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1221.00 | Supply of Digital 2 in 6 out Installation Controller. Spyder Software DSP control via USB. 10-PEQ, peak limiting, 2 sec delay, matrix and crossover. Make: OHM/ British Acoustics/ OSL/ LAcoustics/ D&B | 5.00 | EA |  | 66000.00 | 330000.00 | 38566.00 | 192830.00 | 20425.00 | 102125.00 | 102125.00 | Innovations Workspace Solutions Pvt. Ltd.
1222.00 | Supply, Installation, testing and commissioning of Cable Manager with 1 no. multiregion AC Power socket, 1x USB power, Black anodised /brushed aluminium finish,Tilt up lid with pass through holes for 1 HDMI, 1 VGA with audio, 1x LAN complete etc. as required. Make-Crestron/Satellier/RG Spectrum | 10.00 | EA |  | 60500.00 | 302500.00 | 135000.00 | 675000.00 | 35330.00 | 176650.00 | 176650.00 | Innovations Workspace Solutions Pvt. Ltd.
1223.00 | Supply and Laying of 2.5 Metres HDMI patch cord with connectors in existing conduit i/c testing etc. as required. Make-Crestron/Satellier/RG Spectrum | 10.00 | EA |  | 23000.00 | 230000.00 | 2500.00 | 25000.00 | 20010.00 | 200100.00 | 25000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1224.00 | Supply and Laying of 1.5 Metres HDMI patch cord with connectors in existing conduit i/c testing etc. as required. Make-Crestron/Satellier/RG Spectrum | 20.00 | EA |  | 1800.00 | 18000.00 | 2500.00 | 25000.00 | 3035.00 | 30350.00 | 18000.00 | MANNU LAL AND SONS
1225.00 | Supply and Laying of 16 AWG 2 core speaker cable with connectors in existing conduit i/c testing etc. as required. Make-Kramer/Polycab/Beldon | 250.00 | M |  | 1800.00 | 36000.00 | 1200.00 | 24000.00 | 2210.00 | 44200.00 | 24000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1226.00 | Supply and Laying of 24 AWG or better shielded CAT 6 cable with suitable connectors in existing conduit i/c testing etc. as required. Make-Panduit/Legrand/Corning | 500.00 | M |  | 90.00 | 22500.00 | 135.00 | 33750.00 | 145.00 | 36250.00 | 22500.00 | MANNU LAL AND SONS
1227.00 | S/F of network rack of size 19"having 24U for supporting equiments pertaining to sound system with front/rear lockable doors i/c providing caster wheels and all other accessories for easy storation and movement etc. complete as required. Make-VALRACK/APW/RITTAL | 5.00 | EA |  | 115.00 | 57500.00 | 45.00 | 22500.00 | 130.00 | 65000.00 | 22500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1228.00 | SITC of Soundstation SIP-based IP conference phone of tentative dimensions - 36.8 x 31.1 x 6.4 cm (L x W x H) with two (2) Number of microphone of cisco make or equivalent with power of IEEE 802.3af Power over Ethernet (built in), Optional external universal AC power supply: 100-240V, 0.4A, 48V/19W. Display of Size (pixels): 248 x 68 (W x H), White LED backlight with custom intensity control. Keypad - Standard 12-key keypad, Context-dependent soft keys: 3, On-hook/Off-hook, redial, mute, volume up/ down. Audio features Loudspeaker Frequency: 220-14,000 Hz Volume: Adjustable to 86 dB at 1/2 meter peak volume Individual volume settings with visual feedback for each audio path Voice activity detection Comfort noise fill DTMF tone generation / DTMF event RTP payload Low-delay audio packet transmission Adaptive jitter buffers Packet loss concealment Acoustic echo cancellation Background noise suppression Supported Codecs G.711 (A-law and Mu-law) G.729a (Annex B) G.722, G.722.1 G.722.1C Siren 14 complete in all repsect and as directed by Engineer-In-Charge. | 6.00 | NUM |  | 30800.00 | 154000.00 | 32000.00 | 160000.00 | 35880.00 | 179400.00 | 154000.00 | MANNU LAL AND SONS
1229.00 | SITC of Motorize Floor box enclosure with 2Nos power sockets,1Nos HDMI & 1Nos Network Port.Make-Bestnet/MK/Legrand | 12.00 | EA |  | 36000.00 | 216000.00 | 78500.00 | 471000.00 | 48875.00 | 293250.00 | 216000.00 | MANNU LAL AND SONS
1230.00 | SITC of Logitech Group Video Conferencing Bundle with Expansion Mics HD 1080p Camera Speakerphone of minimum dimensions (LxWxH) ‎24.1 x 24.1 x 6.4 Centimeters complete in all respect. | 6.00 | EA |  | 9350.00 | 112200.00 | 8500.00 | 102000.00 | 34500.00 | 414000.00 | 102000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1231.00 | Supplying and laying of RG6 Cable in the existing surface/ recessed steel/ PVC conduit as required. | 100.00 | M |  | 165000.00 | 990000.00 | 35000.00 | 210000.00 | 145410.00 | 872460.00 | 210000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1232.00 | SITC of L2 10/100/1000 MBPS Switch 24 port Non PoE Switch with 2 SFP port,L2 switch with dedicated 24x10/100/1000BaseT PoE RJ45 Ports and 4 SFP Slots of Make Netgear | 2.00 | EA |  | 46.00 | 4600.00 | 55.00 | 5500.00 | 125.00 | 12500.00 | 4600.00 | MANNU LAL AND SONS
1233.00 | SITC of 10 m HDMI Cable | 3.00 | EA |  | 49000.00 | 98000.00 | 55000.00 | 110000.00 | 35880.00 | 71760.00 | 71760.00 | Innovations Workspace Solutions Pvt. Ltd.
1234.00 | SITC of SM SFP Module | 4.00 | EA |  | 2500.00 | 7500.00 | 650.00 | 1950.00 | 11730.00 | 35190.00 | 1950.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1235.00 | Building Management System (BMS)
1236.00 | Software and Operator Workstation
1237.00 | Supply, installation, testing and commissioning of core i7-4790k or Xeon E5-1650 v3 processor, Memory of 32 GB, Hard disk size (2x 800 GB Professional/Enterprise SSD with SATA or SAS), Giga speed Network card with 2 GB Graphic card of Resolution 2.560 x 1600 with Onboard Intel 4600 HD Windows 8.1, 64 bit Edition or Windows Server 2008 R2 and original anti virus software. | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1238.00 | 32 Inch HD Color LED Monitor. | 1.00 | NUM |  | 145000.00 | 145000.00 | 84500.00 | 84500.00 | 154800.00 | 154800.00 | 84500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1239.00 | Laser jet Printer (A4 size, Colour) | 1.00 | NUM |  | 24200.00 | 24200.00 | 22500.00 | 22500.00 | 23400.00 | 23400.00 | 22500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1240.00 | BUILDING MANAGEMENT SYSTEM WEB-BASED SERVER SOFTWARE
1241.00 | Supply, Installation, Testing & Commissioning of software for Building Management Software with features like 3D vector dynamic graphics with Autocad import of plan with Zoom In & Zoom Out facility, Graphic Builder, Plant Viewer, Trend Viewer, Object Viewer, Report Viewer, Alarm router, Log Viewer. The Web-Based Server software shall permit use of Standard Web-Browsers such as Microsoft Internet Explorer, Netscape Navigator, etc. The software shall be capable of integartion third-party systems and should supports latest IP technology (IP V4/V6). The Management Stations shall match the BACnet Profile B-AWS (Advanced workstation) as per the BTL Listing. The Web based software shall include 1 Client License for remote viewing. The same includes the necessary dongles as required for each of the workstation. Number of IO points shall be considered as per the IO summary considering 15% spares. Make:- Siemens/Carrier ALC/Honeywell EBI | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1242.00 | Supply, Installation, Testing & Commissioning of High-quality CAPACTIVE touch 7.0'' panels for technical on-site operation of plants as well as room operation. The Touch Panel shall have integrated web server and a BACnet/ IP web interface to connect a HTML5 browser to a device on the network. Generic operation and monitoring of plant functions (alarms, schedulers, calendars, set point changes, display of actual values, etc.) | 1.00 | NUM |  | 445000.00 | 445000.00 | 1245000.00 | 1245000.00 | 495000.00 | 495000.00 | 445000.00 | MANNU LAL AND SONS
1243.00 | PROGRAMMABLE & APPLICATION SPECIFIC CONTROLLER (DDC) - UL LISTED/BTL certified.
1244.00 | Supply, Installation, Testing & Commissioning of True IP Based Standalone 32 Bit Intelligent, BTL Listed & UL certified interoperable DDC as per the specification. Each DDC Controller shall have inbuilt IP port & shall directly connect to the Network switches (Supervisory Controller/Router/MSTP Controller shall not be acceptable). The DDC shall be Programmable and Application specific with Real Time clock.The Controller shall have minimum 18 onboard points and can be expandable. The DDC must support trending at Controller level. All trend data must be created and saved to the automation station to achieve gap-free trend documentation during communication failure. Make:- Siemens/Carrier ALC/Honeywell Comfort Point
1245.00 | The above shall be housed in IP 55 vandal proof, lockable & secure MS Cabinets to be supplied along with all necessary switchgear protections as required. Number of controllers shall have spare capacity of 15% for future expansion.
1246.00 | Note: 1. System architecture shall be submitted along with submittal. 2. Provision of integration with any BMS system conforming to ASHRAE BACnet/IP Protocol. 3. Additional supervisory/ MSTP/ Router shall not be acceptable.
1247.00 | DDC for Chilled Plant Room | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1248.00 | DDC for Air Handling Units (Max 2 AHU per DDC) | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 63175.00 | 63175.00 | 63175.00 | Innovations Workspace Solutions Pvt. Ltd.
1249.00 | DDC for Ventilations Fans (Max 5 Fan per DDC) | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 622055.00 | 622055.00 | 125000.00 | MANNU LAL AND SONS
1250.00 | DDC for Air Washer & Scrubber Units (Max 2 per DDC) | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 66800.00 | 66800.00 | 66800.00 | Innovations Workspace Solutions Pvt. Ltd.
1251.00 | DDC for DG system/Transformer/HT/LT | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 58095.00 | 58095.00 | 58095.00 | Innovations Workspace Solutions Pvt. Ltd.
1252.00 | DDC for Lifts & Escalators | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 69935.00 | 69935.00 | 69935.00 | Innovations Workspace Solutions Pvt. Ltd.
1253.00 | DDC for Pumps (Max 5 pumps per DDC) | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 66800.00 | 66800.00 | 66800.00 | Innovations Workspace Solutions Pvt. Ltd.
1254.00 | DDC for UG&OH Tanks | 1.00 | SET |  | 170000.00 | 170000.00 | 285000.00 | 285000.00 | 69935.00 | 69935.00 | 69935.00 | Innovations Workspace Solutions Pvt. Ltd.
1255.00 | DDC for Fire Fighting System | 1.00 | SET |  | 125000.00 | 125000.00 | 285000.00 | 285000.00 | 58095.00 | 58095.00 | 58095.00 | Innovations Workspace Solutions Pvt. Ltd.
1256.00 | SYSTEM INTEGRATION UNITS for 3rd party integartions - UL listed Controllers & BTL label
1257.00 | Supply, Installation, Testing & Commissioning of True IP Based System Integration unit consisting of microprocessor based controller units BTL & UL Listed for third party integration. The same should support operations/ monitoring via portable operator terminal. .The controller shall be Native BACnet type with communication via BACnet/LonTalk, Integration platforms and system controllers for third-party devices and systems via KNX, Modbus, M-Bus and other protocols into the automation level via BACnet. The same shall Support operation via local or network-compatible operator units. It should store trend logs and event buffer for a typical duration of up to 30 Days. All the Integrators shall be seperate. Note: 3rd party make integartor shall not be accepted. Make:- Siemens/Carrier ALC/Honeywell Comfort Point
1258.00 | Integartion of Chillers on Modbus Protocol - 20 Points per Chiller | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1259.00 | Integration of Sec. Pumps & Cooling Tower VFDs on Modbus/RS485 - 6 Nos | 1.00 | SET |  | 123000.00 | 123000.00 | 175000.00 | 175000.00 | 63175.00 | 63175.00 | 63175.00 | Innovations Workspace Solutions Pvt. Ltd.
1260.00 | Integartion of AHU VFD on Modbus/RS485 - 46 Nos | 1.00 | SET |  | 85360.00 | 85360.00 | 175000.00 | 175000.00 | 63175.00 | 63175.00 | 63175.00 | Innovations Workspace Solutions Pvt. Ltd.
1261.00 | Integartion of IAQ Monitor on Modbus/RS485(5 Points per device) - 46 Nos | 1.00 | SET |  | 126720.00 | 126720.00 | 175000.00 | 175000.00 | 63175.00 | 63175.00 | 63175.00 | Innovations Workspace Solutions Pvt. Ltd.
1262.00 | Integartion of UPS on Modbus/RS485 or Bacnet/IP Protocol - 15 Points | 1.00 | SET |  | 126720.00 | 126720.00 | 175000.00 | 175000.00 | 55415.00 | 55415.00 | 55415.00 | Innovations Workspace Solutions Pvt. Ltd.
1263.00 | Integartion of DG on Modbus/RS 485 Communication Port - 20 Points per DG | 1.00 | SET |  | 147400.00 | 147400.00 | 175000.00 | 175000.00 | 55415.00 | 55415.00 | 55415.00 | Innovations Workspace Solutions Pvt. Ltd.
1264.00 | Integartion of MFM, Energy Meters to be on Modbus RTU with RS 485 Communication Port - 10 Points per Meter (25 Nos Meters) | 1.00 | SET |  | 147400.00 | 147400.00 | 175000.00 | 175000.00 | 36945.00 | 36945.00 | 36945.00 | Innovations Workspace Solutions Pvt. Ltd.
1265.00 | Integartion of HT Panel Demand Power Meter to be on Modbus RTU with RS 485 Communication Port | 1.00 | SET |  | 138000.00 | 138000.00 | 175000.00 | 175000.00 | 36945.00 | 36945.00 | 36945.00 | Innovations Workspace Solutions Pvt. Ltd.
1266.00 | Integartions of Lifts on Modbus or Bacnet/IP Protocol - 16 Nos | 1.00 | SET |  | 112000.00 | 112000.00 | 175000.00 | 175000.00 | 36945.00 | 36945.00 | 36945.00 | Innovations Workspace Solutions Pvt. Ltd.
1267.00 | Integartion of Plumbing PLC on Modbus RTU with RS 485 Communication Port - 100 Points | 1.00 | SET |  | 94000.00 | 94000.00 | 175000.00 | 175000.00 | 55415.00 | 55415.00 | 55415.00 | Innovations Workspace Solutions Pvt. Ltd.
1268.00 | Field instruments
1269.00 | Supplying, installing, testing and commissioning of the following sensors / transducers / transmitters.
1270.00 | Supply, Installation, Testing & Commissioning of Immersion temperature sensor 100 mm Pt1000 with Brass Thermowell. | 8.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1271.00 | Supply, Installation, Testing & Commissioning of Outside air temperature + humidity sensors for measuring outside air temperature. It should be provided with sun sheild and rain protection. | 1.00 | NUM |  | 3740.00 | 29920.00 | 28450.00 | 227600.00 | 4455.00 | 35640.00 | 29920.00 | MANNU LAL AND SONS
1272.00 | Supply, Installation, Testing & Commissioning of In line Type Electromagnetic Water Flow Meter - Dia Size 350 mm | 1.00 | NUM |  | 15950.00 | 15950.00 | 12544.00 | 12544.00 | 21075.00 | 21075.00 | 12544.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1273.00 | Supply, Installation, Testing & Commissioning of Differential Pressure Switch Water | 4.00 | NUM |  | 100000.00 | 100000.00 | 35400.00 | 35400.00 | 245160.00 | 245160.00 | 35400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1274.00 | Supply, Installation, Testing & Commissioning of Single Level Switch | 3.00 | NUM |  | 15000.00 | 60000.00 | 12400.00 | 49600.00 | 8155.00 | 32620.00 | 32620.00 | Innovations Workspace Solutions Pvt. Ltd.
1275.00 | Supply, Installation, Testing & Commissioning of PH Analyser | 1.00 | NUM |  | 4500.00 | 13500.00 | 16500.00 | 49500.00 | 12510.00 | 37530.00 | 13500.00 | MANNU LAL AND SONS
1276.00 | Supply, Installation, Testing & Commissioning of TDS Analyser | 1.00 | NUM |  | 10500.00 | 10500.00 | 58400.00 | 58400.00 | 12600.00 | 12600.00 | 10500.00 | MANNU LAL AND SONS
1277.00 | Supply, Installation, Testing & Commissioning of Current Relay for Run Status | 38.00 | NUM |  | 29000.00 | 29000.00 | 58400.00 | 58400.00 | 30480.00 | 30480.00 | 29000.00 | MANNU LAL AND SONS
1278.00 | Supply, Installation, Testing & Commissioning of Differential pressure switch Filter Status (Pa Range 50...500 Pa) | 12.00 | NUM |  | 2600.00 | 98800.00 | 8544.00 | 324672.00 | 2795.00 | 106210.00 | 98800.00 | MANNU LAL AND SONS
1279.00 | Supply, Installation, Testing & Commissioning of Duct sensor for humidity (0...10 V) and temperature (Ni1000). | 12.00 | NUM |  | 15000.00 | 180000.00 | 6500.00 | 78000.00 | 3120.00 | 37440.00 | 37440.00 | Innovations Workspace Solutions Pvt. Ltd.
1280.00 | Supply, Installation, Testing & Commissioning of IAQ Monitor PM2.5, CO2, TVOC,Temp,Humidity Level | 46.00 | NUM |  | 13000.00 | 156000.00 | 6500.00 | 78000.00 | 7685.00 | 92220.00 | 78000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1281.00 | Supply, Installation, Testing & Commissioning of Carbon Monoxide Sensor for Basement. (Range 0 to 300 ppm) | 12.00 | NUM |  | 18000.00 | 828000.00 | 8655.00 | 398130.00 | 53260.00 | 2449960.00 | 398130.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1282.00 | Supply, Installation, Testing & Commissioning of Flameproof Level Sensor | 6.00 | NUM |  | 13000.00 | 156000.00 | 12544.00 | 150528.00 | 9505.00 | 114060.00 | 114060.00 | Innovations Workspace Solutions Pvt. Ltd.
1283.00 | Supply, Installation, Testing & Commissioning of Voltage Transducer | 2.00 | NUM |  | 12000.00 | 72000.00 | 14320.00 | 85920.00 | 24625.00 | 147750.00 | 72000.00 | MANNU LAL AND SONS
1284.00 | Supply, Installation, Testing & Commissioning of Bi Level Switch | 10.00 | NUM |  | 25000.00 | 50000.00 | 8560.00 | 17120.00 | 3430.00 | 6860.00 | 6860.00 | Innovations Workspace Solutions Pvt. Ltd.
1285.00 | Supply, Installation, Testing & Commissioning of Pressure sensor for neutral and slightly aggressive liquids. | 2.00 | NUM |  | 7000.00 | 70000.00 | 13500.00 | 135000.00 | 12510.00 | 125100.00 | 70000.00 | MANNU LAL AND SONS
1286.00 | Cabling and Conduiting
1287.00 | Supplying, laying, termination, testing and commissioning of 2 Core x 1.0 sq mm PVC insulated, Annealed Tinned Copper, twisted, shielded, unarmoured FRLS cable. | 6500.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1288.00 | Supplying, laying, termination, testing and commissioning of 3 Core 1.5 Sqmm, unarmoured ATC conductor multistranded, FRLS cable for Powering DDC , Actuators. | 1500.00 | M |  | 72.00 | 468000.00 | 115.00 | 747500.00 | 45.00 | 292500.00 | 292500.00 | Innovations Workspace Solutions Pvt. Ltd.
1289.00 | Fire Suppression System (FSS)
1290.00 | FIRE SUPPRESSION SYSTEM
1291.00 | For Electrical Panels & Transformer Supression. Make-Siemens/Supremex/Tyco
1292.00 | Supply, Installation, Testing and commissioning of 10 LB capacity Novec 1230, DLP Assembly with automatic value, push in connector for tube, 10 LB Novec 1230 gas mounting bracket, End of Line adopter and low pressure switch for monitoring system activation. | 4.00 | EA |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1293.00 | Supply, Installation, Testing and commissioning of 14 LB capacity Novec 1230, DLP Assembly with automatic value, push in connector for tube, 14 LB Novec 1230 gas mounting bracket, End of Line adopter and low pressure switch for monitoring system activation. | 3.00 | EA |  | 158700.00 | 634800.00 | 80000.00 | 320000.00 | 117600.00 | 470400.00 | 320000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1294.00 | Supply, Installation, Testing and commissioning of Fire Liner pneumatic heat Detection Tube with all necessary fitting & Supports | 338.00 | M |  | 225400.00 | 676200.00 | 85000.00 | 255000.00 | 132000.00 | 396000.00 | 255000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1295.00 | Supply, Installation, Testing and commissioning of Master Control Unit for controlling each system complete with pressure Swithes, buzzers and electronic hooters, Audio Visual Alarm including all necessary accessories + electrical wiring to make each entire system functional. | 7.00 | EA |  | 2323.00 | 785174.00 | 2454.00 | 829452.00 | 1190.00 | 402220.00 | 402220.00 | Innovations Workspace Solutions Pvt. Ltd.
1296.00 | Supply, Installation, Testing and commissioning of Discharge Hose With Two nozzle Kit. | 7.00 | EA |  | 6325.00 | 44275.00 | 30000.00 | 210000.00 | 7800.00 | 54600.00 | 44275.00 | MANNU LAL AND SONS
1297.00 | HIGH PRESSURE CYLINDER OF NOVEC 1230 AGENT COMPLETE WITH VALVE ASSEMBLY, STANDARD ACCESSORIES CAPACITY - 80 LTR | 1.00 | NUM |  | 4485.00 | 31395.00 | 15000.00 | 105000.00 | 35400.00 | 247800.00 | 31395.00 | MANNU LAL AND SONS
1298.00 | NOVEC 1230 GAS | 68.00 | KG |  | 112700.00 | 112700.00 | 100000.00 | 100000.00 | 175000.00 | 175000.00 | 100000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1299.00 | Solenoid Actuator Assembley 24 v DC | 1.00 | NUM |  | 4370.00 | 297160.00 | 250.00 | 17000.00 | 3500.00 | 238000.00 | 17000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1300.00 | Manually operated actuator | 1.00 | NUM |  | 5060.00 | 5060.00 | 10000.00 | 10000.00 | 3165.00 | 3165.00 | 3165.00 | Innovations Workspace Solutions Pvt. Ltd.
1301.00 | High pressure flexible rubber discharge hose | 1.00 | NUM |  | 18975.00 | 18975.00 | 7000.00 | 7000.00 | 3250.00 | 3250.00 | 3250.00 | Innovations Workspace Solutions Pvt. Ltd.
1302.00 | Cylinder Straps | 2.00 | NUM |  | 6095.00 | 6095.00 | 4000.00 | 4000.00 | 18125.00 | 18125.00 | 4000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1303.00 | Pressure Gauge | 1.00 | NUM |  | 5520.00 | 11040.00 | 750.00 | 1500.00 | 2440.00 | 4880.00 | 1500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1304.00 | Manual gas release Switch | 1.00 | NUM |  | 3795.00 | 3795.00 | 1200.00 | 1200.00 | 3125.00 | 3125.00 | 1200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1305.00 | Manual gas abort Switch | 1.00 | NUM |  | 2128.00 | 2128.00 | 800.00 | 800.00 | 1565.00 | 1565.00 | 800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1306.00 | Conventional Hooter cum Flasher | 1.00 | NUM |  | 2128.00 | 2128.00 | 750.00 | 750.00 | 1565.00 | 1565.00 | 750.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1307.00 | Discharge Nozzle | 2.00 | NUM |  | 3220.00 | 3220.00 | 2530.00 | 2530.00 | 2315.00 | 2315.00 | 2315.00 | Innovations Workspace Solutions Pvt. Ltd.
1308.00 | Discharge Pressure switch | 1.00 | NUM |  | 7130.00 | 14260.00 | 1300.00 | 2600.00 | 9375.00 | 18750.00 | 2600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1309.00 | Hydraulic Flow calculation | 1.00 | NUM |  | 4577.00 | 4577.00 | 2700.00 | 2700.00 | 7400.00 | 7400.00 | 2700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1310.00 | Multisensor Detector | 4.00 | NUM |  | 8970.00 | 8970.00 | 2500.00 | 2500.00 | 18750.00 | 18750.00 | 2500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1311.00 | Warning Sign Sticker | 1.00 | NUM |  | 3048.00 | 12192.00 | 1100.00 | 4400.00 | 565.00 | 2260.00 | 2260.00 | Innovations Workspace Solutions Pvt. Ltd.
1312.00 | 2 Zone Single Area Gas Release Panel . | 1.00 | NUM |  | 4025.00 | 4025.00 | 300.00 | 300.00 | 315.00 | 315.00 | 300.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1313.00 | Supply of M.S. Seamless pipes as per ASTM A 106 Gr. B, schedule 40 with necessary fittings. | 1.00 | SET |  | 6210.00 | 6210.00 | 100000.00 | 100000.00 | 10035.00 | 10035.00 | 6210.00 | MANNU LAL AND SONS
1314.00 | Supply of PVC insulated , PVC sheathed, FRLS Fire survival Copper armoured aluminium conductor of cable as per IS 1554- Part- I of size 2x1.5 sq. mm . | 60.00 | M |  | 25300.00 | 25300.00 | 30000.00 | 30000.00 | 62500.00 | 62500.00 | 25300.00 | MANNU LAL AND SONS
1315.00 | HVAC WORK
1316.00 | All technical data of capacity, head, RPM, etc. are indicative and shoulb be compatible with the HVAC Chiller system to achieve the required capacity. Bidders may take the note of the same while quoting.
1317.00 | SUB-HEAD-I: EQUIPMENT
1318.00 | Water Cooled Screw Water Chilling Machine | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1319.00 | Supply, installation, testing & commissioning of water cooled Screw type Single/ Multiple number Compressor chilling machines of Actual capacity at below mentioned operating tender conditions, comprising of direct driven screw type helical rotary compressor and refrigerant circuit/s, having soft/star-delta starter, insulated shell and tube flooded chiller, Shell & tube condenser, ribbed rubber pads for vibration isolation, integral refrigerant piping and wiring,factory charged ozone friendly R-134a refrigerant and compressor oil charge, grooved Victaulic Couplings with spool piece for condenser and chilled water IN/OUT connections, flow switch at chiller & condenser,accessories as required and as called for ,automatic and safety controls mounted in central micro-processor based console panel and all mounted on a steel frame complete as per specifications. The motor shall be suitable for 415 + 10% Volts, 50 Hz, 3 Phase, AC power supply. Chiller shall be factory tested at design conditions at 100%, 75%, 50% and 25% load. Chiller shall have Minimum COP of 5.2 as per AHRI conditions.
1320.00 | General notes for compliance:
1321.00 | Minimum Unloading step : 10%
1322.00 | Evaluation of power consumption shall be done on the basis of NPLV.
1323.00 | Machine shall be equipped with screw single/multiple compressors and Single/Multiple Circuits.
1324.00 | Shell and tube water cooled condenser having max. two passes and constructed of M.S. shell and both side integrally finned copper tubes and pressure drop 5.5 mtr max
1325.00 | Shell & tube flooded type chiller having max. two passes and constructed of MS shell and both side integrally finned copper tubes and pressure drop 5.5 mtr max.
1326.00 | Microprocessor based control panel with graphical/ alphanumeric touch screen display shall have suitable hardware, software and BMS Card so that it can be integrated directly to with standard communication open protocol using Backnet or Modbus IP.
1327.00 | Flow Switches for condenser & chiller, water drain & air purge valves wherever required.
1328.00 | Lot- Initial/ first charge of refrigerant gas & compressor oil duly charged at manufacturing facility.
1329.00 | Software selection sheet in accordance with AHRI 550-590 std rated at site parameters shall be submitted along with the offer.
1330.00 | Only one no. INPUT power supply(Aluminium conductor Armoured cable of suitable run/s) shall be provided at each chiller from HVAC main panel. Chiller vendor to include the cost of adopter box (including output cables from the adopter box to chiller control panel)for bifurcation of power supply in case of dual power input chillers OR for termination of flexible copper conductor cables from the adopter box to their microprocessor panel.
1331.00 | Performance shall be guaranteed for the following parameters:
1332.00 | Condenser:
1333.00 | Condenser water Leaving Temp: 36.1° C (97° F)
1334.00 | Condenser water Entering Temp : 30.6° C (87° F)
1335.00 | Condenser fouling factor : 0.001 (FPS units )
1336.00 | Flow rate:375 USGPM- 390 US GPM
1337.00 | Chiller:
1338.00 | Chilled water Leaving Temp: 7° C (44.6° F)
1339.00 | Chilled water Entering Temp : 12° C (53.6° F )
1340.00 | Chiller fouling factor : 0.0005 (FPS units )
1341.00 | Flow rate: 300USGPM- 312 US GPM
1342.00 | Water cooled Screw chilling machine as described above having a actual capacity of 125TR-130TR at above duty conditions. (Quantity Includes 1 No. standby)
1343.00 | Note: Preferably, 130 TR capacity machine shall be equipped with screw (Twin Type) multiple compressors having independent refrigerant Circuits.
1344.00 | The price quoted for Rotary Screw Water Chilling Unit shall be inclusive of all duties & taxes, insurance, transportation / shipment cost from works to site, loading / unloading,shifting the chillers and placing them on the foundations/designated place, port clearance charges etc. as required in INR.
1345.00 | Water Circulation Chilled & Condenser Pumps
1346.00 | Condenser Water Pumps Set (Constant speed) | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1347.00 | Supply, installation, testing and commissioning of single stage centrifugal split close coupled Vertical Inline condenser water pump sets having in-line suction and discharge ports of identical diameter OR single stage centrifugal split casing long coupled end suction condenser water pumps, made of CI casing with bronze impeller & SS shaft for condenser water recirculation complete with TEFC Sq. Cage induction IE-2 motor with class "F" insulation, coupling guard, factory fitted mechanical seal, conforming to technical specifications as called for. Vertical Pump shall be of top pull out design and Horizontal pump shall be of back pull out design and its motor shall be suitable for operating on adjustable frequency drive.Pump shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply and shall run on 1400 RPM.Performance characteristics shall be as given below.
1348.00 | Capacity of Each Pump : 375 US GPM - 390 US GPM (Each)
1349.00 | Pump Head : 27.5 M (90 ft)
1350.00 | Motor : 11.0 KW (15 HP)
1351.00 | Pumps shall have efficiency above 70% and close to 75%
1352.00 | Quantity indicated include one stand by
1353.00 | Primary Chilled Water Pumps (Constant speed) | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1354.00 | Supply, installation, testing and commissioning of single stage centrifugal split close coupled Vertical Inline chilled water pump sets having in-line suction and discharge ports of identical diameter OR single stage centrifugal split casing long coupled end suction chilled water pumps, made of CI casing with bronze impeller & SS shaft for chilled water recirculation complete with TEFC Sq. Cage induction IE-2 motor with class "F" insulation, coupling guard, factory fitted mechanical seal, conforming to technical specifications as called for. Vertical Pump shall be of top pull out design and Horizontal pump shall be of back pull out design and its motor shall be suitable for operating on adjustable frequency drive.Pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply and shall run on 1400 RPM-1500 RPM.The quoted price shall include cost of thermal insulation and cladding.Performance characteristics shall be as given below.
1355.00 | Capacity of Each Pump : 300 US GPM-325 USGPM (Each)
1356.00 | Pump Head : 12.2 M (40 ft)
1357.00 | Motor : 5.5 KW (7.5 HP)
1358.00 | Pumps shall have efficiency above 70% and close to 75%
1359.00 | Quantity indicated include one stand by
1360.00 | Secondary Chilled Water Pumps | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1361.00 | Supply, installation, testing and commissioning of single stage centrifugal split close coupled Vertical Inline chilled water pump sets having in-line suction and discharge ports of identical diameter OR single stage centrifugal split casing long coupled end suction chilled water pumps, made of CI casing with bronze impeller & SS shaft for chilled water recirculation complete with TEFC Sq. Cage induction IE-2 motor with class "F" insulation, coupling guard, factory fitted mechanical seal, conforming to technical specifications as called for. Vertical Pump shall be of top pull out design and Horizontal pump shall be of back pull out design and its motor shall be suitable for operating on adjustable frequency drive and conforming to the specifications of variable pumping system.VFD for secondary pumps shall preferably be mounted on the body of the pump itself.Pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply and shall run on 1400 RPM -1500 RPM.The quoted price shall include cost of thermal insulation and cladding.Performance characteristics shall be as given below.
1362.00 | Single Zone(Office building)
1363.00 | Capacity of Each Pump : 320 US GPM (Each)
1364.00 | Pump Head : (110 ft) 33.5 M
1365.00 | Motor : (15.0 HP) 11.0 KW
1366.00 | Pumps shall have efficiency above 70% and close to 75%
1367.00 | Quantity indicated include one stand by
1368.00 | Variable Speed Pumping System (Secondary Chilled Water Pumps) | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1369.00 | Supply, installation, testing and commissioning of Variable Speed Pumping system consisting of adjustable frequency drive (AFD) for each pump suitably interfaced with other system components, hand / auto macro designed for pumping application,1 no. dedicated microprocessor based pump logic controller per zone, parallel pumping software duly downloaded, single/multiple differential pressure sensor /transmitters as per the site requirement, interfacing amongst all components and compatibility of I/O signals etc complete with other accessories as required.The entire system along with secondary pumps to be sourced from single manufacturer only, to ensure unit responsibility. Necessary factory test certificates for entire system shall be submitted along with the equipment. System shall be BMS compatible with open protocol communication port, so that complete data can be transported to remote IBMS console. Vendor to include cost of panel/enclosure to house the VFDs (if supplied seperatly) and logic controller with necessary set of ON/OFF indicating lights, input MCCBs and adequate arrangement of ventilation including all related control/communication wiring between logic controller,VFDs and differential pressure sensors.
1370.00 | The system shall be complete in all respects and suitable for following motor ratings :
1371.00 | Supply of AFD , Pump controller & Sensor transmitters
1372.00 | Single Zone (Office building),Motor KW : 11.0 KW (15.0 HP) (2W+1SB)….3nos.
1373.00 | Note: There will be 1no. of independent enclosure for above set of VFDs & Logic controllers.
1374.00 | FRP Induced Draft Cooling Tower | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1375.00 | Supply, installation, testing and commissioning of FRP construction induced draft Single cell cross/counter flow type Cooling towers for Airconditioning system. Each tower shall be complete with FRP cold water basin, honeycomb design PVC fill, Casing, Hot water distribution system, Intake louvers,ladder, Axial flow fan with statically/dynamically balanced belt & pully drive/directly coupled with TEFC, EFF-1 Class F Insulation, IP65 induction motor suitable for 415±10% volts, 50 Hz, 3 phase power supply, Weather proof Isolator panel with MCCB at cooling tower and earthing.Cooling tower motor/s shall be suitable for operating on adjustable frequency drive.Basin shall be provided with accessories like quickfill, makeup & drain, brass construction float valve, overflow pipe etc. Separate motor shall be provided in each cell of multi cell towers. It shall have non-corrosive structure and casing for longer life of all componenets.Tower shall be selected on the basis detailed in the schedule. Tower shall be suitable for outdoor installation next to occupied areas and shall be low noise. Cooling tower shall be CTI certified.Vendor to include the cost of Variable frequency drive(DANFOSS FC-102/Equivalent) of 5.5 KW X 1 no. rating. considering Single cell cooling tower OR as per the motor kw suggested by the tower manufacturer.VFD shall be BMS compatible ,IP-20 rating and shall have in built choke to cater for the longer length of power cabling (Approx. 60 Rmt for each CT fan motor) without deration in the performance of the VFD.
1376.00 | Duty Parameters
1377.00 | Cooling tower capacity shall be suitable for 125TR-130 TR capacity chillers heat rejection.
1378.00 | Water Flow - 375 USGPM - 390 USGPM
1379.00 | Designed Wet Bulb Temperature - 80 °F
1380.00 | Approach : 7 °F
1381.00 | Water Inlet Temperature - 97 °F (36.1 Deg C)
1382.00 | Water Outlet Temperature - 87 °F (30.5 DegC)
1383.00 | Quantity indicated include one stand by
1384.00 | Pressurized Closed Expansion Tank with Air Seperator | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1385.00 | Supply,Installation, Testing & Commissioning of pressurised expansion tank in chilled water circuits along with necessary accessories such as centrifugal air separator, pumps(including one standby) piping, valves, strainers etc. in order to keep chilled water system under pressure and to prevent entrapment of air in the system. The tank shall be precharged steel expansion tank with replaceable heavy duty butyl rubber bladder. The tank shall have suitably sized system connection, PN 16 rated, drain and charging valve connection to facilitate the on site charging of the tank to meet system requirement. The tank and air separator must be constructed in accordance with section VIII of the ASME Boiler and pressure vessel code. The complete system shall be sourced from single manufacturer and supplied and installed with all accessories and safety fixtures required for proper functioning of the complete hydronic system.
1386.00 | Supply, Installation, Testing & Commissioning of above tank, air separator and all accessories as required
1387.00 | Approximate system volume 20000 ltr at Max ambient temp 40Deg C and total Static height above the expansion tank 30 M. MinimumTank capacity shall be 500 litres.Vendor to include cost of thermal insulation with 44mm thick closed cell elastomeric insulation and finally finished with 24G Aluminium cladding for the expansion tank & Air seperator both.
1388.00 | Supply, Installation, Testing & Commissioning of above tank, and all accessories as required. Tank shall be common i.e suitable for either cooling during summer OR heating during winters.
1389.00 | NOTE:Air seperator selected shall be suitable to 150mm dia pipe connection at Inlet & out let with inbuilt strainer/sediment seperator.
1390.00 | The contractor shall submit calculations for the total system volume and tank sizing calculations along with their offer.
1391.00 | AHU's AND THEIR CONTROLS
1392.00 | Double Skin Floor/Ceiling Mounted AHU With Pre Filters + Fine filters (2 pipe system)
1393.00 | Supply, installation, testing and commissioning of double skin construction Horizontal/Vertical Floor/Ceiling mounted(as per approved shop drawing and specifications) draw/blow through type chilled water Air handling units fabricated out of extruded aluminium section with 0.6 mm pre-plasticized / pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside; each complete with 600mm deep mixing box wherever specified, low leakage aluminium aerofoil gear driven VCD & fire resistant neoprene flexible connection at outlet, pre-filter section with 50mm thick filters of non woven synthetic media (efficiency 90% down to 10 microns MERV-8) , fine filter section with 300mm thick fine filters of non woven synthetic media (efficiency 95% down to 3 microns MERV-13),coil section having min 6 Row Deep (8 Row Deep in case of TFA) chilled water coil of copper tube & aluminium fins construction alongwith di- electric union of suitable size (Coil shall have copper header),polished SS 304 drain pan made out of 20G sheet duly insulated, complete with squirrel cage induction VFD Compatible motor.
1394.00 | Belt driven DIDWcentrifugal Backward curved fan(or equivalent performance direct driven plug fan) with vibration isolators. Coil size shall be selected for a maximum face velocity of 500 feet/minute and fan outlet velocity shall be limited to 1800 FPM. Motor shall be atleast IE 2 rated suitable for 415±10% volts, 50 cycles, 3 phase AC supply, meeting criterion as per ASHRAE standard 90.1-2010 & high efficiency. The AHU panels shall be insulated with minimum 23 mm thick (for recirculated AHU) & 46mm thick for (TFA AHU) & 40± 2 Kg/m³ density PU foam & shall have thermal break. The motor & blower assembly shall be mounted on Aluminium extruded section only.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication.Fan capacities shall be based on minimum 60mm static pressure for ceiling mounted AHUs as mentioned below.The AHUs shall be complete in all respects along with accessories as per specifications. The capacity of Air-handlers shall be as follows:
1395.00 | Floor GF-01 Area Office Block Type Horizontal FM Fan Dia in mm 630 Air qty CFM 10250 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 17 Mixing Box 1 No. | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1396.00 | Floor GF-02 Area Staff cafeteria Type Horizontal FM Fan Dia in mm 450 Air qty CFM 5000 SP in mm 60 Motor kW 2.2 Coil Row 6 TR 10 Mixing Box 1 No. | 1.00 | NUM |  | 448500.00 | 448500.00 | 461250.00 | 461250.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1397.00 | Floor 1F-03 Area Office Block Type Horizontal FM Fan Dia in mm 630 Air qty CFM 10500 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 18 Mixing Box 1 No. | 1.00 | NUM |  | 261500.00 | 261500.00 | 225000.00 | 225000.00 | 205275.00 | 205275.00 | 205275.00 | Innovations Workspace Solutions Pvt. Ltd.
1398.00 | Floor 1F-04 Area Office Block Type Horizontal FM Fan Dia in mm 450 Air qty CFM 5500 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 10.5 Mixing Box 1 No. | 1.00 | NUM |  | 448500.00 | 448500.00 | 472500.00 | 472500.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1399.00 | Floor 2F-05 Area Office Block Type Horizontal FM Fan Dia in mm 560 Air qty CFM 10000 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 17 Mixing Box 1 No. | 1.00 | NUM |  | 225400.00 | 225400.00 | 247500.00 | 247500.00 | 205275.00 | 205275.00 | 205275.00 | Innovations Workspace Solutions Pvt. Ltd.
1400.00 | Floor 2F-06 Area Office Block Type Horizontal FM Fan Dia in mm 450 Air qty CFM 5800 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 10.2 Mixing Box 1 No. | 1.00 | NUM |  | 419500.00 | 419500.00 | 450000.00 | 450000.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1401.00 | Floor 3F-07 Area Office Block Type Horizontal FM Fan Dia in mm 560 Air qty CFM 10000 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 17 Mixing Box 1 No. | 1.00 | NUM |  | 248200.00 | 248200.00 | 261000.00 | 261000.00 | 205275.00 | 205275.00 | 205275.00 | Innovations Workspace Solutions Pvt. Ltd.
1402.00 | Floor 3F-08 Area Office Block Type Horizontal FM Fan Dia in mm 450 Air qty CFM 5800 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 10.2 Mixing Box 1 No. | 1.00 | NUM |  | 419500.00 | 419500.00 | 450000.00 | 450000.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1403.00 | Floor 4F-09 Area Office Block Type Horizontal FM Fan Dia in mm 630 Air qty CFM 10500 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 18 Mixing Box 1 No. | 1.00 | NUM |  | 293800.00 | 293800.00 | 261000.00 | 261000.00 | 205275.00 | 205275.00 | 205275.00 | Innovations Workspace Solutions Pvt. Ltd.
1404.00 | Floor 4F-10 Area Office Block Type Horizontal FM Fan Dia in mm 450 Air qty CFM 5800 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 10.2 Mixing Box 1 No. | 1.00 | NUM |  | 448500.00 | 448500.00 | 472500.00 | 472500.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1405.00 | Floor 5F-11 Area Office Block Type Horizontal FM Fan Dia in mm 560 Air qty CFM 10000 SP in mm 60 Motor kW 5.5 Coil Row 6 TR 17 Mixing Box 1 No. | 1.00 | NUM |  | 293800.00 | 293800.00 | 261000.00 | 261000.00 | 205275.00 | 205275.00 | 205275.00 | Innovations Workspace Solutions Pvt. Ltd.
1406.00 | Floor 5F-12 Area Office Block Type Horizontal FM Fan Dia in mm 450 Air qty CFM 6300 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 11.5 Mixing Box 1 No. | 1.00 | NUM |  | 438600.00 | 438600.00 | 450000.00 | 450000.00 | 415275.00 | 415275.00 | 415275.00 | Innovations Workspace Solutions Pvt. Ltd.
1407.00 | Floor 6F-13 Area Office Block Type Horizontal FM Fan Dia in mm 560 Air qty CFM 8000 SP in mm 60 Motor kW 3.7 Coil Row 6 TR 13.5 Mixing Box 1 No. | 1.00 | NUM |  | 310500.00 | 310500.00 | 283000.00 | 283000.00 | 257775.00 | 257775.00 | 257775.00 | Innovations Workspace Solutions Pvt. Ltd.
1408.00 | Floor 6F-14 Area Office Block Type Horizontal FM Fan Dia in mm 355 Air qty CFM 4000 SP in mm 60 Motor kW 2.2 Coil Row 6 TR 7.5 Mixing Box 1 No. | 1.00 | NUM |  | 358600.00 | 358600.00 | 360000.00 | 360000.00 | 341775.00 | 341775.00 | 341775.00 | Innovations Workspace Solutions Pvt. Ltd.
1409.00 | Double Skin Floor/Ceiling Mounted AHU With Pre Filters only (2 pipe system)
1410.00 | Supply, installation, testing and commissioning of double skin construction Horizontal/Vertical Floor/Ceiling mounted(as per approved shop drawing and specifications) draw/blow through type chilled water Air handling units fabricated out of extruded aluminium section with 0.6 mm pre-plasticized / pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside; each complete with 600 mm deep mixing box wherever specified, low leakage aluminium aerofoil gear driven VCD & fire resistant neoprene flexible connection at outlet, pre-filter section with 50mm thick filters of non woven synthetic media (efficiency 90% down to 10 microns MERV-8) ,coil section having min 6 Row Deep (8 Row Deep in case of TFA) chilled water coil of copper tube & aluminium fins construction alongwith di- electric union of suitable size (Coil shall have copper header),polished SS 304 drain pan made out of 20G sheet duly insulated, complete with squirrel cage induction VFD Compatible motor.
1411.00 | Belt driven DIDW centrifugal Backward curved fan (or Equivalent performance direct driven plug fan) with vibration isolators. Coil size shall be selected for a maximum face velocity of 500 feet/minute and fan outlet velocity shall be limited to 1800 FPM. Motor shall be atleast IE 2 rated suitable for 415±10% volts, 50 cycles, 3 phase AC supply, meeting criterion as per ASHRAE standard 90.1-2010 & high efficiency. The AHU panels shall be insulated with minimum 23 mm thick (for recirculated AHU) & 46mm thick for (TFA AHU) & 40± 2 Kg/m³ density PU foam & shall have thermal break. The motor & blower assembly shall be mounted on Aluminium extruded section only.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication.Fan capacities shall be based on minimum 40mm static pressure for floor mounted AHUs and minimum 35mm static pressure for ceiling mounted AHUs as mentioned below.The AHUs shall be complete in all respects along with accessories as per specifications. The capacity of Air-handlers shall be as follows:
1412.00 | Note - Vertical floor mounted AHU for UPS & Server room shall have Inbuilt discharge plenum of 600mm height of same foot print of AHU along with 450mm wide openable plenum for Valve station (To conceal the CHW valves & piping) in double skin construction. Vendor to include the cost of the same.
1413.00 | Floor 1F-15 Area UPS Room Type CSU Fan Dia in mm 315 Air qty CFM 3200 SP in mm 35 Motor kW 1.1 Coil Row 6 TR 5.5 Mixing Box 1 No. | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1414.00 | Floor 1F-16 Area UPS Room Type Vertical floor mounted Fan Dia in mm 315 Air qty CFM 3200 SP in mm 32 Motor kW 1.1 Coil Row 6 TR 5.5 Mixing Box 1 No. | 1.00 | NUM |  | 164000.00 | 164000.00 | 144000.00 | 144000.00 | 174090.00 | 174090.00 | 144000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1415.00 | Floor 1F-17 Area Server Room Type CSU Fan Dia in mm 355 Air qty CFM 3500 SP in mm 35 Motor kW 1.1 Coil Row 6 TR 6 Mixing Box 1 No. | 1.00 | NUM |  | 164000.00 | 164000.00 | 144000.00 | 144000.00 | 174090.00 | 174090.00 | 144000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1416.00 | Floor 1F-18 Area Server Room Type Vertical floor mounted Fan Dia in mm 355 Air qty CFM 3500 SP in mm 32 Motor kW 1.1 Coil Row 6 TR 6 Mixing Box 1 No. | 1.00 | NUM |  | 178700.00 | 178700.00 | 157500.00 | 157500.00 | 188685.00 | 188685.00 | 157500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1417.00 | Floor 6F-19&20 Area Conference Room Type CSU Fan Dia in mm 280 Air qty CFM 2500 SP in mm 32 Motor kW 1.1 Coil Row 6 TR 5 Mixing Box 2 No. | 1.00 | NUM |  | 178700.00 | 178700.00 | 157000.00 | 157000.00 | 188685.00 | 188685.00 | 157000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1418.00 | Floor UB-21 Area LT Panel Room Type Horizontal FM Fan Dia in mm 250 Air qty CFM 2000 SP in mm 40 Motor kW 1.1 Coil Row 6 TR 5 Mixing Box 1 No. | 1.00 | NUM |  | 146500.00 | 146500.00 | 112500.00 | 112500.00 | 143955.00 | 143955.00 | 112500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1419.00 | Fan Coil Unit (High Static) Suitable for 2 pipe system for BOH & Public areas
1420.00 | Supply,installation,testing and commissioning of Horizontal blow through type fan coil units (having 5 mm external static pressure) each complete with fan section having one or more centrifugal fans,minimum 3 row deep chilled water coil, normal three speed motor, washable fabric filters, sandwitched insulated extended drain pan,25mm dia flexible braided drain pipe of 300mm length with clamps, copper pipe connections with brass fittings, wiring with 3 pin switch,socket and plug mounted on M.S. box, wiring in MS rigid/GI flexible conduits as required including wall chasing & finishing upto the thermostat boxes, fire retardant flexible duct connections made of silicon/neoprene rubber with extruded aluminium frame, fan coil unit shall be suitable for 240 ± 10% volts, 50 Hz cycle single phase power supply, maximum RPM of motor shall be 960. The price shall include rubber in shear supporting arrangement and rubber gromets as required. Fan coil units shall be of following refrigeration capacities :
1421.00 | Note: Internal Fan speed connections shall be factory wired from motor upto a connector box installed on the FCU body.
1422.00 | 1.0 TR nominal capacity --- 400 CFM | 7.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1423.00 | 1.5 TR nominal capacity ---- 600 CFM | 24.00 | NUM |  | 17200.00 | 120400.00 | 34538.00 | 241766.00 | 17325.00 | 121275.00 | 120400.00 | MANNU LAL AND SONS
1424.00 | 2.0 TR nominal capacity ---- 800 CFM | 10.00 | NUM |  | 19100.00 | 458400.00 | 43000.00 | 1032000.00 | 19425.00 | 466200.00 | 458400.00 | MANNU LAL AND SONS
1425.00 | 2.5 TR nominal capacity ---- 1000 CFM | 15.00 | NUM |  | 22900.00 | 229000.00 | 51000.00 | 510000.00 | 23625.00 | 236250.00 | 229000.00 | MANNU LAL AND SONS
1426.00 | 3.0 TR nomonal capacity ---- 1200 CFM | 4.00 | NUM |  | 29500.00 | 442500.00 | 55000.00 | 825000.00 | 26775.00 | 401625.00 | 401625.00 | Innovations Workspace Solutions Pvt. Ltd.
1427.00 | Chilled water Cassette units
1428.00 | Supply, installation, testing & commissioning of 4 way Chilled Water Cassette Unit with copper tube and aluminium finned cooling coil, extended tray for valve assembly, low noise fan and motor with ON/OFF and 3 speed control and suitable for 1 phase, 220 ± 10%V, 50 Hz electric supply, with cordless remote control, fabric filter, and decorative front grille.
1429.00 | 2.5 TR nominal capacity --- 1000 CFM | 2.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1430.00 | 3.0 TR nominal capacity --- 1200 CFM | 5.00 | NUM |  | 44000.00 | 88000.00 | 45000.00 | 90000.00 | 35595.00 | 71190.00 | 71190.00 | Innovations Workspace Solutions Pvt. Ltd.
1431.00 | 4.0 TR nominal capacity --- 1400 CFM | 2.00 | NUM |  | 52000.00 | 260000.00 | 54000.00 | 270000.00 | 35805.00 | 179025.00 | 179025.00 | Innovations Workspace Solutions Pvt. Ltd.
1432.00 | Pressure Independent Balancing Cum Two Way Control Valve
1433.00 | (Automatic control for Fan coil unit)
1434.00 | Supply, installation, testing and commissioning of Pressure Independant Balancing Cum Two Way Control Valve in a single body equipped with electronic ON/OFF actuator working on 230V AC. The minimum close off Pressure of actuator must be 1.5 times shut off head of pump as per specifications of following sizes.Valve should come to close position ,if the power supply to the actuator is cut off. The valve actuator shall be compatible with digital snap acting type Heating/Cooling thermostat.Valve sizes shall be as follows:
1435.00 | 25mm dia | 58.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1436.00 | 32mm dia | 11.00 | NUM |  | 7200.00 | 417600.00 | 20500.00 | 1189000.00 | 7875.00 | 456750.00 | 417600.00 | MANNU LAL AND SONS
1437.00 | Snap acting type Thermostat suitable for 2 pipe system (Automatic control for Fan coil unit) | 60.00 | NUM |  | 17500.00 | 192500.00 | 25000.00 | 275000.00 | 11910.00 | 131010.00 | 131010.00 | Innovations Workspace Solutions Pvt. Ltd.
1438.00 | Supply, installation, testing and commissioning of ON/OFF type Digital display thermostat for heating(during winters) and cooling(during summers) in fan coil units as described above. The Heating & cooling thermostat shall be compatible with the above mentioned 2 way PIBC valves and will have provision of setting of room temperature, setting of fan speed (High, Medium, Low) ,capable of providing individual space temperature control for heating/cooling application. The thermostat shall produce a output to cooling OR heating in response to load change in rooms.The valve system shall be complete with necessary control cabling between control transformer (mounted in MS powder coated box with connector,to be included in cost if required), valve,standalone thermostat and the power supply near the FCU.
1439.00 | Providing and fixing in position the following ball valves with strainer & without strainer for the FCU's (PN-16) suitable for following pipe diameter. Ball valves shall have 50mm high extended stem.
1440.00 | 25mm dia | 58.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1441.00 | 32mm dia | 11.00 | SET |  | 3800.00 | 220400.00 | 12465.00 | 722970.00 | 2470.00 | 143260.00 | 143260.00 | Innovations Workspace Solutions Pvt. Ltd.
1442.00 | Two Way High Rangeability Control Valve/Pressure Independent Balancing cum Control Valve
1443.00 | (Automatic control for AHU)
1444.00 | Supply, installation, testing and commissioning of complete set of Self Balancing 2 way High Rangeability (>300)/ Pressure Independent valve with integrated Two Way modulating control valve in a single body. Valves shall be of Brass construction rotary / linear type for DN15 to DN32 of PN25 rating with screwed connections and shall be C.I body linear type for DN40-DN200 of PN16 rating with flanged connections.
1445.00 | Valves shall be complete with electronic motorised modulating actuator of operating on 24V AC, and 0-10V DC or 4-20mA control signal.The actuator shall provide similar transduced feedback output. The linear actuator shall have a stroke of minimum 15 mm.It shall be possible to operate the valve manually also and the actuator shall switch back to auto mode when power supply is restored. .Valve should come to close position ,if the power supply to the actuator is cut off OR AHU fan is shut off.The valve actuator housing shall have IP54 protection.The actuator shall be suitable for a valve close up pressure of 1.5 times the pump head or a minimum of 4bar.
1446.00 | The valve size shall be suitable for the following pipe sizes.
1447.00 | 32 mm Dia pipe | 7.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1448.00 | 40 mm Dia pipe | 1.00 | NUM |  | 15800.00 | 110600.00 | 51500.00 | 360500.00 | 25515.00 | 178605.00 | 110600.00 | MANNU LAL AND SONS
1449.00 | 50 mm Dia pipe | 13.00 | NUM |  | 17200.00 | 17200.00 | 58150.00 | 58150.00 | 34020.00 | 34020.00 | 17200.00 | MANNU LAL AND SONS
1450.00 | Modulating type Digital controller/Thermostat suitable for 2 pipe system for Airhandling units | 21.00 | NUM |  | 19200.00 | 249600.00 | 61540.00 | 800020.00 | 50610.00 | 657930.00 | 249600.00 | MANNU LAL AND SONS
1451.00 | Supply, installation, testing and commissioning of modulating type Digital display thermostat (with NTC sensors) for heating & cooling mode in Airhandling units.The thermostat shall be compatible with above mentioned 2way Hi-rangeability valves (in Sr.No.13) and will have provision of setting of room temperature,capable of providing space temperature control for Heating & cooling application.
1452.00 | The temperature controller shall be electronic microprocessor based with LCD display working on 24 VAC with 0-10Vdc output, 3nos.NTC sensors as required for 2 pipe system with complete wiring within AHU room, brass thermowells (as per the no. of sensors) and power supply unit (SMPS) for 240V AC input to 24V AC output ,300mA/1000mA.Temperature controller shall be capable of accepting inputs from minimum 3 temperature sensors. One temperature sensor for space temperature measurement and the other two temperature sensors for coil inlet and outlet water temperature measurements. The controller shall be capable of comparing the signals and selecting the lower output to prevent excessive water flow through coil. The digital controller shall be also capable of accepting 0-10Vdc signal from BAS. It shall also have RS-485 port for the soft integration with the BAS.One controller shall be suitable to work with either heating OR cooling mode.
1453.00 | A transparent control box of IP55 construction for housing the Digital controller and power supply unit shall be provided & mounted in AHU room.
1454.00 | ELECTRO-CHEMICAL TREATMENT SYSTEM FOR COOLING TOWERS | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1455.00 | SITC of Electro-Chemical Treatment System for Cooling Tower (Non-Chemical) for Cooling Tower Treatment. The system should be equipped with Automatic Self Cleaning Mechanism & Automatic Blowdown Control. The proposed system should be manufactured and complied with ISO 14001:2015, ISO 9001:2015. The system must be CE + RoHS compliant and in accordance with UL standards. The proposed system should minimize blow down water consumption up to 50%. No/Zero Chemicals uses for cooling tower circuit, technology must fall under green technology initiatives, the system must avoids algae and micro-bacterial formation in water or surface of Pipe/ CT/ fills. The system must have components like - Electrolytic Reactor, Automated Scrapper mechanism for reactor cleaning, Automatic Blowdown control, Side Screen Filter, Automatic Back wash Feature, Control Panel, Skid with Pumps & Valves. Note: Above system shall be suitable for 125TR x 3nos. Cooilng Towers
1456.00 | INTELLIGENT ANTI FOULING CONDENSER SYSTEM / SMART AUTOMATIC TUBE CLEANING SYSTEM | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1457.00 | SITC of INTELLIGENT ANTI FOULING CONDENSER SYSTEM/SMART AUTOMATIC TUBE CLEANING SYSTEM with Anti Fouling arrangement on chiller by automatic condenser cleaning Upto 4# Chillers Max, with a Common Skid for the required number of chillers in the plantroom. The system shall include IoT Ready, Industry 4.0 complaint device. The Panel should have minimum 7" Touch Screen Graphical HMI which will log the real time data related to chiller energy (KWH), capacity (TR), Chiller Water Flow monitoring, Water Temperature profile on evaporator and condenser both and graphical representation of historic summary which shall be displayed on the Mobile Application with unlimited user access on cloud based system. The data can also be retrieved in XL or PDF Format. The system shall have one Injection/Collection pump, Motorized Valves, Energy Mater, Flow Meter, Temp. Sensors and complete with all accessories and Low side activities of piping connections of Ball traps & Ball collectors on the Chillers. The Common Skid piping, Ball Trap Size to suit chiller capacity requirement for the project. Note: Above system shall be suitable for 125TR x 3nos. Chillers
1458.00 | SUB-HEAD- II: VENTILATION SYSTEM
1459.00 | Inline Fans Supply, installation, testing and commissioning of duct mounted Cabinet/Circular Inline fans complete with direct driven centrifugal blower/impeller, motor, rubber isolation mounts & other accessories including wiring & conduiting complete in all respects. The casing shall be double skin,internally acoustically lined and constructed of galvanized steel.The inline fans shall be selected for lower noise level. Single phase Inline fans motor shall have inbuilt speed controller & three phase inline fan motor shall be compatible with VFD and shall be provided with suitable starter ,power/control cabling and earthing.NC level 3M away from source should be less than 50db.The fans shall be of following capacity:
1460.00 | Ground floor
1461.00 | 200 CFM (20mm static pressure) for Male & FemaleToilet Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1462.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 8300.00 | 8300.00 | 19367.00 | 19367.00 | 4410.00 | 4410.00 | 4410.00 | Innovations Workspace Solutions Pvt. Ltd.
1463.00 | First floor
1464.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1465.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1466.00 | Second floor
1467.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1468.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1469.00 | Third floor
1470.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1471.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1472.00 | Fourth floor
1473.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1474.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1475.00 | Fifth floor
1476.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1477.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1478.00 | Sixth floor
1479.00 | 300 CFM (20mm static pressure) for Pantry Exhaust | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1480.00 | 900 CFM (30mm static pressure) for Male & Female Toilet Exhaust | 1.00 | NUM |  | 9200.00 | 9200.00 | 21000.00 | 21000.00 | 5880.00 | 5880.00 | 5880.00 | Innovations Workspace Solutions Pvt. Ltd.
1481.00 | Propeller Fans Supplying, installing, testing and commissioning of direct driven PROPELLER FANS for exhaust/fresh air as shown in drawings. Each fan shall be complete with permanent split capacitor or shaded pole motor, mounting plate, accessories like wire guard, bird screen and fixed louvers for weather protection as required.Fan shall be provided with speed regulator and NC level 3M away from source shall be less than 60db. Fan selection arrangement and Electrical characteristics shall be as follows :
1482.00 | 250 mm dia 1400 RPM fan suitable for 240± 10% volts 50 cycles, 1 phase AC supply. (For Toilet exhaust) Plastic Body Designer fan. | 13.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1483.00 | 225 mm dia 1400 RPM fan suitable for 240± 10% volts 50 cycles, 1 phase AC supply. (For electrical Room ) in metal construction as per description above. | 7.00 | NUM |  | 3800.00 | 49400.00 | 7000.00 | 91000.00 | 4045.00 | 52585.00 | 49400.00 | MANNU LAL AND SONS
1484.00 | AXIAL FLOW FANS (NORMAL MODE & PRESSURIZATION)
1485.00 | Supply, Installation testing and commissioning of Vane Axial Fans with impeller having adjustable pitch angle blades and complete with suitable TEFC motor and drive assembly. The fan shall be suitable for ceiling/floor installation along with spring isolators or as recomended by the manufacturer. Fan motor shall be VFD compatible & shall be of high efficiency Class EFF-1(Only for normal working fans). Motor shall be suitable for 415 ± 10% V, 3 Phase, 50 ± 3%Hz electrical supply.Fan & motor shall be selected for minimum 30mm Static pressure.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication. The fan motor shall have class 'F' insulation.The fan shall be selected for low noise level and low RPM as per technical specifications. Fans shall be AMCA Certified. Price shall also include double sleeve fire retardant flexible connection on both sides of the fan.The fan duty shall be as follows: (Normal mode)
1486.00 | Floor GF AF-01,02,03 Area Served AC Plant Room Application Exhaust Air Air qty CFM 4500 SP in mm 10 Motor kW 1.1 | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1487.00 | Floor BF AF-04 Area Served Pump Room Application Fresh Air Air qty CFM 3600 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 28700.00 | 86100.00 | 67500.00 | 202500.00 | 39375.00 | 118125.00 | 86100.00 | MANNU LAL AND SONS
1488.00 | Floor BF AF-05 Area Served Pump Room Application Exhaust Air Air qty CFM 4000 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 37500.00 | 37500.00 | 54000.00 | 54000.00 | 35070.00 | 35070.00 | 35070.00 | Innovations Workspace Solutions Pvt. Ltd.
1489.00 | Floor BF AF-06 Area Served STP Plant Room Application Fresh Air Air qty CFM 5400 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 37500.00 | 37500.00 | 60000.00 | 60000.00 | 39375.00 | 39375.00 | 37500.00 | MANNU LAL AND SONS
1490.00 | Floor BF AF-07 Area Served STP Plant Room Application Exhaust Air Air qty CFM 6000 SP in mm 40 Motor kW 3.7 | 1.00 | NUM |  | 69990.00 | 69990.00 | 81000.00 | 81000.00 | 44100.00 | 44100.00 | 44100.00 | Innovations Workspace Solutions Pvt. Ltd.
1491.00 | Floor BF Terrace AF-08 ,09,10 Area Served Lift well pressurization Application Fresh Air Air qty CFM 13000 SP in mm 30 Motor kW 5.5 | 3.00 | NUM |  | 48800.00 | 48800.00 | 90000.00 | 90000.00 | 57225.00 | 57225.00 | 48800.00 | MANNU LAL AND SONS
1492.00 | Floor BF Terrace AF-11 Area Served Lift lobby pressurization Application Fresh Air Air qty CFM 13000 SP in mm 30 Motor kW 5.5 | 1.00 | NUM |  | 112800.00 | 338400.00 | 195000.00 | 585000.00 | 78015.00 | 234045.00 | 234045.00 | Innovations Workspace Solutions Pvt. Ltd.
1493.00 | Floor BF Terrace AF-12 Area Served Staircase pressurization Application Fresh Air Air qty CFM 15000 SP in mm 30 Motor kW 5.5 | 1.00 | NUM |  | 112800.00 | 112800.00 | 195000.00 | 195000.00 | 78015.00 | 78015.00 | 78015.00 | Innovations Workspace Solutions Pvt. Ltd.
1494.00 | Floor BF Terrace AF-13 Area Served Corridor Makeup air Application Fresh Air Air qty CFM 21000 SP in mm 30 Motor kW 7.5 | 1.00 | NUM |  | 124500.00 | 124500.00 | 225000.00 | 225000.00 | 82320.00 | 82320.00 | 82320.00 | Innovations Workspace Solutions Pvt. Ltd.
1495.00 | Floor BF Terrace AF-14 Area Served Corridor Makeup air Application Fresh Air Air qty CFM 25000 SP in mm 30 Motor kW 11 | 1.00 | NUM |  | 176900.00 | 176900.00 | 315000.00 | 315000.00 | 119700.00 | 119700.00 | 119700.00 | Innovations Workspace Solutions Pvt. Ltd.
1496.00 | AXIAL FLOW FANS (FIRE MODE ) Supply ,Installation testing and commissioning of Vane Axial Fans with impeller having adjustable pitch angle blades and complete with suitable TEFC motor and drive assembly. The fan shall be suitable for ceiling/floor installation along with spring isolators or as recomended by the manufacturer. Fan motor shall be VFD compatible & shall be of high efficiency Class EFF-1(Only for normal working fans). Motor shall be suitable for 415 ± 10% V, 3 Phase, 50 ± 3%Hz electrical supply.Fan & motor shall be selected for minimum 30mm Static pressure.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication. The complete fan assembly alongwith the motor & drive assembly shall be fire rated i.e. suitable to operate upto 250°C for 2 hours and meet the duty parameters.The fan shall be selected for low noise level and low RPM as per technical specifications. Fans shall be AMCA Certified. Price shall also include double sleeve fire retardant flexible connection on both sides of the fan.The fan duty shall be as follows: (Smoke Extraction Mode)
1497.00 | Floor GF AF-15 Area Served Corridor Application Smoke Exhaust Air qty CFM 9400 SP in mm 30 Motor kW 3.7 | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1498.00 | Floor GF AF-16 Area Served Corridor Application Smoke Exhaust Air qty CFM 3600 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 114750.00 | 114750.00 | 141000.00 | 141000.00 | 63840.00 | 63840.00 | 63840.00 | Innovations Workspace Solutions Pvt. Ltd.
1499.00 | Floor 1F AF-17 Area Served Corridor Application Smoke Exhaust Air qty CFM 5500 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 44300.00 | 44300.00 | 54000.00 | 54000.00 | 52290.00 | 52290.00 | 44300.00 | MANNU LAL AND SONS
1500.00 | Floor 1F AF-18 Area Served Corridor Application Smoke Exhaust Air qty CFM 2000 SP in mm 30 Motor kW 0.75 | 1.00 | NUM |  | 66500.00 | 66500.00 | 82500.00 | 82500.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1501.00 | Floor 2F AF-19 Area Served Corridor Application Smoke Exhaust Air qty CFM 5000 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 38700.00 | 38700.00 | 30000.00 | 30000.00 | 40425.00 | 40425.00 | 30000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1502.00 | Floor 2F AF-20 Area Served Corridor Application Smoke Exhaust Air qty CFM 3600 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 64500.00 | 64500.00 | 75000.00 | 75000.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1503.00 | Floor 3F AF-21 Area Served Corridor Application Smoke Exhaust Air qty CFM 5300 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 44300.00 | 44300.00 | 54000.00 | 54000.00 | 52290.00 | 52290.00 | 44300.00 | MANNU LAL AND SONS
1504.00 | Floor 3F AF-22 Area Served Corridor Application Smoke Exhaust Air qty CFM 3000 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 65800.00 | 65800.00 | 79500.00 | 79500.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1505.00 | Floor 4F AF-23 Area Served Corridor Application Smoke Exhaust Air qty CFM 4800 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 68700.00 | 68700.00 | 45000.00 | 45000.00 | 40425.00 | 40425.00 | 40425.00 | Innovations Workspace Solutions Pvt. Ltd.
1506.00 | Floor 4F AF-24 Area Served Corridor Application Smoke Exhaust Air qty CFM 5800 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 58700.00 | 58700.00 | 72000.00 | 72000.00 | 59220.00 | 59220.00 | 58700.00 | MANNU LAL AND SONS
1507.00 | Floor 5F AF-25 Area Served Corridor Application Smoke Exhaust Air qty CFM 4800 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 78700.00 | 78700.00 | 87000.00 | 87000.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1508.00 | Floor 5F AF-26 Area Served Corridor Application Smoke Exhaust Air qty CFM 5500 SP in mm 30 Motor kW 2.2 | 1.00 | NUM |  | 62800.00 | 62800.00 | 72000.00 | 72000.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1509.00 | Floor 6F AF-27 Area Served Corridor Application Smoke Exhaust Air qty CFM 2500 SP in mm 30 Motor kW 1.1 | 1.00 | NUM |  | 66500.00 | 66500.00 | 82500.00 | 82500.00 | 59220.00 | 59220.00 | 59220.00 | Innovations Workspace Solutions Pvt. Ltd.
1510.00 | Floor 6F AF-28 Area Served Corridor Application Smoke Exhaust Air qty CFM 3600 SP in mm 30 Motor kW 1.5 | 1.00 | NUM |  | 42500.00 | 42500.00 | 37500.00 | 37500.00 | 40425.00 | 40425.00 | 37500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1511.00 | PACKAGED AIRWASHER Supply, installation, testing and commissioning of factory fabricated Outdoor type Double Skinned package floor mounted type evaporating air cooling unit fabricated out of extruded aluminium section with 0.6 mm pre-plasticized /pre-coated Galvanised steel sheet outside & 0.6 mm plain stainless steel (SS -304) sheet inside with blower section having DIDW backward curved blower (or equivalent performance direct driven plug fan) and EFF-1 blower motor (VFD Compatible) TEFC type suitable for operating on 415 ± 10% volts, 50 Hz ± 5% AC supply,1400 RPM, belt driven package, manual type aluminium aerofoil gear driven VCD & fire retardent double sleeve flexible connections made of silicon/neoprene rubber at outlet, wet section & tank shall be made of 18 G stainless steel (SS 304) having depth not less than 300mm. The Air-washer shall be complete with Celdek fill of depth 200 mm ,built-in drift PVC eliminators & with 50mm thick HDPE MERV-8 pre filters.The face velocity across the fill shall be limited to 500 FPM maximum.The Air-washer shall have minimum saturation efficiency of 90% & shall be complete with suitable capacity water circulation pump (including standby) GI B Class/CPVC interconnecting piping including valves ,y strainer & distribution header, , The airwasher panels shall be insulated with minimum 23mm thick & 40 ± 2Kg/m³ density PU foam..Fan & motor shall be selected for minimum 45mm Static pressure as required.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication. The Airwasher shall conform to specifications given in the tender & shall be of following capacity.
1512.00 | For AC Plant Room at Ground floor AWS/01 - 11500 CFM, 1 x 630mm DIDW Backward curved Fan,1 x 5.5 KW Fan Motor, 45 mm St. Pressure, 2 x 0.5 HP Water Circulation Monoblock Pumps (1W +1S) | 2.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1513.00 | For Cafeteria kitchen at Ground floor AWS/02 - 4500 CFM, 1 x 400 mm DIDW Backward curved Fan, 1 x 2.2 KW Fan Motor, 45 mm St. Pressure, 2 x 0.5 HP Water Circulation Monoblock Pumps (1W +1S) | 2.00 | NUM |  | 178500.00 | 357000.00 | 172500.00 | 345000.00 | 291900.00 | 583800.00 | 345000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1514.00 | KITCHEN EXTRACT FAN SECTION INTEGRATED WITH DRY SCRUBBER | 1.00 | NUM |  | 92000.00 | 184000.00 | 67500.00 | 135000.00 | 127050.00 | 254100.00 | 135000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1515.00 | Supply, Installation, Testing and Commissioning of Airhandling units comprising of fan section, section for accomodating dry type scrubber unit (specifications as detailed below) and air intake section of minimum 900mm depth for extract air complete with floor standing backward curved DIDW centrifugal fan (or equivalent plug fan) GI/Extruded aluminium base frame,TEFCsquirrel cage induction high efficiency EFF-1 motor (VFD Compatible) with class "H" insulation ,drive package and vibration isolation arrangement including spring isolators or as recommended by manufacturer.Complete unit casing shall be fabricated out of double skin panels with minimum 23mm thick injected puff of density not less than 40Kg/Cum as specified. Fan motor shall be suitable for operating on 415± 10% volts, 50 Hz, 3 phase AC power supply. The kitchen fan motor shall be outside hot air stream. Fan outlet velocity shall not exceed 1800 FPM.Fan & motor shall be selected for minimum 75mm Static pressure as required.Total static pressure shall be checked by vendor. Change in static pressure will not attract any price implication.
1516.00 | Scrubber shall comprise of electrostatic precipitator, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 18 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh pre filters, Ionizing-Collecting cell(s) shall be of one-piece construction minimum 13.38” inches deep in direction of airflow, to work as magnet for charged smoke & oil particles.Average efficiency shall be 90-95% in single pass as per DOP test method. Electrostatic Precipitator shall be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell shall be of permanent type and incorporate slide out facility for easy removal for cleaning.Ionizing electrodes shall be heavy duty tungsten wire rigidly supported both vertically and laterally. High voltage support insulators shall be made of Teflon, including center hole, glazed to enhance dielectric strength and retard tracking. Insulators shall be mounted out of the airstream, to reduce contaminant buildup. All high voltage electrical connections within each tier of cells, shall facilitate automatic connection when cells are installed. Power supplies shall be 100% solid state CE Listed, Module shall be equipped with Pulse width modulating (PWM).The system shall be fitted with interlock switch for safety . The system shall allow connection to a fan section to achieve 500 FPM velocity across the air cleaner. All units shall have Arc Supression & Auto Restart and shall have BMS (Building Management System) compatibility, Performance Indicator Lightsshall be part of the system to indicate the status of the air cleaning system. Power Consumption shall not be more that 50 watts per ESP cell.
1517.00 | Operating Voltage : 220V, 50 Hz
1518.00 | Ionizing Voltage : 12.5 to 13 KVDC
1519.00 | Collector Cell Voltage : 6 to 6.5 KVDC
1520.00 | Power Consumption : 50 Watts
1521.00 | Note:Srcubber supplied at site shall be factory fitted with in the fan section as an integral part of the airhandling unit with necessary air intake section.The fan characteristics shall be as follows :
1522.00 | EFS-1/Terrace floor/ Cafe kitchen - 5000 CFM, 90 mm St. Pr, DIDW Backward curved Fan 1 x 400 mm dia, 1 x 3.7 Kw Fan Motor with class H insulation.(Horizontal floor mounted unit ) Dry scrubber module shall have 2500 cfm x 2 filter modules
1523.00 | SUB-HEAD-III : CHILLED & CONDENSER WATER PIPING
1524.00 | Chilled / Condenser Water Piping
1525.00 | Supply, Installation, testing & Commissioning of MS "C" class ERW Chilled water piping conforming to IS1239/IS3589 cut to required lengths & complete with fittings such as bends, elbows, tees, reducers, rubber gaskets, factory fabricated GI piping supports & vibration isolators, companion flanges,thermowells for sensors/thermometers & socket for BAS, painting etc. Price shall also include pressure testing.
1526.00 | The wall thickness of pipes for 200NB shall be 6.0mm & for 250NB & above shall be 8.0mm.
1527.00 | Chilled water piping
1528.00 | 25 mm dia pipe | 500.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1529.00 | 32 mm dia pipe | 525.00 | M |  | 431.00 | 215500.00 | 255.00 | 127500.00 | 510.00 | 255000.00 | 127500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1530.00 | 40 mm dia pipe | 500.00 | M |  | 587.00 | 308175.00 | 326.00 | 171150.00 | 655.00 | 343875.00 | 171150.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1531.00 | 50 mm dia pipe | 250.00 | M |  | 591.00 | 295500.00 | 376.00 | 188000.00 | 765.00 | 382500.00 | 188000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1532.00 | 65 mm dia pipe | 50.00 | M |  | 791.00 | 197750.00 | 531.00 | 132750.00 | 1045.00 | 261250.00 | 132750.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1533.00 | 80 mm dia pipe | 40.00 | M |  | 986.00 | 49300.00 | 679.00 | 33950.00 | 1330.00 | 66500.00 | 33950.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1534.00 | 100 mm dia pipe | 85.00 | M |  | 1206.00 | 48240.00 | 848.00 | 33920.00 | 1670.00 | 66800.00 | 33920.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1535.00 | 125 mm dia pipe | 150.00 | M |  | 1715.00 | 145775.00 | 1237.00 | 105145.00 | 1970.00 | 167450.00 | 105145.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1536.00 | 150 mm dia pipe | 220.00 | M |  | 2091.00 | 313650.00 | 1526.00 | 228900.00 | 2155.00 | 323250.00 | 228900.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1537.00 | Condenser water piping
1538.00 | 125 mm dia pipe | 90.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1539.00 | 200 mm dia pipe | 95.00 | M |  | 2091.00 | 188190.00 | 1526.00 | 137340.00 | 2155.00 | 193950.00 | 137340.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1540.00 | Manual Balancing Valves Providing and fixing in position the following specified make Manual balancing valves complete with companion flanges, nuts, bolts, gaskets etc. as required. Balancing valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation for chilled & hot water as per the specifications.
1541.00 | 32 mm dia (Insulated) | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1542.00 | 40 mm dia (Insulated) | 1.00 | NUM |  | 6986.00 | 6986.00 | 4250.00 | 4250.00 | 7210.00 | 7210.00 | 4250.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1543.00 | 50 mm dia (Insulated) | 1.00 | NUM |  | 7509.00 | 7509.00 | 4880.00 | 4880.00 | 8035.00 | 8035.00 | 4880.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1544.00 | 65 mm dia (Insulated) | 1.00 | NUM |  | 12789.00 | 12789.00 | 7040.00 | 7040.00 | 7975.00 | 7975.00 | 7040.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1545.00 | 80mm dia (Insulated) | 3.00 | NUM |  | 13968.00 | 13968.00 | 8120.00 | 8120.00 | 8370.00 | 8370.00 | 8120.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1546.00 | 100 mm dia (Insulated) | 4.00 | NUM |  | 15303.00 | 45909.00 | 9200.00 | 27600.00 | 13815.00 | 41445.00 | 27600.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1547.00 | 125 mm dia (Insulated) | 7.00 | NUM |  | 23616.00 | 94464.00 | 13320.00 | 53280.00 | 18150.00 | 72600.00 | 53280.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1548.00 | 125 mm dia (Uninsulated) | 6.00 | NUM |  | 32809.00 | 229663.00 | 18280.00 | 127960.00 | 21120.00 | 147840.00 | 127960.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1549.00 | Butterfly Valves (Manual) Providing and fixing in position the following wafer type Butterfly Valves complete with companion flanges, nuts, bolts, gaskets etc. as required. Butterfly valves shall conform to PN -16 rating as per specifications. Quoted price shall be inclusive of insulation for chilled & hot water as per the specifications.
1550.00 | 50 mm dia (Insulated) | 32.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1551.00 | 65 mm dia (Insulated) | 3.00 | NUM |  | 3381.00 | 108192.00 | 2019.00 | 64608.00 | 2970.00 | 95040.00 | 64608.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1552.00 | 80mm dia (Insulated) | 10.00 | NUM |  | 3704.00 | 11112.00 | 2178.00 | 6534.00 | 3245.00 | 9735.00 | 6534.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1553.00 | 100 mm dia (Insulated) | 8.00 | NUM |  | 4014.00 | 40140.00 | 2387.00 | 23870.00 | 3430.00 | 34300.00 | 23870.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1554.00 | 125 mm dia (Insulated) | 28.00 | NUM |  | 4954.00 | 39632.00 | 3060.00 | 24480.00 | 4455.00 | 35640.00 | 24480.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1555.00 | 125 mm dia (Uninsulated) | 18.00 | NUM |  | 5897.00 | 165116.00 | 3814.00 | 106792.00 | 5500.00 | 154000.00 | 106792.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1556.00 | 150 mm dia (Insulated) | 6.00 | NUM |  | 5497.00 | 98946.00 | 3550.00 | 63900.00 | 6490.00 | 116820.00 | 63900.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1557.00 | 200 mm dia (Gear driven) (Insulated) | 3.00 | NUM |  | 7972.00 | 47832.00 | 4306.00 | 25836.00 | 6435.00 | 38610.00 | 25836.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1558.00 | Butterfly Valves (Motorised) Providing and fixing in position the following Motorised Butterfly Valves with necessary ON/OFF type actuator and control wiring.The valve shall be with extended neck & complete with companion flanges, hot dip galvanised nuts & bolts, gaskets etc. as required. Butterfly valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications. The valve shall be BMS compatible.
1559.00 | 125 mm dia (Insulated) | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1560.00 | 125 mm dia (Uninsulated) | 6.00 | NUM |  | 69240.00 | 207720.00 | 29870.00 | 89610.00 | 36225.00 | 108675.00 | 89610.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1561.00 | Suction Guides Providing and fixing in position the following suction guides as per specifications (PN - 16). Suction guide shall be complete with companion flanges, nuts, bolts, gaskets etc. as required.Quoted price shall be inclusive of insulation as per the specifications. 125 mm dia | 9.00 | NUM |  | 63200.00 | 379200.00 | 25750.00 | 154500.00 | 34325.00 | 205950.00 | 154500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1562.00 | Expansion Bellows Supply & Installation of neoprene single arch rubber expansion bellows with integral reinforced rubber flanges, guide rods on both sides at inlet and outlet of water chilling machines and circulation water pumps, of approved make.(Rating PN-16) 125 mm dia | 30.00 | NUM |  | 69240.00 | 623160.00 | 17250.00 | 155250.00 | 13750.00 | 123750.00 | 123750.00 | Innovations Workspace Solutions Pvt. Ltd.
1563.00 | Ball Valves (For AHU, in Cast steel construction three piece design with screwed end)
1564.00 | Providing and fixing in position the following Ball Valves as per the specifications. Ball valves shall be complete with companion flanges, nuts, bolts, gaskets etc. as required. Quoted price shall be inclusive of insulation for chilled & hot water as per the specifications and of PN-16 rating.
1565.00 | 32 mm dia | 16.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1566.00 | 40 mm dia | 2.00 | NUM |  | 3722.00 | 59552.00 | 750.00 | 12000.00 | 3575.00 | 57200.00 | 12000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1567.00 | Ball Valves (For Drain purpose ,in forged brass/Gun metal construction with screwed end)
1568.00 | Providing and fixing in position the following ball Valves as per the specifications. Quoted price shall be inclusive of insulation as per the specifications and of PN-16 rating.
1569.00 | 40 mm dia | 4.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1570.00 | 32 mm dia | 2.00 | NUM |  | 2670.00 | 10680.00 | 950.00 | 3800.00 | 3280.00 | 13120.00 | 3800.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1571.00 | 25 mm dia | 10.00 | NUM |  | 1780.00 | 3560.00 | 750.00 | 1500.00 | 2815.00 | 5630.00 | 1500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1572.00 | 20 mm dia | 6.00 | NUM |  | 1157.00 | 11570.00 | 500.00 | 5000.00 | 2080.00 | 20800.00 | 5000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1573.00 | 15 mm dia | 42.00 | NUM |  | 634.00 | 3804.00 | 450.00 | 2700.00 | 1430.00 | 8580.00 | 2700.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1574.00 | Check Valves
1575.00 | Providing and fixing in position the following wafer type dual plate check valves. Check valves shall conform to PN-16 rating as per the specifications.Check valves shall be complete with companion flanges, nuts, bolts, gaskets etc. as required. Quoted price shall be inclusive of insulation as per the specifications.
1576.00 | 125 mm dia (Insulated) | 6.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1577.00 | 125 mm dia (Uninsulated) | 3.00 | NUM |  | 11574.00 | 69444.00 | 12000.00 | 72000.00 | 8580.00 | 51480.00 | 51480.00 | Innovations Workspace Solutions Pvt. Ltd.
1578.00 | Y-strainer
1579.00 | Providing and fixing in position the following Y-strainers as per specifications (PN - 16). Y strainers shall be complete with companion flanges, nuts, bolts, gaskets etc. as required.Quoted price shall be inclusive of insulation as per the specifications.
1580.00 | 32 mm dia | 8.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1581.00 | 40 mm dia | 5.00 | NUM |  | 3109.00 | 24872.00 | 2390.00 | 19120.00 | 4395.00 | 35160.00 | 19120.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1582.00 | 50 mm dia | 8.00 | NUM |  | 4352.00 | 21760.00 | 2471.00 | 12355.00 | 5680.00 | 28400.00 | 12355.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1583.00 | Pot Strainer
1584.00 | Supply, installation, testing and commissioning of Pot - Strainer of the following sizes confirming to tender specification.
1585.00 | 200 mm dia (Uninsulated) CDW | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1586.00 | 150 mm dia (Insulated) CHW | 1.00 | NUM |  | 40478.00 | 40478.00 | 7500.00 | 7500.00 | 42350.00 | 42350.00 | 7500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1587.00 | Flow switches | 6.00 | NUM |  | 26890.00 | 26890.00 | 6850.00 | 6850.00 | 35750.00 | 35750.00 | 6850.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1588.00 | Providing and fixing in position approved make pedal type flow switches complete with copper control wiring between inlet and outlet of each chiller. These shall be BMS compatible.
1589.00 | Thermometer | 60.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1590.00 | Supply, installation, testing and commissioning of Glycerine filled Dial type temperature gauge of approved make of dia 100 mm constructed out of SS 304 material.SS siphon shall be factory insulated with closed cell nitrile rubber in tubing form. Pressure gauges shall be fitted with a ball valve at the tube. (For Floor Mounted AHU, Chiller, Condenser & All Pumps)
1591.00 | Pressure Gauges | 76.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1592.00 | Supply, installation, testing and commissioning of Glycerine filled industrial type pressure gauge of approved make of dia 100 mm constructed out of SS 304 material.SS siphon shall be factory insulated with closed cell nitrile rubber in tubing form. Pressure gauges shall be fitted with a ball valve at the tube. (For Floor Mounted AHU, Chiller, Condenser & All Pumps)
1593.00 | Auto air Purge
1594.00 | Providing and fixing in position the following automatic purge valve with ball valve.
1595.00 | 15mm dia | 42.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1596.00 | 20mm dia | 8.00 | NUM |  | 873.00 | 36666.00 | 500.00 | 21000.00 | 1165.00 | 48930.00 | 21000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1597.00 | 25mm dia | 4.00 | NUM |  | 1325.00 | 10600.00 | 550.00 | 4400.00 | 1585.00 | 12680.00 | 4400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1598.00 | Test Points | 8.00 | NUM |  | 1475.00 | 5900.00 | 600.00 | 2400.00 | 1815.00 | 7260.00 | 2400.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1599.00 | Providing and fixing in position of approved make Test Points comprising of accessories such as adaptors, needle etc. The test points shall be installed at inlet and outlet of ceiling suspended AHUs .Test points shall be in brass construction and comprise of 1/4" BSP with neoprene sealing bushes and screwed covers.
1600.00 | Flow meter | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1601.00 | Providing Ultrasonic type flow meter to measure the flow rates in the following chilled water pipe lines. Flow meter shall be with electronic digital readout and shall be capable of receiving 4-20 mA 0-10 volt DC signal from BAS /CPM. Flow rate 625USGPM
1602.00 | Butterfly Valves (Motorised) | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1603.00 | Providing and fixing in position the following Motorised Butterfly Valves with necessary Modulating type actuator and control wiring.The valve shall be with extended neck & complete with companion flanges, hot dip galvanised nuts & bolts, gaskets etc. as required. Butterfly valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications. The valve shall be BMS compatible. 125 mm dia (Insulated)
1604.00 | Condensate Drain Piping
1605.00 | Supply, installation, testing and commissioning of condensate drain water piping of CPVC complete with fittings like elbows, tees, reducers, bends, U-traps, braided flexible pipe connections with GI clamps, flanges, supports, solvent etc. as required conforming to tender specifications and of following sizes.
1606.00 | 25 mm dia pipe | 560.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1607.00 | 32 mm dia pipe | 140.00 | M |  | 250.00 | 140000.00 | 120.00 | 67200.00 | 195.00 | 109200.00 | 67200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1608.00 | 40 mm dia pipe | 30.00 | M |  | 278.00 | 38920.00 | 180.00 | 25200.00 | 275.00 | 38500.00 | 25200.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1609.00 | SUB-HEAD-IV : AIR DISTRIBUTION
1610.00 | Rectangular GI Ducting (Factory Made)
1611.00 | Supply, fabrication, Installation, testing and commissioning of factory fabricated rectangular ducts using G.I Sheets (120GSM coating). The price shall include factory fabricated TDF flanges, turning vanes, splitter dampers, supports (factory fabricated, full threaded GI rod/hangers & G.I slotted channel), sealant, neoprene gasket, access door etc. The joints shall be with least leak and shall be tested with pressure testing machine of approved vendor.Corrective action shall be taken ,if the leakge is more than the permissible limit. Report shall be generated after satisfactory testing of ducts for leakage and shall be duly signed by the client's /PMC representative before giving clearance for the thermal insulation.
1612.00 | 24 gauge galvanized sheet steel ( TDF 01- 750mm) | 1800.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1613.00 | 22 gauge galvanized sheet steel ( TDF 751 - 1500mm) | 2400.00 | M2 |  | 895.00 | 1611000.00 | 450.00 | 810000.00 | 1000.00 | 1800000.00 | 810000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1614.00 | 20 gauge galvanized sheet steel ( TDF 1501- 2250mm) | 30.00 | M2 |  | 1014.00 | 2433600.00 | 500.00 | 1200000.00 | 1165.00 | 2796000.00 | 1200000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1615.00 | 18 gauge galvanized sheet steel ( TDF 2250mm & above ) | 10.00 | M2 |  | 1290.00 | 38700.00 | 739.00 | 22170.00 | 1350.00 | 40500.00 | 22170.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1616.00 | Note :- The Duct shall be manufactured as per SMACNA Standard but the minimum guage shall be 24 G.
1617.00 | 16 gauge (MS welded duct with angle frames duly painted with primer & fire rated paint (From outside for Kitchen exhaust) | 110.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1618.00 | Site Fabricated GI Duct
1619.00 | Supply, fabrication, Installation, testing and commissioning of site fabricated rectangular ducts using G.I Sheets (120GSM coating). The price shall include factory fabricated MS flanges (wherever required), turning vanes, splitter dampers, supports (factory fabricated, full threaded G.I rod/hangers & G.I slotted channel), sealant, neoprene gasket, access door etc.as required and as per ISI specifications.The joints shall be with least leak and shall be tested with pressure testing machine of approved vendor.Corrective action shall be taken ,if the leakge is more than the permissible limit. Report shall be generated after satisfactory testing of ducts for leakage and shall be duly signed by the client's /PMC representative before giving clearance for the thermal insulation.
1620.00 | 24 gauge galvanized sheet steel | 75.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1621.00 | 22 gauge galvanized sheet steel | 130.00 | M2 |  | 895.00 | 67125.00 | 300.00 | 22500.00 | 1000.00 | 75000.00 | 22500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1622.00 | 20 gauge galvanized sheet steel | 5.00 | M2 |  | 1014.00 | 131820.00 | 398.00 | 51740.00 | 1165.00 | 151450.00 | 51740.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1623.00 | 18 gauge galvanized sheet steel | 10.00 | M2 |  | 1290.00 | 6450.00 | 530.00 | 2650.00 | 1350.00 | 6750.00 | 2650.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1624.00 | 16 gauge (MS welded duct with angle frames duly painted for Kitchen exhaust) | 15.00 | M2 |  | 1490.00 | 14900.00 | 664.00 | 6640.00 | 1595.00 | 15950.00 | 6640.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1625.00 | GSS VOLUME CONTROL DAMPER | 10.00 | M2 |  | 2649.00 | 39735.00 | 803.00 | 12045.00 | 2355.00 | 35325.00 | 12045.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1626.00 | Supply, installation, testing and balancing of opposed multiblade box type GI volume control damper within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per approved shop drawings & specifications.(All AHUs, fan sections VCD at machine outlets shall be included in the equipment cost only)
1627.00 | NON RETURN DAMPER | 7.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1628.00 | Supply, installation, testing and commissioning of back draft dampers, gravity louver type on the supply air/ventilation ducts.The dampers shall be installed to avoid the short cycling of air w.r.t these fans/blowers installed in the same vicinity. The dampers shall be with suitable flanges. The frame shall be constructed of minimum 18 Gauge GI and blades shall be minimum of 24Gauge GI. The blades shall be provided with high class rubber/neoprene gaskets to avoid rattling noise during operation and to permit low leakage.All blades shall be fitted to a common linkage in such a manner so that all blades shall lift up and shut down simultaneously. The dampers shall open by the pressure differential generated by fan.
1629.00 | FIRE DAMPERS
1630.00 | Supply, installation, testing and commissioning of multi blade sleeve type combined motorised fire & smoke dampers with spring return actuator. The damper shall be of atleast 1.5 hr. fire rating. The damper shall be as per CBRI approval.The damper shall be constructed out of 16G galvanised sheet steel. It shall be complete with control panel, spring return actuator, sensor . Cost to include control cabling between firedamper control panel , actuator and fan starter panel for necessary inter-locking / for tripping of AHU fan motor.The fire dampers shall be installed at locations shown in approved shop drawings and as per specifications.
1631.00 | Smoke & Fire Dampers. | 22.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1632.00 | Control Panels with actuator suitable for 10-12 NM torque | 75.00 | M2 |  | 6400.00 | 140800.00 | 7318.00 | 160996.00 | 10450.00 | 229900.00 | 140800.00 | MANNU LAL AND SONS
1633.00 | LINEAR GRILL (FIXED BAR) | 90.00 | M2 |  | 9400.00 | 705000.00 | 6734.00 | 505050.00 | 11220.00 | 841500.00 | 505050.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1634.00 | Supply, installation, testing & balancing of removable core type ,continuous, linear, fixed bar extruded aluminium powder coated Supply Air / Return Air / Exhaust Air grills, normal flow, 15° angle one way / two way deflection with all sides flanges.Blade thickness shall be minimum 5mm in front and 1.0 mm in rear side.Grills shall be supplied in accordance with specifications and approved shop drawings. 200 mm/150mm/100mm High
1635.00 | VCDs FOR LINEAR GRILL SUPPLY AIR COLLARS | 50.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1636.00 | Supply, installation, testing & balancing of key operated extruded Aluminium volume control dampers in black mat finish for supply/return/exhaust air duct collars as per approved shop drawings and specifications.
1637.00 | SUPPLY/RETURN AIR SLOT DIFFUSERS
1638.00 | Supply, installation, testing & commissioning of Extruded Aluminium powder coated Supply/Return Air linear Slot Diffusers with all side flanges with out damper.Slot diffusers shall be supplied in accordance with specifications and approved shop drawings.
1639.00 | 2 Slot (20mm gap) | 30.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1640.00 | 3 Slot (20mm gap) | 50.00 | M |  | 5210.00 | 156300.00 | 7500.00 | 225000.00 | 1560.00 | 46800.00 | 46800.00 | Innovations Workspace Solutions Pvt. Ltd.
1641.00 | FRESH AIR INTAKE LOUVERS | 5.00 | M2 |  | 3800.00 | 190000.00 | 8000.00 | 400000.00 | 1975.00 | 98750.00 | 98750.00 | Innovations Workspace Solutions Pvt. Ltd.
1642.00 | Supply, installation, testing & balancing of Fresh air Extruded Aluminium intake louvers with bird screen and opposed blade box type GI volume control damper complete as per specification & approved shop drawings.Construction/profile of the louvers shall give a protection against the rain and suitable for fixing in the external facade of the building.
1643.00 | EXHAUST LOUVERS | 11.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1644.00 | Supply, installation, testing & balancing of Exhaust air Extruded Aluminium intake louvers with bird screen complete as per specification & approved shop drawings.Construction/profile of the louvers shall give a protection against the rain and suitable for fixing in the external facade of the building.
1645.00 | SUPPLY/ RETURN AIR DIFFUSERS (Suitable for Gypsum ceiling ) | 17.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1646.00 | Supply, installation, testing and balancing of square, rectangular and round extruded aluminium powder coated Supply/ Return Air diffusers. Diffuser shall be with spring loaded removable core type distribution grid , key operated aluminium black matt finish dampers .Diffusers shall be supplied in accordance with specifications and approved shop drawings.
1647.00 | RETURN AIR / EXHAUST AIR DIFFUSERS (Suitable for Gypsum ceiling ) | 17.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1648.00 | Supply,installation,testing and balancing of square, rectangular and round extruded aluminium powder coated Return Air Diffusers/ Exhaust Air Diffusers. Diffuser shall be with spring loaded removable core type distribution grid and shall be without dampers.Diffusers shall be supplied in accordance with specifications and approved shop drawings.
1649.00 | PLAQUE TYPE SQUARE DIFFUSER - (Suitable for Grid ceiling )
1650.00 | Supply, Installation , Testing and Balancing of powder coated square Plaque diffusers having removable core and constructed with high grade aluminium extruded alloy (without collar damper). All diffusers shall have a continuous square neck of minimum 32mm height suitable for fixing spill air box.
1651.00 | Neck size: 300 x 300mm., Outer size: 595 x 595mm Standard | 5.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1652.00 | Neck size: 375 x 375mm., Outer size: 595 x 595mm Standard | 160.00 | NUM |  | 1290.00 | 6450.00 | 3240.00 | 16200.00 | 2815.00 | 14075.00 | 6450.00 | MANNU LAL AND SONS
1653.00 | Neck size: 450 x 450mm., Outer size: 595 x 595mm Standard | 180.00 | NUM |  | 1470.00 | 235200.00 | 3500.00 | 560000.00 | 2915.00 | 466400.00 | 235200.00 | MANNU LAL AND SONS
1654.00 | SPILL AIR PLENUM BOX.
1655.00 | The supply & installation of FACTORY FABRICATED spill air boxes made out of 0.6mm thick GI sheet with necessary spigot connection for fixing flexible duct and suitable collar for connecting to various neck diffuser.The box size shall be as mentioned below.
1656.00 | Box size of 300x300x400 mm(H)and equivalent required rectangular sizes. (For 300x300 neck size) | 5.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1657.00 | Box size of 375x375x400 mm(H) and equivalent required rectangular sizes. (For 375x375 neck size) | 160.00 | NUM |  | 750.00 | 3750.00 | 500.00 | 2500.00 | 1595.00 | 7975.00 | 2500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1658.00 | Box size of 450x450x400 mm(H) and equivalent required rectangular sizes. (For 450x450 neck size) | 5.00 | NUM |  | 950.00 | 152000.00 | 700.00 | 112000.00 | 3015.00 | 482400.00 | 112000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1659.00 | FLEXIBLE DUCTING
1660.00 | Supply, Installation, Testing and Commissioning of factory made pre - insulated with 25mm thick glass wool having minimum density of 16 kg/cum. Flexible ducts shall have inner as well as outer skin constructed out of aluminium sheets. Duct shall be of following sizes:
1661.00 | 200 mm dia | 70.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1662.00 | 250 mm dia | 300.00 | M |  | 410.00 | 28700.00 | 750.00 | 52500.00 | 440.00 | 30800.00 | 28700.00 | MANNU LAL AND SONS
1663.00 | 300 mm dia | 20.00 | M |  | 540.00 | 162000.00 | 850.00 | 255000.00 | 495.00 | 148500.00 | 148500.00 | Innovations Workspace Solutions Pvt. Ltd.
1664.00 | BUTTERFLY DAMPER
1665.00 | Butterfly damper made of 22G GI sheet for Supply air and return grills/diffusers in grid/gypsum ceiling. Damper shall be provided with single flap, necessary stopper, flanges for fastening on to the duct surface(with gasket) and with grooves for clamping the flexible ducts securely.
1666.00 | 200 mm dia | 5.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1667.00 | 250 mm dia | 160.00 | NUM |  | 810.00 | 4050.00 | 850.00 | 4250.00 | 1715.00 | 8575.00 | 4050.00 | MANNU LAL AND SONS
1668.00 | 300 mm dia | 5.00 | NUM |  | 980.00 | 156800.00 | 1050.00 | 168000.00 | 2155.00 | 344800.00 | 156800.00 | MANNU LAL AND SONS
1669.00 | AIR TRANSFER GRILLS | 4.00 | M2 |  | 1190.00 | 5950.00 | 1150.00 | 5750.00 | 2365.00 | 11825.00 | 5750.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1670.00 | Supply,installation,testing and balancing of extruded aluminium construction duly powder coated non vision air transfer grills with two side frame to be provided in doors.
1671.00 | FLEXIBLE DUCT CONNECTOR | 1.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1672.00 | Supply,installation and testing of double layer flexible duct connector consisting of a flame retardant fabric secured to extruded aluminium frame on both sides to provide a wear resistant airtight flexible connection. Fabric shall be mildew resistant, water proof and silicon impregnated.Flexible connector shall be supplied in accordance with the specifications and drawings. (This item shall be an integral part of the AHUs,FCUs, Axial flow fans and already captured in their specifications)
1673.00 | BIRD SCREEN | 7.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1674.00 | Supply, installation, testing & balancing of factory made Bird screen made out of galvanized steel mesh in 20G having diamond pattern with GSS flanges and necessary cross bracings suitable for Fresh/ Exhaust air fans on terrace, complete as per specification & approved shop drawings.
1675.00 | Samples of grilles / diffusers will have to be submitted to the Architect for approval on size / shape / shade / colour before ordering.
1676.00 | SUB-HEAD-V: THERMAL INSULATION
1677.00 | Thermal Insulation(Internal ducting): | 4700.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1678.00 | Supply & installation of external thermal insulation on ducts with approved sample of Aluminium foil faced XLPE duct insulation with density 25-30 Kg/Cum for XLPE, class 'O' complete as per specifications. All longitudnal and transverse joints shall be sealed with 50mm wide and 3mm thick XLPE tape .
1679.00 | 13mm thick (Supply air Ducts in return air path)
1680.00 | Acoustic lining for Ducting
1681.00 | Supply & Installation of acoustic lining within supply and return air ducting using open cell elastomeric insulation with antimicrobial protection having 140-160 Kg/cum. density.All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as per the specifications.
1682.00 | 10 mm thick | 250.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1683.00 | 20 mm thick | 200.00 | M2 |  | 714.00 | 178500.00 | 850.00 | 212500.00 | 640.00 | 160000.00 | 160000.00 | Innovations Workspace Solutions Pvt. Ltd.
1684.00 | Acoustic lining (For AHU rooms) | 1250.00 | M2 |  | 1316.00 | 263200.00 | 950.00 | 190000.00 | 870.00 | 174000.00 | 174000.00 | Innovations Workspace Solutions Pvt. Ltd.
1685.00 | Supply and Installation of thermal/acoustic lining of walls & ceiling of AHU rooms using open cell elastomeric with 140-160 Kg/cum. density. The material should be fibre free,as per the specifications.
1686.00 | 25mm thick
1687.00 | Chilled water pipe Insulation
1688.00 | Supply, Installation & Testing of below mentioned thickness of insulation with factory laminated black colour fibre glass cloth on closed cell elastomeric nitrile rubber insulation with density 40-60 Kg/ Cum, class 'O' material, in tubing form/flat sections for chilled water piping (including fittings,valves & flanges) to be installed in risers, branch piping and laid on terrace as per specifications and approved shop drawings. All longitudnal and transverse joints shall be sealed with 50mm wide and 3mm thick Nitrile rubber tape .
1689.00 | Quoted price shall be inclusive of adhesive and UV/mechanical protection using UV resistant paint/starbond coating spread over Glass cloth as per specifications.
1690.00 | 25 mm thick insulation suitable for following pipe sizes
1691.00 | 20 mm dia | 20.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1692.00 | 25 mm dia | 500.00 | M |  | 340.00 | 6800.00 | 750.00 | 15000.00 | 275.00 | 5500.00 | 5500.00 | Innovations Workspace Solutions Pvt. Ltd.
1693.00 | 32 mm thick insulation suitable for following pipe sizes
1694.00 | 32 mm dia | 525.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1695.00 | 38 mm thick insulation suitable for following pipe sizes
1696.00 | 40 mm dia | 500.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1697.00 | 50 mm dia | 250.00 | M |  | 108.00 | 54000.00 | 1500.00 | 750000.00 | 605.00 | 302500.00 | 54000.00 | MANNU LAL AND SONS
1698.00 | 65 mm dia | 50.00 | M |  | 152.00 | 38000.00 | 1650.00 | 412500.00 | 715.00 | 178750.00 | 38000.00 | MANNU LAL AND SONS
1699.00 | 80 mm dia | 40.00 | M |  | 195.00 | 9750.00 | 1700.00 | 85000.00 | 770.00 | 38500.00 | 9750.00 | MANNU LAL AND SONS
1700.00 | 100 mm dia | 40.00 | M |  | 249.00 | 9960.00 | 1750.00 | 70000.00 | 870.00 | 34800.00 | 9960.00 | MANNU LAL AND SONS
1701.00 | 125 mm dia | 40.00 | M |  | 328.00 | 13120.00 | 1800.00 | 72000.00 | 970.00 | 38800.00 | 13120.00 | MANNU LAL AND SONS
1702.00 | Chilled water pipe Insulation with in the AC Plant room
1703.00 | Supply, Installation & Testing of below mentioned thickness of insulation with plain closed cell elastomeric nitrile rubber with density 40-60 Kg/ Cum,class 'O' material, in tubing form/flat sections for chilled water piping (including fittings,valves & flanges) to be installed in plant room and headers running inside the plant room upto shafts as per specifications and approved shop drawings. All longitudnal and transverse joints shall be sealed with 50mm wide and 3mm thick Nitrile rubber . Pipe insulation along with valves shall be finished with 24G Aluminium cladding.Plastic sticker type water flow directions to be marked on the Aluminium sheathing.
1704.00 | 38 mm thick insulation suitable for following pipe sizes
1705.00 | 25 mm dia | 5.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1706.00 | 32 mm dia | 5.00 | M |  | 109.00 | 545.00 | 665.00 | 3325.00 | 275.00 | 1375.00 | 545.00 | MANNU LAL AND SONS
1707.00 | 40 mm dia | 5.00 | M |  | 128.00 | 640.00 | 1120.00 | 5600.00 | 330.00 | 1650.00 | 640.00 | MANNU LAL AND SONS
1708.00 | 50 mm dia | 10.00 | M |  | 132.00 | 660.00 | 1250.00 | 6250.00 | 715.00 | 3575.00 | 660.00 | MANNU LAL AND SONS
1709.00 | 125 mm dia | 90.00 | M |  | 172.00 | 1720.00 | 1365.00 | 13650.00 | 945.00 | 9450.00 | 1720.00 | MANNU LAL AND SONS
1710.00 | 150 mm dia | 90.00 | M |  | 421.00 | 37890.00 | 1400.00 | 126000.00 | 880.00 | 79200.00 | 37890.00 | MANNU LAL AND SONS
1711.00 | Chilled Water Pipe Insulation for Piping Running in Trench
1712.00 | Supply, Installation & Testing of insulation with 50mm thick PUF insulation (density of 36 ± 2kg per m3) covered with 2 layers of polystyrene sheet vapour barrier and finished with chicken wire mesh and 12mm thick sand cement plaster and 1 layer of tarfelt sheathing (STP) for chilled water piping (including fittings,valves & flanges) as per specifications and approved shop drawings.
1713.00 | 100 mm dia pipe | 50.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1714.00 | 125 mm dia pipe | 25.00 | M |  | 800.00 | 40000.00 | 1500.00 | 75000.00 | 1080.00 | 54000.00 | 40000.00 | MANNU LAL AND SONS
1715.00 | 150 mm dia pipe | 140.00 | M |  | 819.00 | 20475.00 | 1800.00 | 45000.00 | 1265.00 | 31625.00 | 20475.00 | MANNU LAL AND SONS
1716.00 | FCU's & AHUs Drain Pipe Insulation:
1717.00 | Supplying & installation of 6 mm thick closed cell nitrile rubber insulation with approved sample of black colour factory laminated fibre glass cloth with density 40-60 Kg/ Cum, class 'O' complete as per specifications in the form of pre-formed pipe sections and complete in all respects as per specifications and drawings on condensate drain pipes of the following sizes:
1718.00 | Quoted price shall be inclusive of adhesive and UV/mechanical protection using UV resistant paint/starbond coating spread over Glass cloth as per specifications.
1719.00 | 25 mm dia | 560.00 | M |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1720.00 | 32 mm dia | 140.00 | M |  | 144.00 | 80640.00 | 665.00 | 372400.00 | 130.00 | 72800.00 | 72800.00 | Innovations Workspace Solutions Pvt. Ltd.
1721.00 | 40 mm dia | 30.00 | M |  | 172.00 | 24080.00 | 1120.00 | 156800.00 | 160.00 | 22400.00 | 22400.00 | Innovations Workspace Solutions Pvt. Ltd.
1722.00 | SUB-HEAD-VI : ELECTRICAL WORK
1723.00 | Preamble to BOQ for MCC , Distribution Boards & wall mounted Starter Panels
1724.00 | General Notes & Specifications as given below shall be applicable to all panels.The vendors shall consider the following details in their item rates, wherever required:
1725.00 | Supporting rigid steel framework.
1726.00 | Cubicle type, 14 gauge CRCA sheet steel enclosure.
1727.00 | Panel Complete with interconnections and distribution bus bars.
1728.00 | Proper bonding to earth.
1729.00 | Painting/lettering on Breakers and distribution boards, the location they serve, Providing on each panel its circuit diagram.
1730.00 | Providing cable clamps / supports within distribution boards cable alley.
1731.00 | TPN MCCBs shall mean 3 pole MCCBs with adequate size of neutral link.
1732.00 | All MCBs shall be of minimum 10 KA breaking capacity.
1733.00 | All motor feeders MCCBs shall be of motor duty and shall be able to carry the inrush current of motor.
1734.00 | Distribution panels shall be Powder Coated with Siemens gray paint shade no. RAL-7032 of IS-5.
1735.00 | Degree of protection for following type of distribution panel enclosure shall be as per IS:13947-1993.
1736.00 | IP 42 for indoor panels.
1737.00 | IP 55 for outdoor panels with double door enclosure.
1738.00 | All MCCB’s shall be provided with operating mechanism for door interlock.
1739.00 | Current density of aluminium shall be 1 sq mm for 1.0 amps for rated current of bus bars and current density of copper shall be 1 sq.mm for 1.25 amps for rated current of bus bars.
1740.00 | Tinned copper earth bus shall be provided through out the length of each board.
1741.00 | All measuring instruments (Meters) shall be of digital electronic with LED of approved make and compatible with BAS.
1742.00 | All indicating lamps shall be LED type.
1743.00 | All current/voltage transformers shall be cast resin type.
1744.00 | All hinged door shall be earthed through 2.5 sq mm tinned braided copper wire.
1745.00 | All panels shall have provision of the following:
1746.00 | Pad locking of Switch board doors.
1747.00 | Pad locking of MCCB’s handles in “OFF” Position.
1748.00 | Additional set of C.T.s, potential free contacts, connectors, contactors with wiring etc are to be provided for BAS including space required for various transducers in Main Switch Board sections. Only transducers shall be supplied by BAS contractor.
1749.00 | All MCB’s used for protection of resistive and lightly inductive load shall be type “B” characteristic and inductive (motor) load shall be of type “C” characteristic and discharge lamps and UPS etc. shall be of type D characteristic.
1750.00 | All incoming and outgoing air circuit breakers shall be placed on middle portion of the vertical in single tier formation.
1751.00 | All PTs / control transformers shall be provided with centre tap earth secondary.
1752.00 | All DOL & Star-Delta Starters shall be provided with voltage based SPPR (single phase preventor relay) and 2 nos. of Aux.Contacts for Remote operation/monitor.
1753.00 | The Panel fabricator shall provide Aluminium Bus-bars link from Breakers wherever more than two nos. of cables are terminated in the breakers.
1754.00 | Readymade 16SWG Sheet steel Enclosure with cutout For MCBs
1755.00 | The breaking capacity of MCCB’s shall be mentioned panel wise. All MCCB’s shall be with thermal magnetic releases upto 250 amps and miroprocessor based above 250 amps capacity, unless specified otherwise.
1756.00 | All internal control wiring shall be heat resistant type.
1757.00 | Bus bar chamber shall be provided at top only. Incoming and outgoing cable entry shall be from top/bottom as required.
1758.00 | Live parts shall not be accessible after opening the door, Transparent acrylic sheet to be provided to cover the same.
1759.00 | Spare contacts of ACBs / MCCBs / Relay / Contactor shall be wired upto terminal block.
1760.00 | All Switchgear used in Starter Circuit shall be type-2 coordinated. Contactor rating shall be selected as per the kVAR rating of the capacitor bank from capacitor duty contactor range. Vendor to furnish the type-2 coordination chart and capacitor duty contactor selection chart.
1761.00 | Protection Releases Microprocessor based (PRMB) & Thermal magnetic (PRTM) shall be as describe below:
1762.00 | Protection Release Microprocessor Based (PRMB-1)
1763.00 | Over-current/long time protection range 105% - 120 % with Time setting
1764.00 | short circuit /short time protection range 100% - 1000 % with Time setting
1765.00 | Instantaneous short circuit Protection range 200% - 1500 % with Time setting
1766.00 | Earth Fault Protection range 20% - 100 % with Time setting
1767.00 | Under voltage & over voltage protection
1768.00 | Reverse power
1769.00 | Current unbalance
1770.00 | Phase sequence
1771.00 | Measurements
1772.00 | Voltage
1773.00 | Current
1774.00 | Power (Active,Reactive & Apparent)
1775.00 | Energy ((Active,Reactive & Apparent)
1776.00 | Power factor
1777.00 | Frequency
1778.00 | Protection Release Microprocessor Based (PRMB-2)
1779.00 | Over-current/long time protection range 105% - 120 % with Time setting
1780.00 | short circuit /short time protection range 100% - 1000 % with Time setting
1781.00 | Instantaneous short circuit Protection range 200% - 1500 % with Time setting
1782.00 | Earth Fault Protection range 20% - 100 % with Time setting
1783.00 | Measurements
1784.00 | Current
1785.00 | Protection Release Microprocessor Based (PRMB-3)
1786.00 | Over-current/long time protection range 105% - 120 % with Time setting
1787.00 | Instantaneous short circuit Protection range 200% - 1500 % with Time setting
1788.00 | Protection Release Thermal-Magnetic Based (PRTM)
1789.00 | Over-current
1790.00 | Short circuit
1791.00 | MOTOR CONTROL CENTRES FOR AIR CONDITIONING ( Suitable for Indoor Duty)
1792.00 | Design, fabrication, assembly, wiring and supply of front operated dead front cubicle type compartmentalised as per Form 3B, rear access free standing, dust and vermin proof main switchboards suitable for use at 415 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of 35 kA at 415 volts, fabricated from 2 mm thick CRCA MS sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom and including lifting hooks and including GI earth strip of required size with 2 nos earthing terminals and including powder coated paint finish of approved shade over metal surface cleaned and treated with minimum seven tank process complete with interconnections etc as per specifications, as required and as below.
1793.00 | Each MCC shall include cost of power cabling/wiring with earthing requirement including control wiring on GI Cable trays and inter locking between chillers, Cooling Tower fan motors (thru isolator switches) primary & secondary chilled water pumps ,condenser pumps,motorized valves & flow switch at chillers, flow meter/two way valve installed in de-coupler by pass line in order to execute the required sequence of operation. All cables and wires shall be FRLS XLPE insulated armoured. All cables shall be of 1100 volt grade FRLS XLPE insulated PVC sheathed (Copper conductor upto 10 sqmm & above 10sqmm Aluminium conductor) armoured.
1794.00 | All outgoing shall be provided with Stop/Manual/ Auto/selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contacts for Connections to Building Automation System.
1795.00 | A separate set of CTs to be provided for BAS and wiring from CT’s and voltage transducers to be brought on to separate set of terminals.
1796.00 | Note : MCCB’s shall be motor duty and suitable for 35 kA (ICS) fault current. ACB shall be suitable for 50 kA fault current.
1797.00 | The final breaker sizes may be changed based on final selection of Chiller. The cost shall be included in this panel and the contractor shall not charged extra cost in future.
1798.00 | Supply including Receiving,unloading , shifting into plant room, fixing, testing & commissioning of HVAC panel as described below | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1799.00 | HVAC Plant room Location : Ground Level Utility Block
1800.00 | Motor Control Centre for Electrical Chillers,associated pumps & Cooling Towers (415 V) consisting of
1801.00 | BUS SECTION
1802.00 | Incoming
1803.00 | 2 No. - 630 Amps each four pole EDO ACB with fault breaking capacity 50 kA (Ics = Icu 100%), fitted with interlocked door having front operating handle, conforming to IS-13947-2 1993 as amended up-to-date complete with following accessories for each ACB.
1804.00 | Microprocessor releases based relay(EMI & EMC certified) for over current, earth fault & short circuit protections with trip indications for each.
1805.00 | 0-630 amps. 1 no. BMS compatible Multifunction meter with 800/5 amps CT's and selector switch. (V, A, power factor ,KWH, Dual) 1 set
1806.00 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes- 1 Set
1807.00 | Terminals suitable to receive XLPE insulated Aluminium cables as indicated in SLD
1808.00 | Following indicating lamps, toggle switch and push buttons for each ACB with back up 2A SP MCB.
1809.00 | 3 No. Phase indicating Lamps.
1810.00 | Indicating Lamps for the following;
1811.00 | Red for ACB ON.
1812.00 | Green for ACB OFF.
1813.00 | Orange for Auto Trip.
1814.00 | Push buttons for the Yellow for trip alarm cancellation.
1815.00 | Busbar
1816.00 | 2 nos. Electrolytic high conductivity Aluminium three phase and neutral busbars with sleeves rated at 800 amps 35 kA for 1 sec. having a maximum current density of 1 amp per sq mm suitable to with stand symmetrical fault level of 35 kA at 415 volts. The neutral busbar is to be of 50% capacity.
1817.00 | Bus Coupler
1818.00 | 630 amps 4 pole ACB, EDO (Bus-coupler) with ON/OFF /TRIP indiating lamps with control Fuse, short trip, breaker, control switch etc.
1819.00 | Outgoing for section-1
1820.00 | Following rated 415V, (icu=ics 100%) 35kA MCCB's with over current and short circuit releases thermal magnetic based (if not specified below) based with ON, indications, front operating handle & door interlock along with 2A SP MCB backup protection and control terminals & wiring as required etc. complete in all respects as mentioned in specifications and as required For each outgoing:
1821.00 | Two (2) nos. 320 Amp. TP+N MCCB (for 2 Chillers,both working) with microprocessor based releases with integrated earth fault protection.
1822.00 | One (1) no.63 Amp. TP + N MCCB with ON/OFF/TRIP indication lamps, digital ammeter with CTs and selector switch (For secondary CHW pumps of 11.0 KW motor serving Single Office Zone)
1823.00 | Two (2) nos. 40 Amp. TP+N MCCB including Variable frequency drive (Model Danfoss FC-102 or Equivalent) having ON/OFF/TRIP indication lamps and push buttons, digital ammeter with CTs and selector switch ,potential free contacts for remote operation in each feeder and Auto Manual Selector Switch as required (For Cooling tower fan of 5.5 KW motor each) or as per motor sugggested by Cooling tower manufacturer).VFD shall be BMS compatible ,IP-20 rating and shall have in built choke to cater for the longer length of power cabling (Approx. 60 Rmt for each CT fan motor) without deration in the performance of the VFD.
1824.00 | Two (2) Nos. 32A TP+N MCCB with fully automatic DOL starter having contactors, O/L relay with voltage based single phase preventor suitable for operating 5.5 KW motor with ON/OFF / Trip indication lamps and push buttons, Digital ammeter with CTs and selector switch, potential free contacts for BMS Compatiability and Auto Manual Selector Switch as required (for Primary chilled Water Pumps)
1825.00 | Two (2) Nos. 63A TP+N MCCB with fully automatic Star/Delta starter having contactors, O/L relay with voltage based single phase preventor suitable for operating 11.0 KW motor with ON/OFF / Trip indication lamps and push buttons, Digital ammeter with CTs and selector switch, potential free contacts for BMS Compatiability and Auto Manual Selector Switch as required (for Condenser Water Pumps)
1826.00 | 20 Amp. DP MCB -1 Nos with ON/OFF/TRIP indication lamps, digital ammeter with CTs and selector switch (For Booster CHW pumps of 1.5 KW motor for closed expansion tank).
1827.00 | 2 Nos. compartment having Spare feeder for the following:
1828.00 | 2 Nos.63 amps TP MCCB (35 kA)
1829.00 | 1 No.100 amps TP MCCB (35 kA)
1830.00 | Outgoing for section-2
1831.00 | Following rated 415V, (icu=ics 100%) 35kA MCCB's with over current and short circuit releases thermal magnetic based (if not specified below) based with ON, indications, front operating handle & door interlock along with 2A SP MCB backup protection and control terminals & wiring as required etc. complete in all respects as mentioned in specifications and as required For each outgoing:
1832.00 | One (1) no. 320 Amp. TP+N MCCB (for 1 Chiller) with microprocessor based releases with integrated earth fault protection.
1833.00 | Two (2) nos.63 Amp. TP + N MCCB with ON/OFF/TRIP indication lamps, digital ammeter with CTs and selector switch (For secondary CHW pumps of 11.0 KW motor serving Single Office Zone)
1834.00 | One (1) no. 40 Amp. TP+N MCCB including Variable frequency drive (Model Danfoss FC-102 or Equivalent) having ON/OFF/TRIP indication lamps and push buttons, digital ammeter with CTs and selector switch ,potential free contacts for remote operation in each feeder and Auto Manual Selector Switch as required (For Cooling tower fan of 5.5 KW motor each) or as per motor sugggested by Cooling tower manufacturer).VFD shall be BMS compatible ,IP-20 rating and shall have in built choke to cater for the longer length of power cabling (Approx. 60 Rmt for each CT fan motor) without deration in the performance of the VFD.
1835.00 | One (1) No. 32A TP+N MCCB with fully automatic DOL starter having contactors, O/L relay with voltage based single phase preventor suitable for operating 5.5 KW motor with ON/OFF / Trip indication lamps and push buttons, Digital ammeter with CTs and selector switch, potential free contacts for BMS Compatiability and Auto Manual Selector Switch as required (for Primary chilled Water Pumps)
1836.00 | One (1) No. 63A TP+N MCCB with fully automatic Star/Delta starter having contactors, O/L relay with voltage based single phase preventor suitable for operating 11.0 KW motor with ON/OFF / Trip indication lamps and push buttons, Digital ammeter with CTs and selector switch, potential free contacts for BMS Compatiability and Auto Manual Selector Switch as required (for Condenser Water Pumps)
1837.00 | 1 No. compartment having Spare feeder for the following:
1838.00 | 1 No.63 amps TP MCCB (35 kA)
1839.00 | 1 No.100 amps TP MCCB (35 kA)
1840.00 | NOTE: Any change in capacity of breakers or feeders if required ,shall be identified by contractor at the time of tendering.After award, no price implication on account of change in capacity of breaker or feeder shall be accepted.
1841.00 | AHU STARTER PANEL - VFD STARTER (Type-1)
1842.00 | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted AHU starter panels including anchoring into the wall with following details:
1843.00 | All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contacts for Connections to Building Automation System.
1844.00 | The panel shall include the following components and accessories.
1845.00 | 16G CRCA Powder Coated panel enclosure with earthing studs & hinged locable doors. IP52 Protection, suitable for 415V, 3 Phase, 4 wire, 50Hz system.
1846.00 | Incomer switch shall be TPN MCB (motor duty) of required rating & 10KA fault withstand capacity for motors upto 11.0KW rating. MCB shall be with short circuit protection.
1847.00 | Incomer switch shall be TP MCCB (motor duty) of required rating & 20KA fault withstand capacity for motors beyond 11.0KW rating. MCCB shall be with overload & short circuit protection.
1848.00 | R,Y,B LED Type Phase indication lamps with control MCB's.
1849.00 | ON'/OFF/TRIP Indication LED Type lamp with control MCB.
1850.00 | ON'/OFF Push Buttons
1851.00 | VFD (Variable Frequency Drive) with all inbuilt features like protection against over load, short circuit & single phasing. VFD shall have inbuilt auto / manual / BMS operation functions selection & shall be BMS compatible. Drive shall have ON/OFF/Trip displays & metering & display of electrical parameters.Drive shall be Danfoss Vacon-20 series /Equivalent.
1852.00 | View window to read VFD parameters.
1853.00 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
1854.00 | A fire detection relay module for tripping of AHU motor on receiving fire signal & fire damper interlocking. Necessary nos. of auxillary contactors & Relays shall be included in cost as required for the interlocking with smoke extraction fans & motorised firedampers.
1855.00 | 240/24V AC Step down transformer for powering to 2 Way / 3 Way motorized valve with control MCB and wiring & conduiting upto valve in the chilled water line. 24V AC supply shall also be used for fire module relay.
1856.00 | 2 Nos of Single Pole MCB's Shall be provided at the incoming section of the starter panel for fire damper actuator & AHU limit switch/Bulk head lighting.
1857.00 | Airwasher panel shall have additional set of On/Off push button with indication ,set of contactor and overload relay for the operation of 1no. Water circulation pump (0.37 Kw) and shall be BMS compatible.
1858.00 | Scrubber panel shall have additional set of On/Off push button with indication ,set of contactor and overload relay for the operation of 1no. dry scrubber (0.37 Kw) and shall be BMS compatible.
1859.00 | Terminal block for power distribution.
1860.00 | Panel shall have adequate ventilation arrangement for heat dissipated by VFD.
1861.00 | Note: Vendor to include the cost of all related power & control cabling (for AHU door limit switch,Bulk head light etc) on GI cable tray along with copper earthing , from airhandling unit motors to VFD control panels, from Exhaust dry scrubber to control panel and from Airwasher fan motor and its pumps to control panel. (For sizes of cables ,refer to the detailed specifications of Electrical section).All cables shall be FRLS XLPE insulated armoured.
1862.00 | The no. of AHU control panels/VFD starters shall be as per KW ratings given below:
1863.00 | AHU VFD Panel for 1.1 KW Motor | 7.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1864.00 | AHU VFD Panel for 2.2 KW Motor | 2.00 | NUM |  | 28900.00 | 202300.00 | 150000.00 | 1050000.00 | 35090.00 | 245630.00 | 202300.00 | MANNU LAL AND SONS
1865.00 | AHU VFD Panel for 3.7 KW Motor | 6.00 | NUM |  | 32400.00 | 64800.00 | 175000.00 | 350000.00 | 37950.00 | 75900.00 | 64800.00 | MANNU LAL AND SONS
1866.00 | AHU VFD Panel for 5.5 KW Motor | 6.00 | NUM |  | 38800.00 | 232800.00 | 225000.00 | 1350000.00 | 47015.00 | 282090.00 | 232800.00 | MANNU LAL AND SONS
1867.00 | Airwasher VFD Panel for 2.2 KW Motor | 1.00 | NUM |  | 42300.00 | 253800.00 | 225000.00 | 1350000.00 | 48065.00 | 288390.00 | 253800.00 | MANNU LAL AND SONS
1868.00 | Airwasher VFD Panel for 5.5 KW Motor | 1.00 | NUM |  | 32400.00 | 32400.00 | 200000.00 | 200000.00 | 32430.00 | 32430.00 | 32400.00 | MANNU LAL AND SONS
1869.00 | Exhaust scrubber VFD Panel for 2.2 KW Motor | 1.00 | NUM |  | 42300.00 | 42300.00 | 225000.00 | 225000.00 | 32430.00 | 32430.00 | 32430.00 | Innovations Workspace Solutions Pvt. Ltd.
1870.00 | NORMAL EXHAUST/SMOKE EXTRACTION FAN STARTER PANEL - (Type-2)
1871.00 | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted Fan starter panels including anchoring into the wall with following details:
1872.00 | All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contacts for Connections to Building Automation System.
1873.00 | The panel shall include the following components and accessories.
1874.00 | 16G CRCA Powder Coated panel enclosure with earthing studs & hinged locable doors. IP52 Protection, suitable for 415V, 3 Phase, 4 wire, 50Hz system.
1875.00 | Incomer switch shall be TPN MCB (motor duty) of required rating & 10KA fault withstand capacity for motors upto 11.0KW rating. MCB shall be with short circuit protection.
1876.00 | Incomer switch shall be TP MCCB (motor duty) of required rating & 20KA fault withstand capacity for motors beyond 11.0KW rating. MCCB shall be with overload & short circuit protection.
1877.00 | R,Y,B LED Type Phase indication lamps with control MCB's.
1878.00 | ON'/OFF/TRIP Indication LED Type lamp with control MCB.
1879.00 | ON'/OFF Push Buttons
1880.00 | Digital ammeter with in built selector switch.
1881.00 | DOL/Star-delta starter for the ratings given below complete with contactors, over load relay with built in single phase protection. Starter shall be BMS compatible for Remote ON/Off & status monitoring complete with Auto/manual switch.
1882.00 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each Fan panel to facilitate override of the automatic operation.
1883.00 | A fire detection relay module for switching 'ON' of Fan motor on receiving fire signal & fire damper interlocking. Necessary nos. of auxillary contactors & Relays shall be included in cost as required for the interlocking with AHU fan motor & motorised firedampers.
1884.00 | 240/24V AC Step down transformer for powering 24V AC auxillary relay.
1885.00 | 2 Nos of Single Pole MCB's Shall be provided at the incoming section of the starter panel for fire damper actuator & AHU limit switch/Bulk head lighting.
1886.00 | Time delay relay for delayed automatic restart of fan motor.
1887.00 | Terminal block for power distribution.
1888.00 | Note: Vendor to include the cost of all related power & control cabling on GI cable tray along with copper earthing , from Axial flow fan/DIDW fan motors to control panels. (For sizes of cables ,refer to the detailed specifications of Electrical section).All cables shall be FRLS XLPE insulated armoured for Normal mode fans and fire survival insulated armoured for Smoke Extraction fans.
1889.00 | DOL starters upto 5.5 KW & beyond star-delta starter shall be considered.
1890.00 | The no. of FAN control panels/starters shall be as per KW ratings given below:
1891.00 | Fan starter Panel for 0.75 KW Motor | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1892.00 | Fan starter Panel for 1.1 KW Motor | 4.00 | NUM |  | 24300.00 | 24300.00 | 175000.00 | 175000.00 | 13530.00 | 13530.00 | 13530.00 | Innovations Workspace Solutions Pvt. Ltd.
1893.00 | Fan starter Panel for 1.5 KW Motor | 6.00 | NUM |  | 26300.00 | 105200.00 | 185000.00 | 740000.00 | 13530.00 | 54120.00 | 54120.00 | Innovations Workspace Solutions Pvt. Ltd.
1894.00 | Fan starter Panel for 2.2 KW Motor | 8.00 | NUM |  | 29800.00 | 178800.00 | 20500.00 | 123000.00 | 13530.00 | 81180.00 | 81180.00 | Innovations Workspace Solutions Pvt. Ltd.
1895.00 | Fan starter Panel for 3.7 KW Motor | 2.00 | NUM |  | 31000.00 | 248000.00 | 32000.00 | 256000.00 | 16390.00 | 131120.00 | 131120.00 | Innovations Workspace Solutions Pvt. Ltd.
1896.00 | Fan starter Panel for 5.5 KW Motor (Suitable for Outdoor duty) | 5.00 | NUM |  | 32101.00 | 64202.00 | 45000.00 | 90000.00 | 16390.00 | 32780.00 | 32780.00 | Innovations Workspace Solutions Pvt. Ltd.
1897.00 | Fan starter Panel for 7.5 KW Motor (Suitable for Outdoor duty) | 1.00 | NUM |  | 34900.00 | 174500.00 | 45000.00 | 225000.00 | 24750.00 | 123750.00 | 123750.00 | Innovations Workspace Solutions Pvt. Ltd.
1898.00 | Fan starter Panel for 11.0 KW Motor (Suitable for Outdoor duty) | 1.00 | NUM |  | 36700.00 | 36700.00 | 55000.00 | 55000.00 | 49390.00 | 49390.00 | 36700.00 | MANNU LAL AND SONS
1899.00 | AIR CURTAIN | 1.00 | NUM |  | 41200.00 | 41200.00 | 55000.00 | 55000.00 | 75350.00 | 75350.00 | 41200.00 | MANNU LAL AND SONS
1900.00 | SITC of high velocity Air Curtain of following size suitable for effective air through of 02 mtrs. and velocity 8/9 mtr./sec at maximum noise level 60-65 decibels and having casing(shell) of robust construction, elegent look with superior quality powder-coated finish, impeller with forwarded curved blades to minimise the air cutting noise vibration free operation, easy mounting arrangement with a flat frame which can be fixed on the wall by suitable coach screws, adjustable louvers to streamline air delivery, coupled with sturdy motors for the continuous duty operation . a) Size: 7' long.
1901.00 | CSS WORK
1902.00 | Sub-Head-I : Preamble to BOQ for (Compact Type Substation)
1903.00 | The contractor shall consider the following details in their item rates, wherever required:
1904.00 | Supporting rigid steel framework.
1905.00 | Proper bonding to earth.
1906.00 | All work shall be executed as per drawing specification and instruction of Engineer-in-charge and shall include supply and installation at site of all the equipments, ancillary material, which may be required to fulfill the complete installation as per IS and IE rules.
1907.00 | HT Metering Panel (SEB's)
1908.00 | Supplying / Receiving, Installation, Testing and Commissioning of Powder coated, 14 SWG CRCA sheet steel enclosed 11 KV H.T. Metering Panel complete with the following:
1909.00 | 1set of 11/ √3KV / 110/ √ 3 Volt, 100 VA burden & accuracy class 0.5, single phase construction, dry type cast resin PT.
1910.00 | 3 Nos. of dual core 50/5A, 15 VA burden, accuracy class CL 0.5, 11 KV cast resin CTs
1911.00 | One Set of Phase Indicating Lamps.
1912.00 | 2 Sets of HRC fuses with fuse base (H.T. Fuse - 1A & LT fuse 2-6A).
1913.00 | 2 Nos. indoor cable end box suitable for 3C x 240 sq.mm. 11 KV(E), aluminium conductor XLPE Ar. cable (Incoming & Outgoing cable).
1914.00 | 1 No. SEB approved digital Trivector meter with MDI in KVA of accuracy class - 0.5.(Accuracy class shall be as per local board)
1915.00 | Note: The contractor shall get the Trivector meter, CTs' & PT tested by SEB and the charges for liasioning for the same will be paid extra.
1916.00 | Supply Rate for Metering Panel as described above | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1917.00 | Installation & Commissioning Rate for Metering Panel as described above | 1.00 | SET |  | 367500.00 | 367500.00 | 1000000.00 | 1000000.00 | 220000.00 | 220000.00 | 220000.00 | Innovations Workspace Solutions Pvt. Ltd.
1918.00 | Note: The contractor shall ensure that the above panel meets the requirement as insisted by State/Local authorities(As per SEB) for satisfactory operation and as per the Drawings
1919.00 | 11kV Compact Sub-Station | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1920.00 | Design, fabrication, assembling, wiring, supply, testing at works, packaging, forwarding to site and supervising the testing & commissioning of 11kV compact secondary substation suitable for Outdoor installation with natural cooling, having type tested equipments comprising of oil-type distribution transformer and SF-6 insulated compact switchgear enclosed in robotically sealed stainless steel tank, low-voltage switchboard, interconnection between HT switchgear and transformer using cables and transformer to LT-switchgear using aluminium busbars, factory built ready for connection type, internal GI earthing provided complete with other associated equipments etc. complete as required conforming to IEC 62271-202 and relevant IS or international specifications, as regards to design, manufacturing, type-testing, routine-testing and operator safety (IAC AFLR). The enclosure shall have modular construction using G.I. Sheet and shall be powder-coated from exterior. The Transformer compartment will have IP-23 ingress protection, whereas the HT/LT compartment will have IP-54 protection. (Factory test or load test as per IS 2026 & IEC 60076)
1921.00 | The 11kV Outdoor Compact Sub-Station shall be consisting of following ,
1922.00 | HT SWITCHGEAR
1923.00 | 11kV 630Amps 20kA for 3 sec. & tested for 20kA/ 1 sec internal arc , SF6 insulated Non-Extensible Compact switchgear consisting of One No. Direct Module for Incomer and one No. of Fixed Manual Vacuum Circuit Breaker in SF6 insulated Stainless steel enclosure with series trip,self powered microprocessor based numerical over current and Earth Fault (IDMT+Inst.) relay protection along with. Interconnection between HT switchgear and transformer shall be using 3Cx240 sq.mm Al. armorured XLPE Cable.....1 Set
1924.00 | TRANSFORMER
1925.00 | 1no. 1000KVA 11KV/433V Dyn11 Oil filled hermatically sealed transformer without conservator type of design having corrugated tank & Top normal porcelein Bushings for HT & LT with OLTC and RTCC switch of rating +5% to -15% @2.5%. Temp Rise - Oil/Winding 40/50 deg cel, NL/FL Losses = 1.4/14 KW (Subject to IS Tol.), Impedanace 5% (Subject to IS Tol.) .....1 Set
1926.00 | Oil temperature Indicator, Winding Temperature indicator with Alarm and Trip Contact…..1 Set
1927.00 | LVS PANEL -2000AMPS ALUMINIUM BUSBARS….1Set
1928.00 | INCOMER
1929.00 | 1 Nos. 1600A, 50KA 4 pole microprocessor based EDO, ACB with integral protection
1930.00 | OUTGOING
1931.00 | Direct Cable termination Suitable for 5 nos 3.5 core 300 sqmm, 1100 V grade, XLPE insulated PVC sheathed Arnoured Aluminium cables
1932.00 | APFC (Automatic Powerfactor control)
1933.00 | 330 kVAR APFC with 50X4, 25X3, 15X3,5X2 KVAR MPP type capacitor with MCCB/MCB/contactor & 12 step RVC relay with 800 Amp. 3P MCCB for incomer to APFC…..1 Set
1934.00 | OUTDOOR ENCLOSURE
1935.00 | Outdoor type enclosure with slanted roof & having construction of Galvanised Sheet Steel of thickness 1.5/2mm. The enclosure shall be type tested for IAC 20 kA/ 1 sec AB class as well as impact test as per IEC 62271-202 or international standards with reports not later than 5 years. The Enclosure shall have IP54 degree of protection for HT & LT switchgear compartment & IP23 degree of protection for Transformer compartment with transformer compartment thermal class of K-20 as per latest IEC. The enclosure shall be Powder Coated (Colour Light Gray & D.A.Gray ). Each compartment will be provided with the door and pad locking arrangement. The Compartment illumination lamp with door operated switch shall be provided for each compartment.....1 Set
1936.00 | INTERCONNECTION AND EARTHING
1937.00 | Interconnection Between HT switchgear & Transformer using 3Cx240Sq.mm XLPE Single core cable & Interconnection between Transformer & LT switchgear using Aluminium Busbars. Internal earthing connections by using 50x6 mm GI strips…...1 Set
1938.00 | Supply of 11kV Compact Substation including Receiving,unloading , shifting at designated place, fixing, testing & commissioning as per specifications described above.
1939.00 | 11 kV 2 POLE STRUCTURE | 1.00 | SET |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1940.00 | Supply, installation, testing & commissioning of two 11Mtr. pole structure, 11KV with cross arms, suitable clamps, insulators, disc insulators, 11KV lightning arrestors, complete stay with insulator & wire, foundations, gang operated air break switch with extended handle, 11KV drop out fuses. This shall have termination arrangement for outgoing through HT XLPE cable of suitable size and necessary 6 inches dia GI pipe shall be provided for cable support complete in every way.
1941.00 | WATER FOUNTAIN WORK
1942.00 | Water Feature 1:- Providing, fixing, testing & commissioning of Bubbler Jet with water fall Fountain
1943.00 | Providing, fixing, testing & commissioning of Nozzles
1944.00 | Supply, Installation, Testing & Commissioning of Bubbler Jet 1.5" Nozzles Standard.etc., complete | 20.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1945.00 | Supply, Installation, Testing & Commissioning of White ABS plastic bottom inlet 2" for concrete with S.S. screws and regulable .. Flow/ inlet = 4,000 l/hr. | 6.00 | NUM |  | 9000.00 | 180000.00 | 2250.00 | 45000.00 | 4600.00 | 92000.00 | 45000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1946.00 | Providing, fixing, testing & commissioning of Lights
1947.00 | Supply, Installation, Testing & Commissioning of SS 316 Niche Light 12V 18Watt RGB/WW (3watt x 6Nos Led) With Niche Standard etc., complete | 50.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1948.00 | Supply, Installation, Testing & Commissioning of Power Supply, | 10.00 | NUM |  | 9661.00 | 483050.00 | 4165.00 | 208250.00 | 4600.00 | 230000.00 | 208250.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1949.00 | Providing, fixing, testing & commissioning of Pump
1950.00 | Supply, installation, testing and commissioning of single stage/Horizontal Openwell submersible pump 10HP | 2.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1951.00 | Supply, installation, testing and commissioning of single stage/Horizontal Openwell submersible pump 2HP | 1.00 | NUM |  | 56000.00 | 112000.00 | 70384.00 | 140768.00 | 51750.00 | 103500.00 | 103500.00 | Innovations Workspace Solutions Pvt. Ltd.
1952.00 | Providing, fixing, testing & commissioning of Filter
1953.00 | Supply, Installation, Testing & Commissioning of TOTALLY ANTI- CORROSIVE Bobbin Wound filter,700mm diameter. Fitted with pressure gauge panel manual air bleeder, water drain and emptying plug.fitted with collector arms and diffuser made from unplasticizedPVC and polypropelene .etc., complete. Max.EN ISO 9001 :2000 Standard.working pressure : 2.5 kg/cm². Flow rate = 16m³/hr. | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1954.00 | Sand for Sand Filter (SIZE 16/32 Mesh) | 300.00 | KG |  | 65000.00 | 65000.00 | 37145.00 | 37145.00 | 59800.00 | 59800.00 | 37145.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1955.00 | Providing, fixing, testing & commissioning of Control Panel (Equipments Make-L & T, Heger, Elmex, Rishabh, FTC, Esbee, Salzer etc.) | 1.00 | LS |  | 20.00 | 6000.00 | 150.00 | 45000.00 | 15.00 | 4500.00 | 4500.00 | Innovations Workspace Solutions Pvt. Ltd.
1956.00 | Supply & Commisioning of control panel complete as required. MCC(L&T)Relay(L&T)Push Bottom(Surdhi)Indicator(Surdhi)Auto Mannul Switch(Selzer)Auto Timer(L&T) Contactors(L&T)as described above and below.etc., complete DOL Starter
1957.00 | Ammeter(Selec),Volt Meter(Selec),
1958.00 | Lugs, Wires, Enclosure, .
1959.00 | Centrifugal Pump and power supply and automation for pump
1960.00 | Providing & fixing of Wires/cables of various sizes including necessary accessories(Flexible Round Cable) as per Design | 1.00 | LS |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1961.00 | Wire 2.5mm Two Core (Round)
1962.00 | Wire 2.5mm Three Core (Flat)
1963.00 | Wire 4mm Three Core (Flat)
1964.00 | PVC Conduit 25mm
1965.00 | Providing and fixing of pipes (uPVC pipe- 10 kg. Pressure) & fittings (Heavy) | 1.00 | LS |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1966.00 | Providing & fixing of Valves, fittings etc of required size | 1.00 | LS |  | 150000.00 | 150000.00 | 100000.00 | 100000.00 | 74750.00 | 74750.00 | 74750.00 | Innovations Workspace Solutions Pvt. Ltd.
1967.00 | FURNITURE WORKS
1968.00 | Furniture works 1. The furniture product should be from the manufacture which have BIFMA Certification, GREENGUARD/ GREENPRO, AIOTA Certification. 2. The dimensions of the furniture as given in the respective items as below are indicative and there shall be no deviation of cost on account of this. However, the dimensions mentioned below may vary in between ± 10% during execution as directed by Engineer-In-Charge.
1969.00 | Reception table- Providing and fixing 4000 x 1000 x 1050/ 750 made out of 25mm thk commercial board as per approved drawing. The table finish include 60% Corian 20% laminate and 10% lacquered glass as per dimension, shape, size and colour. The Corian shall be buffed/ polished as per direction by engineer in charge. Provision for LED Light as per drawing shall be provided. Additional structure for the Cable Cubbies, VC connectivity's etc. The finishes to be of the highest quality standard conforming to the best of world class workmanship. And nothing extra shall be payable on this account. | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1970.00 | Drawer Pedestal - : Providing & making 2 Side Units for reception table made of 18 mm thick MDF top, sides, bottom, drawers of size 400mm width, 450mm long and 600 mm height finished with 1.0 mm laminate at top & sides, and 0.8 mm laminate on the inner sides. Side Unit will have 3 nos. of drawers with central locking arrangement, running on sliding channels. Drawers will be made of 12mm thick MDF sides, front & back with 4 mm thick base ply. Also 12 mm ply will be fixed on back side of unit. All internal surfaces will be finished with 0.8 mm laminate approved colour & shade complete as per instructions/ detail drawings at site. | 1.00 | NUM |  | 300000.00 | 300000.00 | 150000.00 | 150000.00 | 187500.00 | 187500.00 | 150000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1971.00 | Linear Workstation for Security Staff room/Working Hall/Technical room | 22.00 | NUM |  | 8000.00 | 8000.00 | 7500.00 | 7500.00 | 31250.00 | 31250.00 | 7500.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
1972.00 | Dimension: 1200mm(L) x 600mm(D) x 1200mm(H)
1973.00 | Supplying and placing in position of sliding tile/Panel base modular Workstation as per photograph/drawing. Free standing partition height 1200mm and should be minimum of 60-70mm thick. Partition inner frame is 1.1-1.2 mm thick mild steel/Aluminium. Horizontal and vertical trims are made out of extruded aluminium of 1.mm thick. All Panels/trims shall be powder coated with 50 microns. Aluminium trims are elegantly fixed with special fixtures in the partition. The frame work shall be fitted with 9mm thick pre laminated Particle tiles of approved shade. Partition shall have provision for pin up board with fabric/ white marker/ laminated of approved shade. Partition framework shall have adequate provisions for the movement of electric data cables at desired 2 levels; one at skirting and another above / below the table top. The complete partitioning work shall be carried out as per the approved drawing. Table top for workstation made up of 25mm thick pre laminated Particle board of approved shade. The worktop shall be supported on minimum 2mm thick powder coated CRCA brackets and side panels. Side’s panels should be made from 18mm thick pre laminated Particle board of approved shade. All working or non-working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. . Provision of one PVC keyboard tray and Metal CPU trolley with lockable castors for each seating. Also a provision of Mobile Pedestal Unit (size: - L-400mm x D-450mm x H-600mm) with a combination of 2 drawer & one filing drawer. The pedestal storage unit shall be made of 18 mm thick prelaminated Particle board with provision of handles & central Locking arrangement. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1974.00 | L-Shape Workstation for Security Staff room/ Working hall/ PS with Steno | 125.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1975.00 | Dimension: 1500mm(L) x 1350mm(L) x 600mm(D) x 1200mm(H)
1976.00 | Supplying and placing in position of sliding tile/Panel base modular Workstation as per photograph. Free standing partition height 1200mm and should be minimum of 60-70mm thick. Partition inner frame is 1.2-1.5mm thick mild steel/Aluminium. Horizontal and vertical trims are made out of extruded aluminium of 1.2-1.5mm thick. All Panels/trims shall be powder coated with 50 micron. Aluminium trims are elegantly fixed with hidden connectors on the partition. The frame work shall be fitted with 8mm thick pre laminated Particle tiles of approved shade. Partition shall have provision for pin up board with fabric/ white marker/ laminated of approved shade. Partition framework shall have adequate provisions for the movement of electric data cables at desired 2 levels; one at skirting and another above / below the table top. The complete partitioning work shall be carried out as per the approved drawing. Table top for workstation made up of 25mm thick pre laminated Particle board of approved shade. The worktop shall be supported on minimum 2mm thick powder coated CRCA brackets and side panels. Side’s panels should be made from 18mm thick pre laminated Particle board of approved shade. All working or non-working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. Provision of one PVC keyboard tray and CPU trolley for each seating. Also a provision of Pedestal Unit (size: - L-400mm x D-450mm x H-600mm) with a combination of 2 drawer & one filing drawer. The pedestal storage unit shall be made of 18 mm thick prelaminated Particle board with provision of handles & locking arrangement the product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1977.00 | Medium height Storage for Security Staff room/Technical Room
1978.00 | Dimension: 2700mm(L) x 450mm(D) x 1200mm(H) | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1979.00 | Dimension: 1300mm(L) x 450mm(D) x 1200mm(H) | 8.00 | NUM |  | 30954.00 | 30954.00 | 40000.00 | 40000.00 | 28350.00 | 28350.00 | 28350.00 | Innovations Workspace Solutions Pvt. Ltd.
1980.00 | Dimension: 1400mm(L) x 450mm(D) x 1200mm(H) | 16.00 | NUM |  | 15484.00 | 123872.00 | 19000.00 | 152000.00 | 13650.00 | 109200.00 | 109200.00 | Innovations Workspace Solutions Pvt. Ltd.
1981.00 | Dimension: 6000mm(L) x 450mm(D) x 1200mm(H) | 2.00 | NUM |  | 16500.00 | 264000.00 | 20000.00 | 320000.00 | 14700.00 | 235200.00 | 235200.00 | Innovations Workspace Solutions Pvt. Ltd.
1982.00 | Dimension: 2000mm(L) x 450mm(D) x 1200mm(H) | 20.00 | NUM |  | 66339.00 | 132678.00 | 86400.00 | 172800.00 | 63000.00 | 126000.00 | 126000.00 | Innovations Workspace Solutions Pvt. Ltd.
1983.00 | Dimension: 950mm(L) x 450mm(D) x 1200mm(H) | 16.00 | NUM |  | 23220.00 | 464400.00 | 29000.00 | 580000.00 | 21000.00 | 420000.00 | 420000.00 | Innovations Workspace Solutions Pvt. Ltd.
1984.00 | Dimension: 2480mm(L) x 450mm(D) x 1200mm(H) | 12.00 | NUM |  | 9949.00 | 159184.00 | 13680.00 | 218880.00 | 9975.00 | 159600.00 | 159184.00 | MANNU LAL AND SONS
1985.00 | Dimension: 2970mm(L) x 450mm(D) x 1200mm(H) | 3.00 | NUM |  | 28194.00 | 338328.00 | 36000.00 | 432000.00 | 26040.00 | 312480.00 | 312480.00 | Innovations Workspace Solutions Pvt. Ltd.
1986.00 | Dimension: 1850mm(L) x 450mm(D) x 1200mm(H) | 16.00 | NUM |  | 33169.00 | 99507.00 | 43000.00 | 129000.00 | 31185.00 | 93555.00 | 93555.00 | Innovations Workspace Solutions Pvt. Ltd.
1987.00 | Dimension: 1600mm(L) x 450mm(D) x 1200mm(H) | 17.00 | NUM |  | 21559.00 | 344944.00 | 26640.00 | 426240.00 | 19425.00 | 310800.00 | 310800.00 | Innovations Workspace Solutions Pvt. Ltd.
1988.00 | Supplying, and placing in position of medium height storage @ 1200mm height as per photograph/drawing. Storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. Each unit to have openable shutters with handles & locking provision. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1989.00 | Emergency Response Table | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1990.00 | Dimension: 4450mm(L) x 1500mm(D) x 750mm(H)
1991.00 | Supplying and placing in position of meeting table as per drawing. Table top made out of 25mm Thk Prelam particle board Table Top with 2mm PVC Edge Banding on all Exposed edges.The table top supported on Mild Steel 50mm x50mm Slanted Leg and 50mm x 25mm Horizontal connectors with Powder coating of 50 Micron.Wire Management : 220/350mm Flip Up with soft closure and on Metal Cable Tray, Vertical wire entry cover considered for Power and data Management. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1992.00 | Main Table for DGM Cabin/ CA room/Doctors Room | 24.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1993.00 | Main Table Dimension: (L)2100mm X (D)900mm X (H)750mm All over Side Runner Dimension: (L)1900mm X (D)450mm X (H)750mm
1994.00 | Providing and placing of table as per drawing. . Table top made up of 25mm thick pre-laminated particle board and understructure shall be made of 18mm thick prelaminated particle board gable ends and modesty panels. The working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. Provision of 3 drawer mobile pedestal, one CPU trolley and PVC keyboard tray attached to the table top. The table shall be provisioned with free standing. Storage Top made out of 25mm thick pre laminated particle board and rest all storage to be made out of 18 mm thick prelaminated particle board . Storage having a openable shutter with handles and central locking arrangement. All exposed edges shall be provided with machine pressed 2 mm thick PVC lipping glued with hot melt EVA glue. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1995.00 | Back Storage for DGM Cabin/ CA room | 24.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1996.00 | Dimension: (L)3000mm X (D)450mm X (H)750mm
1997.00 | Supplying, and placing in position of back storage as per photograph/drawing. The complete storage unit shall be made up of 18 mm thick Prelam particle board with 2mm thk PVC edge banding. The storage shall be provisioned with one shelf and 2 nos compartments .The storage shall have openable shutters with handles and locking arrangements. All working or non-working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
1998.00 | Main Table for Ex. Cubicle | 60.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
1999.00 | Main Table Dimension : 1650mm(L) X 750mm(d) x 750mm(h) Side Runner Dimension: 900mm(L) X 450mm(d) x 750mm(h)
2000.00 | Supplying, and placing in position of main Table as per drawing. Modular tables size 1650mm (L) x 750mm (D) x 750mm (H).The Table top made out of 25mm thk Prelam particle board with 2mm thk pvc edge banding & side panel & modesty panel made up of 18mm thick pre-laminated particle board .The working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. The table have a provision of free standing Side Storage of size 900mm L x 450mm D x 750mm Ht., Storage Top made out of 25mm thick pre laminated particle board and rest all storage to be made out of 18 mm thick prelaminated particle board . All exposed edges shall be provided with machine pressed 2 mm thick PVC lipping glued with hot melt EVA glue. Storage having provision of 3 drawer unit, one openable shutter, one open storage with handle & central locking provision. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2001.00 | Back Storage for Ex. Cubicle | 60.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2002.00 | Dimension: (L)2100mm X (D)450mm X (H)750mm
2003.00 | Supplying, and placing in position of back storage as per photograph/drawing. The complete storage unit shall be made up of 18 mm thick Prelam particle board with 2mm thk PVC edge banding. The storage shall be provisioned with one shelf and 2 nos compartments .The storage shall have openable shutters with handles and locking arrangements. All working or non-working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2004.00 | Medium height Storage for Ex. Cubicle room
2005.00 | Dimension: (L)1725mm X (D)450mm X (H)1200mm | 30.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2006.00 | Dimension: (L)1920mm X (D)450mm X (H)1200mm | 8.00 | NUM |  | 19912.00 | 597360.00 | 25000.00 | 750000.00 | 18375.00 | 551250.00 | 551250.00 | Innovations Workspace Solutions Pvt. Ltd.
2007.00 | Supplying, and placing in position of medium height storage @ 1200mm height as per photograph/drawing. Storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. Each unit to have openable shutters with handles & locking provision. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2008.00 | Medium height Storage for Passage area
2009.00 | Dimension: (L)2400mm X (D)450mm X (H)1200mm | 3.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2010.00 | Dimension: (L)1725mm X (D)450mm X (H)1200mm | 2.00 | NUM |  | 26541.00 | 79623.00 | 35000.00 | 105000.00 | 25200.00 | 75600.00 | 75600.00 | Innovations Workspace Solutions Pvt. Ltd.
2011.00 | Dimension: (L)1350mm X (D)450mm X (H)1200mm | 1.00 | NUM |  | 19912.00 | 39824.00 | 25000.00 | 50000.00 | 18110.00 | 36220.00 | 36220.00 | Innovations Workspace Solutions Pvt. Ltd.
2012.00 | Supplying, and placing in position of medium height storage @ 1200mm height as per photograph/drawing. Storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. Each unit to have openable shutters with handles & locking provision. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2013.00 | Conference / Meeting table- : Diamond Shaped : providing and fixing of the following as per design, Using Action Tesa High Gloss/Matt finish 18mm Pre Laminated Board, Fixed on 25 mm pre laminated MDF base TOP, with support structure of BSL MDF of matching design, Complete with SS T strip on the edge, Additional structure for the Cable Cubbies, VC connectivity's etc. The finishes to be of the highest quality standard conforming to the best of world class workmanship.
2014.00 | TABLE-1 4600 X 1500 | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2015.00 | TABLE-2 6000 X 1500 | 1.00 | NUM |  | 125000.00 | 125000.00 | 85000.00 | 85000.00 | 53905.00 | 53905.00 | 53905.00 | Innovations Workspace Solutions Pvt. Ltd.
2016.00 | TABLE-3 7000 X 1500 | 1.00 | NUM |  | 152000.00 | 152000.00 | 108000.00 | 108000.00 | 70315.00 | 70315.00 | 70315.00 | Innovations Workspace Solutions Pvt. Ltd.
2017.00 | TABLE-4 6000 X 1500 | 1.00 | NUM |  | 175000.00 | 175000.00 | 126000.00 | 126000.00 | 82030.00 | 82030.00 | 82030.00 | Innovations Workspace Solutions Pvt. Ltd.
2018.00 | TABLE-5 6000 X 1500 | 1.00 | NUM |  | 152000.00 | 152000.00 | 108000.00 | 108000.00 | 70315.00 | 70315.00 | 70315.00 | Innovations Workspace Solutions Pvt. Ltd.
2019.00 | TABLE-6 11000 X 2000 | 1.00 | NUM |  | 152000.00 | 152000.00 | 108000.00 | 108000.00 | 70315.00 | 70315.00 | 70315.00 | Innovations Workspace Solutions Pvt. Ltd.
2020.00 | Back storage for GM Cabin-01,02/ CGM Cabin | 7.00 | NUM |  | 390000.00 | 390000.00 | 108000.00 | 108000.00 | 180125.00 | 180125.00 | 108000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
2021.00 | Dimension:(L)3800mm X (D)450mm X (H)750mm
2022.00 | Supplying, and placing in position of back storage as per photograph/drawing. The complete storage unit shall be made up of 18 mm thick Prelam particle board with 2mm thk PVC edge banding. The storage shall be provisioned with one shelf and 2 nos compartments .The storage shall have openable shutters with handles and locking arrangements. All working or non-working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2023.00 | Main Table for PS to GM Cabin/ PS with Steno | 6.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2024.00 | Main Table Dimension: 1650mm(L) X 750mm(d) x 750mm(h) Side Runner Dimension: 900mm(L) X 450mm(d) x 750mm(h)
2025.00 | Providing and placing of table as per drawing. Modular tables size 1650mm (L) x 750mm (D) x 750mm (H). Table top made up of 25mm thick pre-laminated particle board and understructure shall be made of 18mm thick prelaminated particle board gable ends and modesty panels. The working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. Provision of 3 drawer mobile pedestal, one CPU trolley and PVC keyboard tray attached to the table top. The table shall be provisioned with free standing Side Storage of size 900mm L x 400mm D x 750mm Ht., Storage Top made out of 25mm thick pre laminated particle board and rest all storage to be made out of 18 mm thick prelaminated particle board . Storage having a openable shutter with handles and central locking arrangement. All exposed edges shall be provided with machine pressed 2 mm thick PVC lipping glued with hot melt EVA glue. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2026.00 | Back Storage for PS to GM Cabin/ PS with Steno/ CGM Cabin/ED Cabin-01 | 6.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2027.00 | Dimension: 2480mm(L) X 450mm(d) x 750mm(h)
2028.00 | Supplying, and placing in position of medium height storage @ 750mm height as per photograph/drawing. Storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. Each unit to have openable shutters with handles & locking provision. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2029.00 | INCHARGE TABLE- providing and fixing 4000 x 900 x 750 made out of 25mm thk commercial board as per approved drawing. The table finish include veneer whereever required as per dimension, shape, size and colour. The Corian shall be buffed/ polished as per direction by engineer in charge. Provision for LED Light as per drawing shall be provided. Additional structure for the Cable Cubbies, VC connectivity's etc. The finishes to be of the highest quality standard conforming to the best of world class workmanship. And nothing extra shall be payable on this account. | 2.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2030.00 | Back Storage for INCHARGE | 4.00 | NUM |  | 150000.00 | 300000.00 | 35000.00 | 70000.00 | 237500.00 | 475000.00 | 70000.00 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED
2031.00 | Dimension:(L)3500mm X (D)450mm X (H)750mm
2032.00 | Supplying and placing in position of 18mm thick plywood with laminate finish back storage as per image. A well-built bookcase with the looks this is the complete package. A compartmentalized shelving system with adequate space ensures any book will fit in the shelf. This Bookshelf is built using plywood with laminate with 2mm thick PVC edges.. The lower cabinets provide an alcoved space to ensure your books don't yellow with age. The lower area to be provisioned with openable shutters with handles and locking arrangements. The upper area to have open shelves for display. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2033.00 | Main table for BMS room/Fire control room/ CCTV Control room/ Dispatch room/RGMC/CGD Control room | 8.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2034.00 | Dimension: 1200mm(L) X 600mm(D) X 750mm(H)
2035.00 | Supplying, and placing in position of free standing table as per Image/drawing. The table top are made up of 25mm thick pre-laminated particle board with 2mm thk PVC edge banding. The Table supported with 18mm thk Prelam Particle board side panel & Modesty panel. The working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. Provision of one fixed Pedestal storage unit (combination of two drawers and one filing drawer). Pedestal Unit made of 18mm thk prelaminated particle board with 2mm thk PVC edge banding. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2036.00 | Medium Height storage for Dispatch room | 1.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2037.00 | Dimension: 1800mm(L) X 450mm(D) x 1200mm(H)
2038.00 | Supplying, and placing in position of medium height storage @ 1200mm height as per photograph/drawing. The storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. The storage unit having openable shutters withD shape handles & locking arrangement. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2039.00 | Full Height storage fort Record room | 12.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2040.00 | Dimension : 900mm(L) X 450mm(D) X 1800mm(H)
2041.00 | Supplying, and placing in position of full height storage @ 1800mm height as per photograph/drawing. The storage unit having Openable shutters with shelf in it. The modular storage unit top shall be made from 18 mm thick pre-laminated particle board and rest of the sides as well as shelves and shutter to be made up of 18 mm thick pre-laminated particle board while back to be made of 8 mm thick pre-laminated particle board. All edges to be provided with 2 mm thick PVC lipping. The modular storage have openable shutters with Dshape handles and locking arrangement. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2042.00 | Medium height partition | 460.00 | M2 |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2043.00 | Supplying and placing in position of sliding tile/Panel base medium ht partition as per photograph/drawing. Free standing partition height 1200mm and should be minimum of 65-67mm thick. Partition inner frame is 1.1-1.2 mm thick mild steel/Aluminium. Horizontal and vertical trims are made out of extruded aluminium of 1.mm thick. All Panels/trims shall be powder coated with 50 microns. Aluminium trims are elegantly fixed with special fixtures in the partition. The frame work shall be fitted with 9mm thick pre laminated Particle tiles of approved shade. Partition shall have provision for pin up board with fabric/ white marker/ laminated of approved shade. Partition framework shall have adequate provisions for the movement of electric data cables at desired 2 levels; one at skirting and another above / below the table top. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2044.00 | Main Table for GM Cabin-01,02/ CGM Cabin | 7.00 | NUM |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
2045.00 | Main Table Dimension:(L)2400mm X (D)1130mm X (H)770mm Side Runner Dimension: :(L)1200mm X (D)600mm X (H)770mm
2046.00 | Providing and placing of table as per drawing. Table top made up of 25mm thick pre-laminated particle board and understructure shall be made of 18mm thick prelaminated particle board gable ends and modesty panels. The working edges shall be provided with machine pressed 2mm thick PVC edging using special hot melt glue at hot temperature. Provision of 3 drawer mobile pedestal, one CPU trolley and PVC keyboard tray attached to the table top. The table shall be provisioned with free standing, Storage Top made out of 25mm thick pre laminated particle board and rest all storage to be made out of 18 mm thick prelaminated particle board . Storage having a openable shutter with handles and central locking arrangement. All exposed edges shall be provided with machine pressed 2 mm thick PVC lipping glued with hot melt EVA glue. The product should be same as per the specification as above & ref image under the guidance of project architect and Engineer in charge. Make: Godrej, HNI, Spacewood Office Solutions (SOS), Herman Miller, Geeken
2047.00 | Total Amount of all items (Sl No. 1 to Sl No. 2046) excluding GST
2048.00 | GST (CGST&SGST/UTGST or IGST) in percentage (%) on Total Amount of all items (i.e. GST on Sl No. 2047 above) | 1.00 | percentage |  | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted | Not Quoted
| Total in Figures |  |  |  |  | 259181168.00 |  | 298825270.75 |  | 266991574.03
Lowest Amount Quoted BY: MANNU LAL AND SONS(259181168.00)

## BOQ Summary
BOQ Summary Details Tender Title: INTERIOR, MEP AND RELATED WORKS FOR OFFICE BUILDING AT RANCHI, JHARKHAND Tender ID: 2024_GAIL_188833_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | MANNU LAL AND SONS | 259181168.00 | L1
| 2 | Innovations Workspace Solutions Pvt. Ltd. | 266991574.03 | L2
| 3 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED | 298825270.75 | L3

## Preferential Bidder BOQ Summary
Preferential Bidder Non-Itemwise BOQ Summary Details Tender Title: INTERIOR, MEP AND RELATED WORKS FOR OFFICE BUILDING AT RANCHI, JHARKHAND Tender ID: 2024_GAIL_188833_1
Sheet Name | Sl.No | Bidder Name | Amount | Difference Amount from L1 | Difference Percentage from L1 | Tolerance Percentage | Preference Category
BoQ1 | 1 | MANNU LAL AND SONS | 259181168.00 |  |  | 20.00% | Make in India
| 2 | Innovations Workspace Solutions Pvt. Ltd. | 266991574.03
| 3 | RAM KRIPAL SINGH CONSTRUCTION PRIVATE LIMITED | 298825270.75