## BoQ1
Government eProcurement System Created By: NIREEKSHANA RAO K Created Date/Time: 09-Sep-2024 11:48 AM Tender Title: SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF AUTOMATIC CO2 FLOODING SYSTEM AT SSLNG SITE AT GAIL VIJAIPUR. Tender ID: 2024_GAIL_199286_1
Tender Inviting Authority: GAIL INDIA LTD, VIJAIPUR
Name of Work: SUPPLY, INSTALLATION, TESTING & COMMISSIONING OF AUTOMATIC CO2 FLOODING SYSTEM AT SSLNG SITE AT GAIL VIJAIPUR.
Tender No: GAIL/VH/C24060/NR/F&S/2024 (NIC TENDER ID: 2024_GAIL_199286_1) & DATE: 25.06.2024
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S. Safe N Secure Fire Systems (GSTN-27BDLPK4182N1ZX) BID ID -720558 |  | Newage Fire Protection Engineers Pvt. Ltd. (GSTN-27AACCN9026C1ZN) BID ID -721576 |  | New Fire Engineers Pvt. Ltd.(GSTN-NA)--721359 |  | chetan engineers(GSTN-NA)--721163
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | CO2 Flooding System for ZPTS skid: Supply, installation, testing & commissioning of automatic CO2 Flooding System for ZPTS skid comprising of Seamless cylinders of 22.5 Kg Capacity filled with CO2 gas (CCOE Approved) with safety burst disc,a safety cap dicharge valves,manifold, discharge hose, interconnection pipe, System cabinet/enclosure to prevent from rain/sunlight, low weight sensing mechanism and 24VDC electrically operated solenoid coil arrangement to release the Co2 gas. All the electrical devices, associate fittings and junction box etc. in and around process units should be suitable for Zone-1 Area classification and shall have valid PESO certifcation. Required CO2 Cylinders stand frame and enclosure for CO2 system and supply of mandatory spare list as per tender document shall also included in bidder's scope. The Contractor has to furnish flow calculations through nozzles and submit all the drawings, documents for approval. Detailed bidder's scope mentioned in SCC & SOW of tender document. | 2.00 | Each |  | 443600.00 | 1046896.00 | 395948.71 | 934438.95 | 1160050.00 | 2737718.00 | 821453.00 | 1938629.08 | 934438.95 | Newage Fire Protection Engineers Pvt. Ltd.
2.00 | CO2 Flooding System for Cryobox Skid: Supply, installation, testing & commissioning of automatic CO2 Flooding System for Cryobox Skid comprising of Seamless cylinders of 22.5 Kg Capacity filled with CO2 gas (CCOE Approved) with safety burst disc,a safety cap dicharge valves,manifold, discharge hose, interconnection pipe, System cabinet/enclosure to prevent from rain/sunlight low weight sensing and 24VDC electrically operated solenoid coil arrangement to release the Co2 gas. All the electrical devices, associate fittings and junction box etc. in and around process units should be suitable for Zone-1 Area classification and shall have valid PESO certifcation. Required CO2 Cylinders stand frame and enclosure for CO2 system and supply of mandatory spares list as per tender document shall also included in bidder's scope. The Contractor has to furnish flow calculations through nozzles and submit all the drawings, documents for approval. Detailed bidder's scope mentioned in SCC & SOW of tender document. | 2.00 | Each |  | 512250.00 | 1208910.00 | 620065.47 | 1463354.52 | 1264825.00 | 2984987.00 | 1263430.00 | 2981694.80 | 1208910.00 | M/S. Safe N Secure Fire Systems
3.00 | Spare CO2 cylinedrs 22 KG: Spare PESO approved CO2 cylinders of capacity 22.5kg, compatible with master or slave cylinder of abaove mentioned system | 4.00 | Each |  | 39400.00 | 157600.00 | 44517.36 | 210121.93 | 41000.00 | 193520.00 | 62500.00 | 295000.00 | 157600.00 | M/S. Safe N Secure Fire Systems
| Total in Figures |  |  |  |  | 2413406.00 |  | 2607915.40 |  | 5916225.00 |  | 5215323.88
Lowest Amount Quoted BY: M/S. Safe N Secure Fire Systems(2413406.00)

## BOQ Summary
BOQ Summary Details Tender Title: SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF AUTOMATIC CO2 FLOODING SYSTEM AT SSLNG SITE AT GAIL VIJAIPUR. Tender ID: 2024_GAIL_199286_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S. Safe N Secure Fire Systems | 2413406.00 | L1
| 2 | Newage Fire Protection Engineers Pvt. Ltd. | 2607915.40 | L2
| 3 | chetan engineers | 5215323.88 | L3
| 4 | New Fire Engineers Pvt. Ltd. | 5916225.00 | L4