## BoQ1
Government eProcurement System Created By: RAJNEESH KUMAR Created Date/Time: 04-Oct-2024 11:28 AM Tender Title: SUPPLY INSTALLATION COMMISSIONING AND CALIBRATION OF LEL DETECTORS UNDER DIBIYAPUR REGION Tender ID: 2024_GAIL_202861_1
Tender Inviting Authority: GAIL (INDIA)LTD
Name of Work:SUPPLY, INSTALLATION, COMMISSIONING & CALIBRATION OF LEL DETECTORS UNDER DIBIYAPUR REGION THROUGH NIC PORTAL
Contract No: Tender Ref No: 2024_GAIL_202861 _1 (GAIL/AU/C&P/24-25/P-045/RK)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DETECTION INSTRUMENTS INDIA PVT LTD (GSTN-27AAACD1659F1ZU) BID ID -736649 |  | Safe-Tronics Automation Pvt. Ltd. (GSTN-NA) BID ID -736072 |  | HI POINT SERVICES (I) PRIVATE LIMITED (GSTN-NA) BID ID -733617
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | DETECTOR, GAS, HYDROCARBON, INFRARED, LEL LEL Detector, IR type, SIL2, HC Service along with Relay with base, 24V, Analogue Inpur barrier, Flameproof Hooter with flasher, 24V and MCB- 6 AMP, 24VDC | 10.00 | EA |  | 105000.00 | 1239000.00 | 170409.00 | 2010826.20 | 173576.00 | 2048196.80 | 1239000.00 | DETECTION INSTRUMENTS INDIA PVT LTD
1.02 | Supply, Installation & Commissioning charges for LEL detector at SV stations (25 SV's & 2 LEL detectors per SV) along with SITC of all other accessories to complete this turnkey project shall be covered under this SoR (Schedule of rate) 1.Supply & Installation of LEL Detector, IR type, SIL2, HC Service along with Relay with base, 24V, Analogue Inpur barrier, Flameproof Hooter with flasher, 24V and MCB- 6 AMP, 24VDC , 2" GI Pipe, Canopy etc. as per SOW. 2. Supply and laying of CABLE,CU,1T X1.5MM2,PVC INS,ARM,SH,FR (Detector triad cable) as per measurement (75 M per for one detector per SV) 3. Supply and Fixing/laying of cable tray,G.I,60MMx30MM with proper support/anchoring as per measurement (approximately 25M per SV). 4. Supply and laying of CABLE,CU, 2CX1.5MM2,PVC INS,ARM,SH,FR (For Hooter cum Beacon) and dressing with saddling and wall drilling if requires on wall as per measurement for Hooter . (20 Mtr for 1 SV) 5. Supply & Installation of Concrete block for detectors stand wherever required of (300*300*400mm). 1 Qty for each Detector. 6. Trenching for cable laying- this include laying of bricks and sand as per standard prectices (approximately 36M per SV). 7. Supply and Installation of Cable route markers. Concrete block for cable route marker ( 200X200X300mm ) wherever necessary (5 No's for Each SV) 8. Road cutting and cementing after work along with supply 4" GI pipe for crossing Concrete block required for tray support in the soft soil wherever necessary(200*200*300). One each per 1.5 mtrs. 9. Supply & Installation of 6mm sq mm copper Earthing cable wherever required.(10 Mtr per Detector) | 50.00 | EA |  | 285000.00 | 16815000.00 | 246994.00 | 14572646.00 | 301686.00 | 17799474.00 | 14572646.00 | Safe-Tronics Automation Pvt. Ltd.
1.03 | Calibration of Fixed Gas Detectors | 200.00 | EA |  | 1500.00 | 354000.00 | 991.00 | 233876.00 | 9120.00 | 2152320.00 | 233876.00 | Safe-Tronics Automation Pvt. Ltd.
| Total in Figures |  |  |  |  | 18408000.00 |  | 16817348.20 |  | 21999990.80
Lowest Amount Quoted BY: Safe-Tronics Automation Pvt. Ltd.(16817348.20)

## BOQ Summary
BOQ Summary Details Tender Title: SUPPLY INSTALLATION COMMISSIONING AND CALIBRATION OF LEL DETECTORS UNDER DIBIYAPUR REGION Tender ID: 2024_GAIL_202861_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Safe-Tronics Automation Pvt. Ltd. (BID ID -736072) | 16817348.20 | L1
| 2 | DETECTION INSTRUMENTS INDIA PVT LTD (BID ID -736649) | 18408000.00 | L2
| 3 | HI POINT SERVICES (I) PRIVATE LIMITED (BID ID -733617) | 21999990.80 | L3