## BoQ1
Government eProcurement System Created By: RAKESH SHARMA Created Date/Time: 07-Oct-2024 12:12 PM Tender Title: SOLAR POWER SYSTEM FOR BARAUNI GUWAHATI PIPELINE PROJECT OF GAIL (INDIA) LIMITED Tender ID: 2024_GAIL_203496_1
Tender Inviting Authority:
Name of Work: SOLAR POWER SYSTEM FOR BARUNI GUWAHATI PIPELINE PROJECT
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | STATCON ENERGIAA PVT LTD (GSTN-09AAACT2688L1ZS) BID ID -735906 |  | FISCO ENERGY PRIVATE LIMITED (GSTN-09AADCF2529H1ZO) BID ID -736137 |  | VOLKS ENERGIE PVT LTD (GSTN-07AADCV9396C1ZZ) BID ID -736323
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PART 1 -Supply - System Design, Detailed Engineering, procurement of materials, Inspection/FAT (Factory acceptance test), Supply of materials, Transportation, loading/unloading, insurance, Storage at site of complete Solar system-
2.00 | PART 1 -Supply - System Design, Detailed Engineering, procurement of materials, Inspection/FAT (Factory acceptance test), Supply of materials, Transportation, loading/unloading, insurance, Storage at site of complete Solar system-
3.00 | 200 WATT HYBRID SPV SYSTEM WITH 48 Hrs BACKUP FOR SV STATION WITH PCP STATIONS IN BIHAR /WB/ASSAM STATE (REFER SCOPE OF WORK FOR LOCATION OF THE SYSTEM)-48 Hrs back up. System Design, Detailed Engineering, procurement of materials, Inspection/FAT (Factory acceptance test), Supply of materials, Transportation, loading/unloading, insurance, Storage at site of complete Solar PV based Power source with two days autonomy (48 Hrs Backup) for 200W DC load for twenty four hours operation per day operation as per tender specification, data sheet, scope of work and block diagram enclosed including commissioning spares as required at SV station- The system shall include following- (i) Ni-Cd (1.2V/Cell) Pocket Plate Battery Bank (60V DC) (ii) Solar PV array with junction boxes, Anodized AL/ Hot dipped Galvanized M-Steel structure (ii) DC-DC Converter( 48V +/-1% Regulated DC Output) (iii) Interconnecting cables among battery bank, Grid charger, junction boxes etc including supply of all accessories like cable glands, cable tray, tinned-cu lugs etc as required. iv) Earthing and lightning protection system as required to complete the system. v) Supply of 2 year O&M spares as per list attached in scope of work vi) Balance of System Material, Required material for Erection work, Civil & Other miscellaneous work. Rating of battery bank shall be selected to meet the load requirement as specified above. However, each subsystem rating shall not be less then the value given below-
4.00 | Solar PV Modules- Mono crystalline (Min 500Wp) BIS certified for SPV array Min 3KWp (2X1500Wp) along with junction boxes as per specification and scope of work. | 6.00 | Set |  | 120350.00 | 812112.00 | 112340.00 | 754924.80 | 48825.00 | 328104.00 | 328104.00 | VOLKS ENERGIE PVT LTD
5.00 | Anodized AL/ Hot dipped Galvanized M-Steel structure as per specification and scope of work for SPV array Min 3KWp (2X1500 Wp) along with all required hardware, material & anchoring material etc. | 6.00 | Set |  | 62100.00 | 443208.00 | 31168.00 | 220669.44 | 18900.00 | 133812.00 | 133812.00 | VOLKS ENERGIE PVT LTD
6.00 | MPPT Solar Charger Min (Dual-2x60A ) @ 60V as per specification and scope of work with DC_DC Converter (48V+/-1% Regulated DC Output 1000W convertor with input variation of +/- 20%) and DCDB [48V] as per specification and scope of work. | 6.00 | Set |  | 450000.00 | 3189540.00 | 695500.00 | 4924140.00 | 761063.00 | 5388326.04 | 3189540.00 | STATCON ENERGIAA PVT LTD
7.00 | Ni-Cd Battery bank (Pocket Plate type) in (2x50%) arrangement, 26 KVAH @ 60V, (where KVAH = battery cell AH x 1.2 V x No. of cells) as per specification and scope of work. . | 6.00 | Set |  | 1021000.00 | 7845120.00 | 1002150.00 | 7696512.00 | 950544.00 | 7300177.92 | 7300177.92 | VOLKS ENERGIE PVT LTD
8.00 | Balance of System materials & equipments- 1) Interconnecting cables among arrays (solar grade), charge controller, battery bank, Grid charger, DCDBs, junction boxes etc including supply of all erection material & accessories like cable glands, cable tray, tinned-cu lugs etc as required. 2) Earthing and lightning protection system as required to complete the system. 3) Required material for Erection work, Civil & Other miscellaneous work | 6.00 | Set |  | 216000.00 | 1532820.00 | 357800.00 | 2533224.00 | 361690.00 | 2560765.20 | 1532820.00 | STATCON ENERGIAA PVT LTD
9.00 | DC-AC INVERTER (REFER SCOPE OF WORK FOR SUPPLY LOCATION)- Pure sine wave output inverter (dual redudant) for fire system having DC Input range (75-135V DC) and AC Output (230V AC +/-1%, 50 Hz +/- 1%), 500VA with over load, short circuit and over temp protection and with galvanic isolation as per specification with 04 nos of MCB output (6A) including supply of all interconnecting cables. | 15.00 | Set |  | 72000.00 | 1283250.00 | 65800.00 | 1164660.00 | 50198.00 | 888504.60 | 888504.60 | VOLKS ENERGIE PVT LTD
10.00 | GRID CHARGER FOR BATTERY BANK FOR FOR 200 WATT SYSTEM- Design, Detailed Engineering, Manufacturing, Inspection/FAT (Factory acceptance test), Supply, Transportation, loading/unloading, insurance, Storage at site of DSP based FCBC CHARGER (1x100%, single redudant, auto & manual operation of float & boost function) to charge the battery bank from grid supply, including commissioning spare excluding O&M spares as required, as per specifications, data sheet and instruction of Engineer-in-charge. The charger shall operate on the single phase with the input voltage supply of 415Vac, 3 Phase with Neutral, 50 Hz 330 ~ 460 Vac, 47 ~ 53 Hz. FCBC shall consist of three single phase chargers connected in parallel fed by R-Y-B phase respectively. The rating of FCBC shall be min 60V & 60 Amp, shall be calculated such that it can charge fully discharged complete battery bank at C10 rating. | 6.00 | Set |  | 650000.00 | 4605540.00 | 695500.00 | 4924140.00 | 761063.00 | 5388326.04 | 4605540.00 | STATCON ENERGIAA PVT LTD
11.00 | Total price for Part 1 (Supply) including all costs, freight, insurance till commissioning, GST etc.
12.00 | PART 2 - Site work -Installation, testing & commissioning- Loading/unloading at site, transportation, Installation, testing, commissioning and performance test at site (ODISHA/ WB/ANDHRA PRADESH)-
13.00 | SYSTEM-I- 200 WATT HYBRID SPV SYSTEM WITH 48 Hrs BACKUP FOR SV STATION WITH PCP STATIONS IN BIHAR /ASSAM STATE (REFER SCOPE OF WORK FOR LOCATION OF THE SYSTEM)-48 Hrs back up. Loading/unloading at site, Installation, testing, commissioning and performance test at site of complete Solar PV based Power source with two days autonomy for 200W DC load for twenty four hours operation per day operation (48 Hr back up) as per tender specification, data sheet, scope of work and block diagram enclosed including commissioning spares as required at each SV station. The system shall include following- (i) Ni-Cd (1.2V/Cell) Pocket Plate Battery Bank (60V DC) (ii) Solar PV array with junction boxes, Anodized AL/ Hot dipped Galvanized M-Steel structure (ii) DC-DC Converter( 48V +/-1% Regulated DC Output) (iii) Interconnecting cables among battery bank, Grid charger, junction boxes etc including laying & termination of all accessories like cable glands, cable tray, tinned-cu lugs etc as required. iv) Earthing and lightning protection system as required to complete the system. (vii) Erection materials & Other miscellaneous work Rating of SPV array, charge controller and battery bank shall be selected to meet the load requirement as specified above. However, each subsystem rating shall not be less than the value given below-
14.00 | Solar PV Modules- Mono crystalline (Min 500Wp) BIS certified for SPV array Min 3KWp (2X1500Wp) along with junction boxes as per specification and scope of work. | 6.00 | Set |  | 10000.00 | 70800.00 | 8050.00 | 56994.00 | 33250.00 | 235410.00 | 56994.00 | FISCO ENERGY PRIVATE LIMITED
15.00 | Anodized AL/ Hot dipped Galvanized M-Steel structure as per specification and scope of work for SPV array Min 3KWp (2X1500 Wp) along with all required hardware, material & anchoring material etc. | 6.00 | Set |  | 40000.00 | 283200.00 | 11500.00 | 81420.00 | 33250.00 | 235410.00 | 81420.00 | FISCO ENERGY PRIVATE LIMITED
16.00 | MPPT Solar Charger Min (Dual-2x60A ) @ 60V as per specification and scope of work with DC_DC Converter (48V+/-1% Regulated DC Output 1000W convertor with input variation of +/- 20%) and DCDB [48V] as per specification and scope of work. | 6.00 | Set |  | 45000.00 | 318600.00 | 28750.00 | 203550.00 | 33250.00 | 235410.00 | 203550.00 | FISCO ENERGY PRIVATE LIMITED
17.00 | Ni-Cd Battery bank (Pocket Plate type) in (2x50%) arrangement, 26 KVAH @ 60V, (where KVAH = battery cell AH x 1.2 V x No. of cells) as per specification and scope of work. . | 6.00 | Set |  | 60000.00 | 424800.00 | 115000.00 | 814200.00 | 115377.50 | 816872.70 | 424800.00 | STATCON ENERGIAA PVT LTD
18.00 | Balance of System materials & equipments- 1) Interconnecting cables among arrays (solar grade), charge controller, battery bank, Grid charger, DCDBs, junction boxes etc including laying & termination of all erection material & accessories like cable glands, cable tray, tinned-cu lugs etc as required. 2) Earthing and lightning protection system as required to complete the system. 3) Required material for Erection work, Civil & Other miscellaneous work | 6.00 | Set |  | 30000.00 | 212400.00 | 59800.00 | 423384.00 | 33250.00 | 235410.00 | 212400.00 | STATCON ENERGIAA PVT LTD
19.00 | DC-AC INVERTER- Pure sine wave output inverter (dual redudant) for fire system having DC Input range (75-135V DC) and AC Output (230V AC +/-1%, 50 Hz +/- 1%), 500VA with over load, short circuit and over temp protection and with galvanic isolation as per specification with 04 nos of MCB output (6A) including layinig & termination of all interconnecting cables. | 15.00 | Set |  | 15000.00 | 265500.00 | 5750.00 | 101775.00 | 6650.00 | 117705.00 | 101775.00 | FISCO ENERGY PRIVATE LIMITED
20.00 | GRID CHARGER FOR BATTERY BANK FOR FOR 200 WATT SYSTEM- Loading/unloading at site, Installation, testing, commissioning and performance test at site of DSP based FCBC CHARGER (1x100%, single redudant, auto & manual operation of float & boost function) to charge the battery bank from grid supply, including commissioning spare excluding O&M spares as required, as per specifications, data sheet and instruction of Engineer-in-charge. The charger shall operate on the single phase with the input voltage supply of 415Vac, 3 Phase with Neutral, 50 Hz 330 ~ 460 Vac, 47 ~ 53 Hz. FCBC shall consist of three single phase chargers connected in parallel fed by R-Y-B phase respectively. The rating of FCBC shall be min 60V & 60 Amp, shall be calculated such that it can charge fully discharged complete battery bank at C10 rating. | 6.00 | Set |  | 30000.00 | 212400.00 | 23000.00 | 162840.00 | 13300.00 | 94164.00 | 94164.00 | VOLKS ENERGIE PVT LTD
21.00 | Total price including all costs including GST for SiteWorks
22.00 | NOTE: 1. The offer shall be evaluated on package wise basis ( Supply + Site Works ). 2.State wise quantity distribution of each Part is indicated in MR. 3. The above shall be read in conjunction with notes of MR .
| Total in Figures |  |  |  |  | 21499290.00 |  | 24062433.24 |  | 23958397.50
Lowest Amount Quoted BY: STATCON ENERGIAA PVT LTD(21499290.00)

## BOQ Summary
BOQ Summary Details Tender Title: SOLAR POWER SYSTEM FOR BARAUNI GUWAHATI PIPELINE PROJECT OF GAIL (INDIA) LIMITED Tender ID: 2024_GAIL_203496_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | STATCON ENERGIAA PVT LTD (BID ID -735906) | 21499290.00 | L1
| 2 | VOLKS ENERGIE PVT LTD (BID ID -736323) | 23958397.50 | L2
| 3 | FISCO ENERGY PRIVATE LIMITED (BID ID -736137) | 24062433.24 | L3