## BoQ1
Government eProcurement System Created By: ANUPAM KUMAR TRIPATHI Created Date/Time: 17-Jan-2025 12:31 PM Tender Title: HIRING OF SERVICES FOR SUPPLY INSTALLATION AND COMMISSIONING OF EXTERNAL AND INTERNAL LIGHTNING PROTECTION SYSTEM AT PIPELINE INSTALLATIONS UNDER DIBIYAPUR REGIONS AS PER IEC 62305 Tender ID: 2024_GAIL_213565_1
Tender Inviting Authority: GAIL (India) LIMITED
Name of Work: GROUP -A [SITC of LPS at (30"HVJ & 36"VAPL) ]
Tender No: GAIL/AU/C&P/P-097/24-25/AKT
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEHN INDIA PVT. LTD. (GSTN-06AADCD9928J1ZA) BID ID -778688 |  | JMV LPS Limited (GSTN-NA) BID ID -781604 |  | Roksna India Private Limited (GSTN-NA) BID ID -785428
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Air Termination Rod . As per IEC Standard.
2.00 | Supply, Installation, Testing & Commissioning of Air termination rod having total length - 5000mm, Material of air termination rod - Al, Diameter Ø D40/16/10mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 23.00 | EA |  | 17616.00 | 478098.24 | 13500.00 | 366390.00 | 8075.34 | 219164.73 | 219164.73 | Roksna India Private Limited
3.00 | Supply, Installation, Testing & Commissioning of D 8mm L 700mm air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 62.00 | EA |  | 74.00 | 5413.84 | 258.00 | 18875.28 | 240.98 | 17629.73 | 5413.84 | DEHN INDIA PVT. LTD.
4.00 | Supply, Installation, Testing & Commissioning of D 8mm L 2m air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 29.00 | EA |  | 952.00 | 32577.44 | 890.00 | 30455.80 | 642.60 | 21989.77 | 21989.77 | Roksna India Private Limited
5.00 | Supply, Installation, Testing & Commissioning of Clamps and Other Accessories to Hold Air Termination Rod . As per IEC Standard.
6.00 | Supply, Installation, Testing & Commissioning of Tripods for Supporting Tubes with side outlet. As per IEC Standard. | 23.00 | EA |  | 174.00 | 4722.36 | 2750.00 | 74635.00 | 4316.13 | 117139.77 | 4722.36 | DEHN INDIA PVT. LTD.
7.00 | Supply, Installation, Testing & Commissioning of Sets of Threaded Rods for Tripod. As per IEC Standard. | 23.00 | EA |  | 174.00 | 4722.36 | 2162.00 | 58676.68 | 1350.53 | 36653.41 | 4722.36 | DEHN INDIA PVT. LTD.
8.00 | Supply, Installation, Testing & Commissioning of Plastic support plate for concrete base. For protecting the roofing sheets under the concrete base(17 kg.). The Diameter Ø outside 370 mm, Diameter Ø inside 360 mm and Material EVA. As per IEC Standard. | 68.00 | EA |  | 235.00 | 18856.40 | 451.00 | 36188.24 | 556.92 | 44687.26 | 18856.40 | DEHN INDIA PVT. LTD.
9.00 | Supply, Installation, Testing & Commissioning of Concrete base for air-termination rods, for self-supporting air-termination rods in the tripod. Support Wedge- Ø16 mm, Diameter- Ø 337 mm, Material- concrete, Material of wedge- StSt & Weight 17kg. As per IEC Standard. | 205.00 | EA |  | 533.00 | 128932.70 | 750.00 | 181425.00 | 417.69 | 101039.21 | 101039.21 | Roksna India Private Limited
10.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 700mm air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 62.00 | EA |  | 235.00 | 17192.60 | 271.00 | 19826.36 | 273.11 | 19980.36 | 17192.60 | DEHN INDIA PVT. LTD.
11.00 | Supply, Installation, Testing & Commissioning of Wall mounting bracket for fixing supporting tubes (D50 mm) to the structure to be protected or the wall. As per IEC Standard. | 29.00 | EA |  | 1464.00 | 50098.08 | 800.00 | 27376.00 | 1392.30 | 47644.51 | 27376.00 | JMV LPS Limited
12.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 2 m air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 43.00 | EA |  | 775.00 | 39323.50 | 271.00 | 13750.54 | 273.11 | 13857.35 | 13750.54 | JMV LPS Limited
13.00 | Supply, Installation, Testing & Commissioning of Clamp to connect Air termination rod on Side Wall, Material - StSt, clamping range of air termination rod- Rd 10-16mm. As per IEC Standard. | 14.00 | EA |  | 775.00 | 12803.00 | 700.00 | 11564.00 | 696.15 | 11500.40 | 11500.40 | Roksna India Private Limited
14.00 | Supply, Installation, Testing & Commissioning of Anchor Fastener -2 , Size-M10x50mm, Material-SS. As per IEC Standard. | 29.00 | EA |  | 36.00 | 1231.92 | 100.00 | 3422.00 | 240.98 | 8246.16 | 1231.92 | DEHN INDIA PVT. LTD.
15.00 | Supply, Installation, Testing & Commissioning of Nut Bolt - 2 , Size-M8x50mm, Material-SS. As per IEC Standard. | 29.00 | EA |  | 19.00 | 650.18 | 25.00 | 855.50 | 111.38 | 3811.56 | 650.18 | DEHN INDIA PVT. LTD.
16.00 | Supply, Installation, Testing & Commissioning of FS Clamps (Air-termination Rod Clamps 16mm) for connecting air-termination rods to roof. As per IEC Standard. | 7.00 | EA |  | 287.00 | 2370.62 | 271.00 | 2238.46 | 236.69 | 1955.07 | 1955.07 | Roksna India Private Limited
17.00 | Supply, Installation, Testing & Commissioning of Roof/Down Conductor & Conductor Holder . As per IEC Standard.
18.00 | Supply, Installation, Testing & Commissioning of With accessories Screw and Gitty, Material SS (M5 x 50mm). As per relevant Standard. | 1372.00 | M |  | 17.00 | 27522.32 | 48.00 | 77710.08 | 32.13 | 52017.18 | 27522.32 | DEHN INDIA PVT. LTD.
19.00 | Supply, Installation, Testing & Commissioning of 8mm Al Roof Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 936.00 | EA |  | 74.00 | 81731.52 | 120.00 | 132537.60 | 209.38 | 231256.57 | 81731.52 | DEHN INDIA PVT. LTD.
20.00 | Supply, Installation, Testing & Commissioning of Roof conductor holder FB2 for flat roofs with concrete block C35/45 with double conductor holder Rd 8 mm fixed, Dimension 141 x 86 x 70 mm. As per IEC Standard. | 92.00 | EA |  | 82.00 | 8901.92 | 145.00 | 15741.20 | 208.84 | 22672.21 | 8901.92 | DEHN INDIA PVT. LTD.
21.00 | Supply, Installation, Testing & Commissioning of Roof Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base. As per IEC Standard. | 936.00 | EA |  | 172.00 | 189970.56 | 145.00 | 160149.60 | 127.45 | 140764.87 | 140764.87 | Roksna India Private Limited
22.00 | Supply, Installation, Testing & Commissioning of 8mm Al Down Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 436.00 | M |  | 74.00 | 38071.52 | 120.00 | 61737.60 | 209.38 | 107722.08 | 38071.52 | DEHN INDIA PVT. LTD.
23.00 | Supply, Installation, Testing & Commissioning of Down Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base. As per IEC Standard. | 436.00 | EA |  | 172.00 | 88490.56 | 145.00 | 74599.60 | 127.45 | 65569.96 | 65569.96 | Roksna India Private Limited
24.00 | Supply, Installation, Testing & Commissioning of Universal Connector for interconnecting roof conductor & down conductor, Material of clamp StSt, clamping range Rd 8-10 mm. As per IEC Standard. | 79.00 | EA |  | 167.00 | 15567.74 | 200.00 | 18644.00 | 273.11 | 25458.85 | 15567.74 | DEHN INDIA PVT. LTD.
25.00 | Supply, Installation, Testing & Commissioning of Lightning strike counter for digital recording of impulse currents. The device is preferably installed on the down conductors of the lightning protection system. Operating current (8/20 μs): 1 kA, Max. discharge current (10/350 μs): 100 kA, clamping range of rod: 8- 10mm, clamping range of flat: 30mm, Degree of protection: IP 65. As per IEC Standard. | 7.00 | M |  | 16978.00 | 140238.28 | 16000.00 | 132160.00 | 10442.25 | 86252.99 | 86252.99 | Roksna India Private Limited
26.00 | Supply, Installation, Testing & Commissioning of Earthing System. As per IEC Standard.
27.00 | Supply, Installation, Testing & Commissioning of Pipe clamp D 16-168 mm (3/4-6") StSt with terminal clamp 1xRd 10 mm or 2xRd 6-8 mm for connecting metal railing with 8mm Al solid round conductor. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 30.00 | M |  | 342.00 | 12106.80 | 631.00 | 22337.40 | 633.50 | 22425.78 | 12106.80 | DEHN INDIA PVT. LTD.
28.00 | Supply, Installation, Testing & Commissioning of GI flat (25x6mm) Strip having width- 25mm, thickness- 6mm, Material- Hot dipped Galvanized Iron, Cross Section- 150 mm2, Coating thickness- Avg. 70 microns. & Complied as per IEC 62561 for termination of down conductor from test link to the earth pit termination clamp and Interconnection of the earth pit to form type B earthing. As per IEC Standard. | 1830.00 | EA |  | 176.00 | 380054.40 | 300.00 | 647820.00 | 452.50 | 977123.10 | 380054.40 | DEHN INDIA PVT. LTD.
29.00 | Supply, Installation, Testing & Commissioning of GI strip holder- Insulated holder, Material of construction - Dow moulded compound, height 19mm, Slot Size- 25x6 mm. As per IEC Standard. | 132.00 | EA |  | 49.00 | 7632.24 | 82.00 | 12772.32 | 139.23 | 21686.46 | 7632.24 | DEHN INDIA PVT. LTD.
30.00 | Supply, Installation, Testing & Commissioning of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 250 microns of copper plating. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 68.00 | EA |  | 2196.00 | 176207.04 | 2850.00 | 228684.00 | 4733.82 | 379841.72 | 176207.04 | DEHN INDIA PVT. LTD.
31.00 | Supply, Installation, Testing & Commissioning of 22.6kg backfilled compound, - Graphite based backfill compound having low resisitvity, does not decay or leachout, moisture retention capacity 10-15%, shall be tested for thermal stability for temp range -60 to +60 degree C, shall have sulphure content less than 0.04% shall have resistivity of 0.08 ohm or less, ROHS certified, to fill the bore area around the rod. As per IEC Standard. | 68.00 | EA |  | 2154.00 | 172836.96 | 1800.00 | 144432.00 | 2409.75 | 193358.34 | 144432.00 | JMV LPS Limited
32.00 | Supply, Installation, Testing & Commissioning of SS 316 grade Termination clamp to terminate the load on earth electrode for termination, Material of construction - 316 grade stainless steel, Dimension - 160x35x3 mm. As per IEC Standard. | 68.00 | M |  | 482.00 | 38675.68 | 649.00 | 52075.76 | 996.03 | 79921.45 | 38675.68 | DEHN INDIA PVT. LTD.
33.00 | Supply, Installation, Testing & Commissioning of Poly plastic pit cover of material- Polymer Body & Cover, Product Code- HEP, Dimensions- 308 mm (L) x 308 mm (W) X 214 mm (H), Weight 2.5 kg (5.50 LBS). As per IEC Standard. | 68.00 | EA |  | 1689.00 | 135525.36 | 1100.00 | 88264.00 | 1124.55 | 90233.89 | 88264.00 | JMV LPS Limited
34.00 | Supply, Installation, Testing & Commissioning of UNI disconnecting clamp with intermediate plate for round and flat conductor, Material StSt, clamping range Rd / Fl 8-10 / 30 mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 77.00 | EA |  | 120.00 | 10903.20 | 1400.00 | 127204.00 | 401.62 | 36491.65 | 10903.20 | DEHN INDIA PVT. LTD.
35.00 | Supply, Installation, Testing & Commissioning of Internal Protection System (SPD’s) . As per IEC Standard.
36.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single-pole combined lightning current and surge arrester, Type 1 SPD. . As per IEC Standard. | 170.00 | EA |  | 11808.00 | 2368684.80 | 7000.00 | 1404200.00 | 20383.27 | 4088884.36 | 1404200.00 | JMV LPS Limited
37.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (N-PE) Single-pole combined lightning current arrester, Type 1 SPD. . As per IEC Standard. | 59.00 | EA |  | 9118.00 | 634795.16 | 7000.00 | 487340.00 | 15156.79 | 1055215.86 | 487340.00 | JMV LPS Limited
38.00 | Supply, Installation, Testing & Commissioning of Combined lightning current and surge arrester for use in single phase TT and TN system at mains LT panel (1 phase, 230 V), Type 1 + 2 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 17.00 | EA |  | 5095.00 | 102205.70 | 16000.00 | 320960.00 | 7100.73 | 142440.64 | 102205.70 | DEHN INDIA PVT. LTD.
39.00 | Supply, Installation, Testing & Commissioning of For 48 V DC Supply: Coordinated and modular single-pole spark-gap-based lightning current arrester for d.c. applications from 12 to 60 volts; with remote signalling contact for monitoring device (floating changeover contact). Type 1 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 28.00 | EA |  | 15940.00 | 526657.60 | 12500.00 | 413000.00 | 7657.65 | 253008.76 | 253008.76 | Roksna India Private Limited
40.00 | Supply, Installation, Testing & Commissioning of Arrester for CCTV, Data Networks and Ethernet Applications, Universal arrester for Industrial Ethernet, Power over Ethernet (IEEE 802.3 compliant up to PoE++ / 4PPoE) and similar applications in structured cabling systems according to class E up to 250 MHz. Protection of all pairs by powerful gas discharge tubes. DIN rail mounted adapter type with sockets, for protecting four pairs of data network interfaces via RJ45 sockets, for single-user application or application in 19 inch cabinets, space-saving. Max. continuous operating voltage (d.c.) (Uc ): 48V RJ 45 Connection or Ethernet Cable . As per IEC Standard. | 186.00 | EA |  | 2434.00 | 534214.32 | 4000.00 | 877920.00 | 6961.50 | 1527910.02 | 534214.32 | DEHN INDIA PVT. LTD.
41.00 | Supply, Installation, Testing & Commissioning of Modular and pluggable four-pole surge arrester with integrated Advanced Circuit Interruption (ACI) switch / spark gap for TT and TN-S systems (3+1 configuration); FM version with floating remote signaling contact, Type 2 SPD according to EN 61643-11 (no external backup fuse required) . As per IEC Standard. | 1.00 | EA |  | 12784.00 | 15085.12 | 7500.00 | 8850.00 | 39359.25 | 46443.92 | 8850.00 | JMV LPS Limited
42.00 | Supply, Installation, Testing & Commissioning of Multi-purpose surge arrester consisting of a base element and a plug-in protection module, high discharge capacity due to heavy-duty zinc oxide varistor, high reliability due to "Thermo Dynamic Control" SPD monitoring device (for 24V DC and 48V DC) . As per IEC Standard. | 18.00 | EA |  | 1996.00 | 42395.04 | 7500.00 | 159300.00 | 5944.05 | 126251.62 | 42395.04 | DEHN INDIA PVT. LTD.
43.00 | Supply, Installation, Testing & Commissioning of Universal single-pole surge arrester consisting of a base part and a plug-in protection module, Powerful d.c. switching device DCD, can be used without additional backup fuse. (for 220V DC) . As per IEC Standard. | 19.00 | EA |  | 1366.00 | 30625.72 | 6050.00 | 135641.00 | 5944.05 | 133265.60 | 30625.72 | DEHN INDIA PVT. LTD.
44.00 | Supply, Installation, Testing & Commissioning of Modular combined lightning current and surge arrester for use in single phase TT system at mains LT panel (1 phase, 230 V) . As per IEC Standard. | 24.00 | EA |  | 5095.00 | 144290.40 | 8000.00 | 226560.00 | 12048.75 | 341220.60 | 144290.40 | DEHN INDIA PVT. LTD.
45.00 | Supply, Installation, Testing & Commissioning of Modular Surge Arrester with integrated backup fuses for TT and TN-S system (3 phase, 415V) . As per IEC Standard. | 4.00 | EA |  | 12784.00 | 60340.48 | 15000.00 | 70800.00 | 39359.25 | 185775.66 | 60340.48 | DEHN INDIA PVT. LTD.
46.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-232, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 14.00 | EA |  | 4171.00 | 68904.92 | 6050.00 | 99946.00 | 5622.75 | 92887.83 | 68904.92 | DEHN INDIA PVT. LTD.
47.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-485, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 14.00 | EA |  | 4171.00 | 68904.92 | 6050.00 | 99946.00 | 5622.75 | 92887.83 | 68904.92 | DEHN INDIA PVT. LTD.
48.00 | Supply, Installation, Testing & Commissioning of SPD FOR PLC SUPPLY . As per IEC Standard.
49.00 | Supply, Installation, Testing & Commissioning of Space-saving combined lightning current and surge arrester module with Life Check feature for protecting four single lines sharing a common reference potential as well as unbalanced interfaces, for 24 V DC . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Base part as a very space-saving and universal four pole feedthrough terminal for the insertion of a protection module without signal disconnection if the protection module is removed . As per IEC Standard. | 17.00 | EA |  | 4075.00 | 81744.50 | 9200.00 | 184552.00 | 11834.55 | 237401.07 | 81744.50 | DEHN INDIA PVT. LTD.
50.00 | Supply, Installation, Testing & Commissioning of SPDs FOR FIELD DEVICES/EQUPMENTS (PRESSURE & TEMPERATURE TRANSMITTERS etc.) . As per IEC Standard.
51.00 | Supply, Installation, Testing & Commissioning of Surge arrester with a low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Parallel Connection ½ NTP thread) For 24 V DC Supply (for PTs) . As per IEC Standard. | 53.00 | EA |  | 3383.00 | 211572.82 | 8000.00 | 500320.00 | 7550.55 | 472211.40 | 211572.82 | DEHN INDIA PVT. LTD.
52.00 | Supply, Installation, Testing & Commissioning of Surge arrester with low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Series Connection ½ NTP thread) For 24 V DC Supply (for TTs) . As per IEC Standard. | 24.00 | EA |  | 4383.00 | 124126.56 | 8000.00 | 226560.00 | 7550.55 | 213831.58 | 124126.56 | DEHN INDIA PVT. LTD.
53.00 | Supply, Installation, Testing & Commissioning of SPD’s FOR TELEPHONE LINE PROTECTION . As per IEC Standard.
54.00 | Supply, Installation, Testing & Commissioning of Lightning current carrying DRL plug-in SPD block (10 pairs) for almost all applications. Expandable to a combined lightning current and surge arrester by means of a DRL protective plug. The integrated disconnection block contacts allow testing, measuring and patching with plugged-in protection.The three-pole gas discharge tubes have a fail-safe function with visual fault indicator. . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Snap-on earthing frame for earthing and installation of max 10 DRL protection modules. Plugs into a 10-pair disconnection block or DRL plug- in SPD block. As per IEC Standard. | 73.00 | EA |  | 7090.00 | 610732.60 | 7000.00 | 602980.00 | 4803.43 | 413767.46 | 413767.46 | Roksna India Private Limited
55.00 | Supply, Installation, Testing & Commissioning of Protective plug (one pair), energy-coordinated with DRL plug-in SPD block, for use as single-stage protective device for terminal equipment. Low voltage protection level line and integrated overcurrent protection for ADSL, ISDN Uk0 or a/b lines. To be mounted into EF 10 DRL. Installation recommended only in combination with DRL plug-in SPD block. As per IEC Standard. | 732.00 | EA |  | 1094.00 | 944953.44 | 2000.00 | 1727520.00 | 883.57 | 763192.42 | 763192.42 | Roksna India Private Limited
| Total in Figures |  |  |  |  | 8891663.44 |  | 10388943.02 |  | 13384693.02
Lowest Amount Quoted BY: DEHN INDIA PVT. LTD.(8891663.44)

## BoQ2
Government eProcurement System Created By: ANUPAM KUMAR TRIPATHI Created Date/Time: 17-Jan-2025 12:31 PM Tender Title: HIRING OF SERVICES FOR SUPPLY INSTALLATION AND COMMISSIONING OF EXTERNAL AND INTERNAL LIGHTNING PROTECTION SYSTEM AT PIPELINE INSTALLATIONS UNDER DIBIYAPUR REGIONS AS PER IEC 62305 Tender ID: 2024_GAIL_213565_1
Tender Inviting Authority: GAIL (India) LIMITED
Name of Work: Group - B [SITC of LPS at (18"AJPL & 24"APPL)]
Tender No: GAIL/AU/C&P/P-097/24-25/AKT
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEHN INDIA PVT. LTD. (GSTN-06AADCD9928J1ZA) BID ID -778688 |  | JMV LPS Limited (GSTN-NA) BID ID -781604 |  | Roksna India Private Limited (GSTN-NA) BID ID -785428
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Air Termination Rod . As per IEC Standard.
2.00 | Supply, Installation, Testing & Commissioning of Air termination rod having total length - 4500mm, Material of air termination rod - Al, Diameter Ø D40/22/16/10mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 7.00 | EA |  | 16472.00 | 136058.72 | 10500.00 | 86730.00 | 7690.80 | 63526.01 | 63526.01 | Roksna India Private Limited
3.00 | Supply, Installation, Testing & Commissioning of Air termination rod having total length - 5000mm, Material of air termination rod - Al, Diameter Ø D40/16/10mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 34.00 | EA |  | 17616.00 | 706753.92 | 13500.00 | 541620.00 | 7690.80 | 308554.90 | 308554.90 | Roksna India Private Limited
4.00 | Supply, Installation, Testing & Commissioning of D 8mm L 700mm air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 101.00 | EA |  | 74.00 | 8819.32 | 258.00 | 30748.44 | 229.50 | 27351.81 | 8819.32 | DEHN INDIA PVT. LTD.
5.00 | Supply, Installation, Testing & Commissioning of D 8mm L 2m air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 34.00 | EA |  | 952.00 | 38194.24 | 890.00 | 35706.80 | 612.00 | 24553.44 | 24553.44 | Roksna India Private Limited
6.00 | Supply, Installation, Testing & Commissioning of Clamps and Other Accessories to Hold Air Termination Rod . As per IEC Standard.
7.00 | Supply, Installation, Testing & Commissioning of Tripods for Supporting Tubes with side outlet. As per IEC Standard. | 41.00 | EA |  | 174.00 | 8418.12 | 2750.00 | 133045.00 | 4110.60 | 198870.83 | 8418.12 | DEHN INDIA PVT. LTD.
8.00 | Supply, Installation, Testing & Commissioning of Sets of Threaded Rods for Tripod. As per IEC Standard. | 41.00 | EA |  | 174.00 | 8418.12 | 2162.00 | 104597.56 | 1286.22 | 62227.32 | 8418.12 | DEHN INDIA PVT. LTD.
9.00 | Supply, Installation, Testing & Commissioning of Plastic support plate for concrete base. For protecting the roofing sheets under the concrete base(17 kg.). The Diameter Ø outside 370 mm, Diameter Ø inside 360 mm and Material EVA.. As per IEC Standard. | 122.00 | EA |  | 235.00 | 33830.60 | 451.00 | 64925.96 | 530.40 | 76356.38 | 33830.60 | DEHN INDIA PVT. LTD.
10.00 | Supply, Installation, Testing & Commissioning of Concrete base for air-termination rods, for self-supporting air-termination rods in the tripod. Support Wedge- Ø16 mm, Diameter- Ø 337 mm, Material- concrete, Material of wedge- StSt & Weight 17kg.. As per IEC Standard. | 367.00 | EA |  | 533.00 | 230820.98 | 750.00 | 324795.00 | 397.80 | 172271.27 | 172271.27 | Roksna India Private Limited
11.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 700mm air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 101.00 | EA |  | 235.00 | 28007.30 | 271.00 | 32297.78 | 260.10 | 30998.72 | 28007.30 | DEHN INDIA PVT. LTD.
12.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 2 m air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 50.00 | EA |  | 775.00 | 45725.00 | 271.00 | 15989.00 | 260.10 | 15345.90 | 15345.90 | Roksna India Private Limited
13.00 | Supply, Installation, Testing & Commissioning of Clamp to connect Air termination rod on Side Wall, Material - StSt, clamping range of air termination rod- Rd 10-16mm. As per IEC Standard. | 17.00 | EA |  | 775.00 | 15546.50 | 700.00 | 14042.00 | 663.00 | 13299.78 | 13299.78 | Roksna India Private Limited
14.00 | Supply, Installation, Testing & Commissioning of Anchor Fastener -2 , Size-M10x50mm, Material-SS. As per IEC Standard. | 34.00 | EA |  | 36.00 | 1444.32 | 100.00 | 4012.00 | 229.50 | 9207.54 | 1444.32 | DEHN INDIA PVT. LTD.
15.00 | Supply, Installation, Testing & Commissioning of Nut Bolt - 2 , Size-M8x50mm, Material-SS. As per IEC Standard. | 34.00 | EA |  | 19.00 | 762.28 | 25.00 | 1003.00 | 106.08 | 4255.93 | 762.28 | DEHN INDIA PVT. LTD.
16.00 | Supply, Installation, Testing & Commissioning of FS Clamps (Air-termination Rod Clamps 16mm) for connecting air-termination rods to roof. As per IEC Standard. | 8.00 | EA |  | 287.00 | 2709.28 | 271.00 | 2558.24 | 225.42 | 2127.96 | 2127.96 | Roksna India Private Limited
17.00 | Supply, Installation, Testing & Commissioning of Roof/Down Conductor & Conductor Holder . As per IEC Standard.
18.00 | Supply, Installation, Testing & Commissioning of With accessories Screw and Gitty, Material SS (M5 x 50mm). As per IEC Standard. | 1925.00 | EA |  | 17.00 | 38615.50 | 48.00 | 109032.00 | 30.60 | 69507.90 | 38615.50 | DEHN INDIA PVT. LTD.
19.00 | Supply, Installation, Testing & Commissioning of 8mm Al Roof Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 1244.00 | M |  | 74.00 | 108626.08 | 120.00 | 176150.40 | 211.14 | 309936.63 | 108626.08 | DEHN INDIA PVT. LTD.
20.00 | Supply, Installation, Testing & Commissioning of Roof conductor holder FB2 for flat roofs with concrete block C35/45 with double conductor holder Rd 8 mm fixed, Dimension 141 x 86 x 70 mm. As per IEC Standard. | 121.00 | EA |  | 82.00 | 11707.96 | 145.00 | 20703.10 | 198.90 | 28398.94 | 11707.96 | DEHN INDIA PVT. LTD.
21.00 | Supply, Installation, Testing & Commissioning of Roof Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base. As per IEC Standard. | 1244.00 | EA |  | 172.00 | 252482.24 | 145.00 | 212848.40 | 128.52 | 188657.08 | 188657.08 | Roksna India Private Limited
22.00 | Supply, Installation, Testing & Commissioning of 8mm Al Down Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 680.00 | M |  | 74.00 | 59377.60 | 120.00 | 96288.00 | 211.14 | 169418.74 | 59377.60 | DEHN INDIA PVT. LTD.
23.00 | Supply, Installation, Testing & Commissioning of Down Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base. As per IEC Standard. | 680.00 | EA |  | 172.00 | 138012.80 | 145.00 | 116348.00 | 128.52 | 103124.45 | 103124.45 | Roksna India Private Limited
24.00 | Supply, Installation, Testing & Commissioning of Universal Connector for interconnecting roof conductor & down conductor, Material of clamp StSt, clamping range Rd 8-10 mm. As per IEC Standard. | 112.00 | EA |  | 167.00 | 22070.72 | 200.00 | 26432.00 | 260.10 | 34374.82 | 22070.72 | DEHN INDIA PVT. LTD.
25.00 | Supply, Installation, Testing & Commissioning of Lightning strike counter for digital recording of impulse currents. The device is preferably installed on the down conductors of the lightning protection system. Operating current (8/20 μs): 1 kA, Max. discharge current (10/350 μs): 100 kA, clamping range of rod: 8- 10mm, clamping range of flat: 30mm, Degree of protection: IP 65. As per IEC Standard. | 8.00 | EA |  | 16978.00 | 160272.32 | 16000.00 | 151040.00 | 10608.00 | 100139.52 | 100139.52 | Roksna India Private Limited
26.00 | Supply, Installation, Testing & Commissioning of Earthing System. As per IEC Standard.
27.00 | Supply, Installation, Testing & Commissioning of Pipe clamp D 16-168 mm (3/4-6") StSt with terminal clamp 1xRd 10 mm or 2xRd 6-8 mm for connecting metal railing with 8mm Al solid round conductor. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 49.00 | EA |  | 342.00 | 19774.44 | 631.00 | 36484.42 | 603.33 | 34884.54 | 19774.44 | DEHN INDIA PVT. LTD.
28.00 | Supply, Installation, Testing & Commissioning of GI flat (25x6mm) Strip having width- 25mm, thickness- 6mm, Material- Hot dipped Galvanized Iron, Cross Section- 150 mm2, Coating thickness- Avg. 70 microns. & Complied as per IEC 62561 for termination of down conductor from test link to the earth pit termination clamp and Interconnection of the earth pit to form type B earthing. As per IEC Standard. | 2932.00 | M |  | 176.00 | 608917.76 | 300.00 | 1037928.00 | 430.95 | 1490983.57 | 608917.76 | DEHN INDIA PVT. LTD.
29.00 | Supply, Installation, Testing & Commissioning of GI strip holder- Insulated holder, Material of construction - Dow moulded compound, height 19mm, Slot Size- 25x6 mm.. As per IEC Standard. | 197.00 | EA |  | 49.00 | 11390.54 | 82.00 | 19061.72 | 132.60 | 30824.20 | 11390.54 | DEHN INDIA PVT. LTD.
30.00 | Supply, Installation, Testing & Commissioning of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 250 microns of copper plating. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 108.00 | EA |  | 2196.00 | 279858.24 | 2850.00 | 363204.00 | 4508.40 | 574550.50 | 279858.24 | DEHN INDIA PVT. LTD.
31.00 | Supply, Installation, Testing & Commissioning of 22.6kg backfilled compound, - Graphite based backfill compound having low resisitvity, does not decay or leachout, moisture retention capacity 10-15%, shall be tested for thermal stability for temp range -60 to +60 degree C, shall have sulphure content less than 0.04% shall have resistivity of 0.08 ohm or less, ROHS certified, to fill the bore area around the rod. As per IEC Standard. | 108.00 | EA |  | 2154.00 | 274505.76 | 1800.00 | 229392.00 | 2142.00 | 272976.48 | 229392.00 | JMV LPS Limited
32.00 | Supply, Installation, Testing & Commissioning of SS 316 grade Termination clamp to terminate the load on earth electrode for termination, Material of construction - 316 grade stainless steel, Dimension - 160x35x3 mm. As per IEC Standard. | 108.00 | EA |  | 482.00 | 61426.08 | 649.00 | 82708.56 | 948.60 | 120889.58 | 61426.08 | DEHN INDIA PVT. LTD.
33.00 | Supply, Installation, Testing & Commissioning of Poly plastic pit cover of material- Polymer Body & Cover, Product Code- HEP, Dimensions- 308 mm (L) x 308 mm (W) X 214 mm (H), Weight 2.5 kg (5.50 LBS). As per IEC Standard. | 108.00 | EA |  | 1689.00 | 215246.16 | 1100.00 | 140184.00 | 1071.00 | 136488.24 | 136488.24 | Roksna India Private Limited
34.00 | Supply, Installation, Testing & Commissioning of UNI disconnecting clamp with intermediate plate for round and flat conductor, Material StSt, clamping range Rd / Fl 8-10 / 30 mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 104.00 | EA |  | 120.00 | 14726.40 | 1400.00 | 171808.00 | 382.50 | 46940.40 | 14726.40 | DEHN INDIA PVT. LTD.
35.00 | Supply, Installation, Testing & Commissioning of Internal Protection System (SPD’s) . As per IEC Standard.
36.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single-pole combined lightning current and surge arrester, Type 1 SPD. As per IEC Standard. | 112.00 | EA |  | 11808.00 | 1560545.28 | 7000.00 | 925120.00 | 19890.00 | 2628662.40 | 925120.00 | JMV LPS Limited
37.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (N-PE) Single-pole combined lightning current arrester, Type 1 SPD. As per IEC Standard. | 37.00 | EA |  | 9118.00 | 398091.88 | 7000.00 | 305620.00 | 14790.00 | 645731.40 | 305620.00 | JMV LPS Limited
38.00 | Supply, Installation, Testing & Commissioning of Combined lightning current and surge arrester for use in single phase TT and TN system at mains LT panel (1 phase, 230 V), Type 1 + 2 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 44.00 | EA |  | 5095.00 | 264532.40 | 16000.00 | 830720.00 | 6762.60 | 351114.19 | 264532.40 | DEHN INDIA PVT. LTD.
39.00 | Supply, Installation, Testing & Commissioning of For 48 V DC Supply: Coordinated and modular single-pole spark-gap-based lightning current arrester for d.c. applications from 12 to 60 volts; with remote signalling contact for monitoring device (floating changeover contact). Type 1 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 23.00 | EA |  | 15940.00 | 432611.60 | 12500.00 | 339250.00 | 7293.00 | 197932.02 | 197932.02 | Roksna India Private Limited
40.00 | Supply, Installation, Testing & Commissioning of Arrester for CCTV, Data Networks and Ethernet Applications, Universal arrester for Industrial Ethernet, Power over Ethernet (IEEE 802.3 compliant up to PoE++ / 4PPoE) and similar applications in structured cabling systems according to class E up to 250 MHz. Protection of all pairs by powerful gas discharge tubes. DIN rail mounted adapter type with sockets, for protecting four pairs of data network interfaces via RJ45 sockets, for single-user application or application in 19 inch cabinets, space-saving. Max. continuous operating voltage (d.c.) (Uc ): 48V RJ 45 Connection or Ethernet Cable . As per IEC Standard. | 151.00 | EA |  | 2434.00 | 433690.12 | 4000.00 | 712720.00 | 6885.00 | 1226769.30 | 433690.12 | DEHN INDIA PVT. LTD.
41.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-232, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 58.00 | EA |  | 4171.00 | 285463.24 | 6050.00 | 414062.00 | 5355.00 | 366496.20 | 285463.24 | DEHN INDIA PVT. LTD.
42.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-485, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 58.00 | EA |  | 4171.00 | 285463.24 | 6050.00 | 414062.00 | 5355.00 | 366496.20 | 285463.24 | DEHN INDIA PVT. LTD.
43.00 | Supply, Installation, Testing & Commissioning of SPD FOR PLC SUPPLY . As per IEC Standard.
44.00 | Supply, Installation, Testing & Commissioning of Space-saving combined lightning current and surge arrester module with Life Check feature for protecting four single lines sharing a common reference potential as well as unbalanced interfaces, for 24 V DC . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Base part as a very space-saving and universal four pole feedthrough terminal for the insertion of a protection module without signal disconnection if the protection module is removed . As per IEC Standard. | 44.00 | EA |  | 4075.00 | 211574.00 | 9200.00 | 477664.00 | 11271.00 | 585190.32 | 211574.00 | DEHN INDIA PVT. LTD.
45.00 | Supply, Installation, Testing & Commissioning of SPDs FOR FIELD DEVICES/EQUPMENTS (PRESSURE & TEMPERATURE TRANSMITTERS etc.) . As per IEC Standard.
46.00 | Supply, Installation, Testing & Commissioning of Surge arrester with a low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Parallel Connection ½ NTP thread) For 24 V DC Supply (for PTs) . As per IEC Standard. | 161.00 | EA |  | 3383.00 | 642702.34 | 8000.00 | 1519840.00 | 7191.00 | 1366146.18 | 642702.34 | DEHN INDIA PVT. LTD.
47.00 | Supply, Installation, Testing & Commissioning of Surge arrester with low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Series Connection ½ NTP thread) For 24 V DC Supply (for TTs) . As per IEC Standard. | 100.00 | EA |  | 4383.00 | 517194.00 | 8000.00 | 944000.00 | 7191.00 | 848538.00 | 517194.00 | DEHN INDIA PVT. LTD.
48.00 | Supply, Installation, Testing & Commissioning of SPD’s FOR TELEPHONE LINE PROTECTION . As per IEC Standard.
49.00 | Supply, Installation, Testing & Commissioning of Lightning current carrying DRL plug-in SPD block (10 pairs) for almost all applications. Expandable to a combined lightning current and surge arrester by means of a DRL protective plug. The integrated disconnection block contacts allow testing, measuring and patching with plugged-in protection.The three-pole gas discharge tubes have a fail-safe function with visual fault indicator. . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Snap-on earthing frame for earthing and installation of max 10 DRL protection modules. Plugs into a 10-pair disconnection block or DRL plug- in SPD block. As per IEC Standard. | 113.00 | EA |  | 7090.00 | 945380.60 | 7000.00 | 933380.00 | 4574.70 | 609990.50 | 609990.50 | Roksna India Private Limited
50.00 | Supply, Installation, Testing & Commissioning of Protective plug (one pair), energy-coordinated with DRL plug-in SPD block, for use as single-stage protective device for terminal equipment. Low voltage protection level line and integrated overcurrent protection for ADSL, ISDN Uk0 or a/b lines. To be mounted into EF 10 DRL. Installation recommended only in combination with DRL plug-in SPD block. As per IEC Standard. | 1128.00 | EA |  | 1094.00 | 1456157.76 | 2000.00 | 2662080.00 | 841.50 | 1120070.16 | 1120070.16 | Roksna India Private Limited
| Total in Figures |  |  |  |  | 10975925.76 |  | 14860201.38 |  | 15034180.24
Lowest Amount Quoted BY: DEHN INDIA PVT. LTD.(10975925.76)

## BoQ3
Government eProcurement System Created By: ANUPAM KUMAR TRIPATHI Created Date/Time: 17-Jan-2025 12:31 PM Tender Title: HIRING OF SERVICES FOR SUPPLY INSTALLATION AND COMMISSIONING OF EXTERNAL AND INTERNAL LIGHTNING PROTECTION SYSTEM AT PIPELINE INSTALLATIONS UNDER DIBIYAPUR REGIONS AS PER IEC 62305 Tender ID: 2024_GAIL_213565_1
Tender Inviting Authority: GAIL (India) LIMITED
Name of Work: Group - C [SITC of LPS at (24"ABPL)]
Tender No: GAIL/AU/C&P/P-097/24-25/AKT
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEHN INDIA PVT. LTD. (GSTN-06AADCD9928J1ZA) BID ID -778688 |  | JMV LPS Limited (GSTN-NA) BID ID -781604 |  | Roksna India Private Limited (GSTN-NA) BID ID -785428
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Air Termination Rod . As per IEC Standard.
2.00 | Supply, Installation, Testing & Commissioning of Air termination rod having total length - 4500mm, Material of air termination rod - Al, Diameter Ø D40/22/16/10mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 1.00 | EA |  | 16472.00 | 19436.96 | 10500.00 | 12390.00 | 7690.80 | 9075.14 | 9075.14 | Roksna India Private Limited
3.00 | Supply, Installation, Testing & Commissioning of Air termination rod having total length - 5000mm, Material of air termination rod - Al, Diameter Ø D40/16/10mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 60.00 | EA |  | 17616.00 | 1247212.80 | 13500.00 | 955800.00 | 7690.80 | 544508.64 | 544508.64 | Roksna India Private Limited
4.00 | Supply, Installation, Testing & Commissioning of D 8mm L 700mm air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 120.00 | EA |  | 74.00 | 10478.40 | 258.00 | 36532.80 | 229.50 | 32497.20 | 10478.40 | DEHN INDIA PVT. LTD.
5.00 | Supply, Installation, Testing & Commissioning of D 8mm L 2m air termination rod, Material of air termination rod - Almgsi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. As per IEC Standard. | 29.00 | EA |  | 952.00 | 32577.44 | 890.00 | 30455.80 | 612.00 | 20942.64 | 20942.64 | Roksna India Private Limited
6.00 | Supply, Installation, Testing & Commissioning of Clamps and Other Accessories to Hold Air Termination Rod . As per IEC Standard.
7.00 | Supply, Installation, Testing & Commissioning of Tripods for Supporting Tubes with side outlet. As per IEC Standard. | 61.00 | EA |  | 174.00 | 12524.52 | 2750.00 | 197945.00 | 4110.60 | 295880.99 | 12524.52 | DEHN INDIA PVT. LTD.
8.00 | Supply, Installation, Testing & Commissioning of Sets of Threaded Rods for Tripod. As per IEC Standard. | 61.00 | EA |  | 174.00 | 12524.52 | 2162.00 | 155620.76 | 1286.22 | 92582.12 | 12524.52 | DEHN INDIA PVT. LTD.
9.00 | Supply, Installation, Testing & Commissioning of Plastic support plate for concrete base. For protecting the roofing sheets under the concrete base(17 kg.). The Diameter Ø outside 370 mm, Diameter Ø inside 360 mm and Material EVA. As per IEC Standard. | 184.00 | EA |  | 235.00 | 51023.20 | 451.00 | 97921.12 | 530.40 | 115160.45 | 51023.20 | DEHN INDIA PVT. LTD.
10.00 | Supply, Installation, Testing & Commissioning of Concrete base for air-termination rods, for self-supporting air-termination rods in the tripod. Support Wedge- Ø16 mm, Diameter- Ø 337 mm, Material- concrete, Material of wedge- StSt & Weight 17kg. As per IEC Standard. | 551.00 | EA |  | 533.00 | 346545.94 | 750.00 | 487635.00 | 397.80 | 258641.60 | 258641.60 | Roksna India Private Limited
11.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 700mm air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 120.00 | EA |  | 235.00 | 33276.00 | 271.00 | 38373.60 | 260.10 | 36830.16 | 33276.00 | DEHN INDIA PVT. LTD.
12.00 | Supply, Installation, Testing & Commissioning of Parallel clamp to connect D 8mm L 2 m air termination rod, Material - StSt, clamping range Rd / Rd 7-10 mm. As per IEC Standard. | 43.00 | EA |  | 775.00 | 39323.50 | 271.00 | 13750.54 | 260.10 | 13197.47 | 13197.47 | Roksna India Private Limited
13.00 | Supply, Installation, Testing & Commissioning of Clamp to connect Air termination rod on Side Wall, Material - StSt, clamping range of air termination rod- Rd 10-16mm. As per IEC Standard. | 14.00 | EA |  | 775.00 | 12803.00 | 700.00 | 11564.00 | 663.00 | 10952.76 | 10952.76 | Roksna India Private Limited
14.00 | Supply, Installation, Testing & Commissioning of Anchor Fastener -2 , Size-M10x50mm, Material-SS. As per IEC Standard. | 29.00 | EA |  | 36.00 | 1231.92 | 100.00 | 3422.00 | 229.50 | 7853.49 | 1231.92 | DEHN INDIA PVT. LTD.
15.00 | Supply, Installation, Testing & Commissioning of Nut Bolt - 2 , Size-M8x50mm, Material-SS. As per IEC Standard. | 29.00 | EA |  | 19.00 | 650.18 | 25.00 | 855.50 | 106.08 | 3630.06 | 650.18 | DEHN INDIA PVT. LTD.
16.00 | Supply, Installation, Testing & Commissioning of FS Clamps (Air-termination Rod Clamps 16mm) for connecting air-termination rods to roof. As per IEC Standard. | 7.00 | EA |  | 287.00 | 2370.62 | 271.00 | 2238.46 | 225.42 | 1861.97 | 1861.97 | Roksna India Private Limited
17.00 | Supply, Installation, Testing & Commissioning of Roof/Down Conductor & Conductor Holder . As per IEC Standard.
18.00 | Supply, Installation, Testing & Commissioning of With accessories Screw and Gitty, Material SS (M5 x 50mm) | 2694.00 | EA |  | 17.00 | 54041.64 | 48.00 | 152588.16 | 30.60 | 97274.95 | 54041.64 | DEHN INDIA PVT. LTD.
19.00 | Supply, Installation, Testing & Commissioning of 8mm Al Roof Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 1655.00 | M |  | 74.00 | 144514.60 | 120.00 | 234348.00 | 211.14 | 412335.31 | 144514.60 | DEHN INDIA PVT. LTD.
20.00 | Supply, Installation, Testing & Commissioning of Roof conductor holder FB2 for flat roofs with concrete block C35/45 with double conductor holder Rd 8 mm fixed, Dimension 141 x 86 x 70 mm. As per IEC Standard. | 154.00 | EA |  | 82.00 | 14901.04 | 145.00 | 26349.40 | 198.90 | 36144.11 | 14901.04 | DEHN INDIA PVT. LTD.
21.00 | Supply, Installation, Testing & Commissioning of Roof Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base | 1669.00 | EA |  | 172.00 | 338740.24 | 145.00 | 285565.90 | 121.38 | 239048.20 | 239048.20 | Roksna India Private Limited
22.00 | Supply, Installation, Testing & Commissioning of 8mm Al Down Conductor. Diameter Ø conductor- 8 mm, Crosssection- 50 mm2, Material- AlMgSi. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 1025.00 | M |  | 74.00 | 89503.00 | 120.00 | 145140.00 | 211.14 | 255373.83 | 89503.00 | DEHN INDIA PVT. LTD.
23.00 | Supply, Installation, Testing & Commissioning of Down Conductor holder StSt for Rd 8-10 mm H 20 mm with female thread M8 preassembled with plastic base. As per IEC Standard. | 1025.00 | EA |  | 172.00 | 208034.00 | 145.00 | 175377.50 | 128.52 | 155444.94 | 155444.94 | Roksna India Private Limited
24.00 | Supply, Installation, Testing & Commissioning of Universal Connector for interconnecting roof conductor & down conductor, Material of clamp StSt, clamping range Rd 8-10 mm. As per IEC Standard. | 145.00 | EA |  | 167.00 | 28573.70 | 200.00 | 34220.00 | 260.10 | 44503.11 | 28573.70 | DEHN INDIA PVT. LTD.
25.00 | Supply, Installation, Testing & Commissioning of Lightning strike counter for digital recording of impulse currents. The device is preferably installed on the down conductors of the lightning protection system. Operating current (8/20 μs): 1 kA, Max. discharge current (10/350 μs): 100 kA, clamping range of rod: 8- 10mm, clamping range of flat: 30mm, Degree of protection: IP 65. As per IEC Standard. | 7.00 | EA |  | 16978.00 | 140238.28 | 16000.00 | 132160.00 | 9945.00 | 82145.70 | 82145.70 | Roksna India Private Limited
26.00 | Supply, Installation, Testing & Commissioning of Earthing System. As per IEC Standard.
27.00 | Supply, Installation, Testing & Commissioning of Pipe clamp D 16-168 mm (3/4-6") StSt with terminal clamp 1xRd 10 mm or 2xRd 6-8 mm for connecting metal railing with 8mm Al solid round conductor. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 90.00 | EA |  | 342.00 | 36320.40 | 631.00 | 67012.20 | 603.33 | 64073.65 | 36320.40 | DEHN INDIA PVT. LTD.
28.00 | Supply, Installation, Testing & Commissioning of GI flat (25x6mm) Strip having width- 25mm, thickness- 6mm, Material- Hot dipped Galvanized Iron, Cross Section- 150 mm2, Coating thickness- Avg. 70 microns. & Complied as per IEC 62561 for termination of down conductor from test link to the earth pit termination clamp and Interconnection of the earth pit to form type B earthing. As per IEC Standard. | 3546.00 | M |  | 176.00 | 736433.28 | 300.00 | 1255284.00 | 430.95 | 1803215.47 | 736433.28 | DEHN INDIA PVT. LTD.
29.00 | Supply, Installation, Testing & Commissioning of GI strip holder- Insulated holder, Material of construction - Dow moulded compound, height 19mm, Slot Size- 25x6 mm. | 293.00 | EA |  | 49.00 | 16941.26 | 82.00 | 28350.68 | 132.60 | 45845.12 | 16941.26 | DEHN INDIA PVT. LTD.
30.00 | Supply, Installation, Testing & Commissioning of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 250 microns of copper plating. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 131.00 | EA |  | 2196.00 | 339457.68 | 2850.00 | 440553.00 | 4508.40 | 696908.47 | 339457.68 | DEHN INDIA PVT. LTD.
31.00 | Supply, Installation, Testing & Commissioning of 22.6kg backfilled compound, - Graphite based backfill compound having low resisitvity, does not decay or leachout, moisture retention capacity 10-15%, shall be tested for thermal stability for temp range -60 to +60 degree C, shall have sulphure content less than 0.04% shall have resistivity of 0.08 ohm or less, ROHS certified, to fill the bore area around the rod. As per IEC Standard. | 131.00 | EA |  | 2154.00 | 332965.32 | 1800.00 | 278244.00 | 2295.00 | 354761.10 | 278244.00 | JMV LPS Limited
32.00 | Supply, Installation, Testing & Commissioning of SS 316 grade Termination clamp to terminate the load on earth electrode for termination, Material of construction - 316 grade stainless steel, Dimension - 160x35x3 mm. As per IEC Standard. | 131.00 | EA |  | 482.00 | 74507.56 | 649.00 | 100322.42 | 948.60 | 146634.59 | 74507.56 | DEHN INDIA PVT. LTD.
33.00 | Supply, Installation, Testing & Commissioning of Poly plastic pit cover of material- Polymer Body & Cover, Product Code- HEP, Dimensions- 308 mm (L) x 308 mm (W) X 214 mm (H), Weight 2.5 kg (5.50 LBS). | 131.00 | EA |  | 1689.00 | 261085.62 | 1100.00 | 170038.00 | 1071.00 | 165555.18 | 165555.18 | Roksna India Private Limited
34.00 | Supply, Installation, Testing & Commissioning of UNI disconnecting clamp with intermediate plate for round and flat conductor, Material StSt, clamping range Rd / Fl 8-10 / 30 mm. AllConductors/Components shall conform to the requirements of IEC 62305 & IEC 62561. | 138.00 | EA |  | 120.00 | 19540.80 | 1400.00 | 227976.00 | 382.50 | 62286.30 | 19540.80 | DEHN INDIA PVT. LTD.
35.00 | Supply, Installation, Testing & Commissioning of Internal Protection System (SPD’s) . As per IEC Standard.
36.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single-pole combined lightning current and surge arrester, Type 1 SPD. . As per IEC Standard. | 43.00 | EA |  | 11808.00 | 599137.92 | 7000.00 | 355180.00 | 21481.20 | 1089956.09 | 355180.00 | JMV LPS Limited
37.00 | Supply, Installation, Testing & Commissioning of Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (N-PE) Single-pole combined lightning current arrester, Type 1 SPD. . As per IEC Standard. | 14.00 | EA |  | 9118.00 | 150629.36 | 7000.00 | 115640.00 | 15973.20 | 263877.26 | 115640.00 | JMV LPS Limited
38.00 | Supply, Installation, Testing & Commissioning of Combined lightning current and surge arrester for use in single phase TT and TN system at mains LT panel (1 phase, 230 V), Type 1 + 2 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 18.00 | EA |  | 5095.00 | 108217.80 | 16000.00 | 339840.00 | 6762.60 | 143637.62 | 108217.80 | DEHN INDIA PVT. LTD.
39.00 | Supply, Installation, Testing & Commissioning of For 48 V DC Supply: Coordinated and modular single-pole spark-gap-based lightning current arrester for d.c. applications from 12 to 60 volts; with remote signalling contact for monitoring device (floating changeover contact). Type 1 SPD (If Breaker Rating < 250 A) . As per IEC Standard. | 28.00 | EA |  | 15940.00 | 526657.60 | 12500.00 | 413000.00 | 7293.00 | 240960.72 | 240960.72 | Roksna India Private Limited
40.00 | Supply, Installation, Testing & Commissioning of Arrester for CCTV, Data Networks and Ethernet Applications, Universal arrester for Industrial Ethernet, Power over Ethernet (IEEE 802.3 compliant up to PoE++ / 4PPoE) and similar applications in structured cabling systems according to class E up to 250 MHz. Protection of all pairs by powerful gas discharge tubes. DIN rail mounted adapter type with sockets, for protecting four pairs of data network interfaces via RJ45 sockets, for single-user application or application in 19 inch cabinets, space-saving. Max. continuous operating voltage (d.c.) (Uc ): 48V RJ 45 Connection or Ethernet Cable . As per IEC Standard. | 53.00 | EA |  | 2434.00 | 152222.36 | 4000.00 | 250160.00 | 7140.00 | 446535.60 | 152222.36 | DEHN INDIA PVT. LTD.
41.00 | Supply, Installation, Testing & Commissioning of Modular and pluggable four-pole surge arrester with integrated Advanced Circuit Interruption (ACI) switch / spark gap for TT and TN-S systems (3+1 configuration); FM version with floating remote signaling contact, Type 2 SPD according to EN 61643-11 (no external backup fuse required) . As per IEC Standard. | 2.00 | EA |  | 12784.00 | 30170.24 | 7500.00 | 17700.00 | 37485.00 | 88464.60 | 17700.00 | JMV LPS Limited
42.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-232, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 24.00 | EA |  | 4171.00 | 118122.72 | 6050.00 | 171336.00 | 5355.00 | 151653.60 | 118122.72 | DEHN INDIA PVT. LTD.
43.00 | Supply, Installation, Testing & Commissioning of Serial Surge protector RS-485, underwriters laboratories (UL) listed. With DIN rail mounting kit, Operating temperature -10 to 70 degree C . As per IEC Standard. | 24.00 | EA |  | 4171.00 | 118122.72 | 6050.00 | 171336.00 | 5355.00 | 151653.60 | 118122.72 | DEHN INDIA PVT. LTD.
44.00 | Supply, Installation, Testing & Commissioning of SPD FOR PLC SUPPLY . As per IEC Standard.
45.00 | Supply, Installation, Testing & Commissioning of Space-saving combined lightning current and surge arrester module with Life Check feature for protecting four single lines sharing a common reference potential as well as unbalanced interfaces, for 24 V DC . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Base part as a very space-saving and universal four pole feedthrough terminal for the insertion of a protection module without signal disconnection if the protection module is removed . As per IEC Standard. | 37.00 | EA |  | 4075.00 | 177914.50 | 9200.00 | 401672.00 | 11271.00 | 492091.86 | 177914.50 | DEHN INDIA PVT. LTD.
46.00 | Supply, Installation, Testing & Commissioning of SPDs FOR FIELD DEVICES/EQUPMENTS (PRESSURE & TEMPERATURE TRANSMITTERS etc.) . As per IEC Standard.
47.00 | Supply, Installation, Testing & Commissioning of Surge arrester with a low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Parallel Connection ½ NTP thread) For 24 V DC Supply (for PTs) . As per IEC Standard. | 76.00 | EA |  | 3383.00 | 303387.44 | 8000.00 | 717440.00 | 7191.00 | 644888.88 | 303387.44 | DEHN INDIA PVT. LTD.
48.00 | Supply, Installation, Testing & Commissioning of Surge arrester with low-capacitance protective circuit for protecting intrinsically safe measuring circuits and bus systems, meets FISCO requirements. Insulation strength > 500 V to earth. (For Series Connection ½ NTP thread) For 24 V DC Supply (for TTs) . As per IEC Standard. | 23.00 | EA |  | 4383.00 | 118954.62 | 8000.00 | 217120.00 | 7191.00 | 195163.74 | 118954.62 | DEHN INDIA PVT. LTD.
49.00 | Supply, Installation, Testing & Commissioning of SPD’s FOR TELEPHONE LINE PROTECTION . As per IEC Standard.
50.00 | Supply, Installation, Testing & Commissioning of Lightning current carrying DRL plug-in SPD block (10 pairs) for almost all applications. Expandable to a combined lightning current and surge arrester by means of a DRL protective plug. The integrated disconnection block contacts allow testing, measuring and patching with plugged-in protection.The three-pole gas discharge tubes have a fail-safe function with visual fault indicator. . As per IEC Standard. Along with Supply, Installation, Testing & Commissioning of Snap-on earthing frame for earthing and installation of max 10 DRL protection modules. Plugs into a 10-pair disconnection block or DRL plug- in SPD block. As per IEC Standard. | 92.00 | EA |  | 7090.00 | 769690.40 | 7000.00 | 759920.00 | 4574.70 | 496629.43 | 496629.43 | Roksna India Private Limited
51.00 | Supply, Installation, Testing & Commissioning of Protective plug (one pair), energy-coordinated with DRL plug-in SPD block, for use as single-stage protective device for terminal equipment. Low voltage protection level line and integrated overcurrent protection for ADSL, ISDN Uk0 or a/b lines. To be mounted into EF 10 DRL. Installation recommended only in combination with DRL plug-in SPD block. As per IEC Standard. | 924.00 | EA |  | 1094.00 | 1192810.08 | 2000.00 | 2180640.00 | 841.50 | 917504.28 | 917504.28 | Roksna India Private Limited
| Total in Figures |  |  |  |  | 9023815.18 |  | 11909017.84 |  | 11428182.00
Lowest Amount Quoted BY: DEHN INDIA PVT. LTD.(9023815.18)

## BOQ Summary
BOQ Summary Details Tender Title: HIRING OF SERVICES FOR SUPPLY INSTALLATION AND COMMISSIONING OF EXTERNAL AND INTERNAL LIGHTNING PROTECTION SYSTEM AT PIPELINE INSTALLATIONS UNDER DIBIYAPUR REGIONS AS PER IEC 62305 Tender ID: 2024_GAIL_213565_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 8891663.44 | L1
| 2 | JMV LPS Limited (BID ID -781604) | 10388943.02 | L2
| 3 | Roksna India Private Limited (BID ID -785428) | 13384693.02 | L3
BoQ2 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 10975925.76 | L1
| 2 | JMV LPS Limited (BID ID -781604) | 14860201.38 | L2
| 3 | Roksna India Private Limited (BID ID -785428) | 15034180.24 | L3
BoQ3 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 9023815.18 | L1
| 2 | Roksna India Private Limited (BID ID -785428) | 11428182.00 | L2
| 3 | JMV LPS Limited (BID ID -781604) | 11909017.84 | L3

## Preferential Bidder BOQ Summary
Preferential Bidder Non-Itemwise BOQ Summary Details Tender Title: HIRING OF SERVICES FOR SUPPLY INSTALLATION AND COMMISSIONING OF EXTERNAL AND INTERNAL LIGHTNING PROTECTION SYSTEM AT PIPELINE INSTALLATIONS UNDER DIBIYAPUR REGIONS AS PER IEC 62305 Tender ID: 2024_GAIL_213565_1
Sheet Name | Sl.No | Bidder Name | Amount | Difference Amount from L1 | Difference Percentage from L1 | Tolerance Percentage | Preference Category
BoQ1 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 8891663.44
| 2 | JMV LPS Limited (BID ID -781604) | 10388943.02
| 3 | Roksna India Private Limited (BID ID -785428) | 13384693.02
BoQ2 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 10975925.76
| 2 | JMV LPS Limited (BID ID -781604) | 14860201.38
| 3 | Roksna India Private Limited (BID ID -785428) | 15034180.24
BoQ3 | 1 | DEHN INDIA PVT. LTD. (BID ID -778688) | 9023815.18
| 2 | Roksna India Private Limited (BID ID -785428) | 11428182.00
| 3 | JMV LPS Limited (BID ID -781604) | 11909017.84