## BoQ1
Government eProcurement System Created By: SUJATHA R Created Date/Time: 04-Jul-2024 03:21 PM Tender Title: Extension of 380V Power Supply to Polar Crane panel and 180T Crane in UMA at Unit 4 including supply of specified materials Tender ID: 2024_NPCIL_193972_1
Tender Inviting Authority: CE(E-MP), KK-3&4
Name of Work: Extension of 380V Power Supply to Polar Crane panel and 180T Crane in UMA at Unit 4 including supply of specified materials
Contract No: NPCIL/KK-3&4/CONST/E&I/PT/2024/65
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Prime Electriks and Machinery Services(GSTN-NA)--699868
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Excavation of trenches for cable laying including dewatering wherever required, necessary shoring, strutting in hard soil / disintegrated rocks etc, either manually or with the use of mechanical equipment to proper grades and levels, including refilling with selected earth and disposal off the surplus earth as directed upto a lead of 2 km all complete as per IS Standard . | 2250.00 | Cubic-m |  | 320.00 | 720000.00 | 720000.00 | Prime Electriks and Machinery Services
2.00 | Supply & Providing of 9 " x 4 1/2" x 3" table moulded bricks/Flyash bricks for cable protection (18 nos/mtr) | 50000.00 | Nos. |  | 10.50 | 525000.00 | 525000.00 | Prime Electriks and Machinery Services
3.00 | Transporation and Laying of 3C x 150 Sqmm size 11KV grade 3Core Al cable in excavated cable trenches, RCC hume pipes,cable covered by cement slab and testing ,comissioning of the above cables.Scope includes clamping of cable,cable without any kinks and bend all as per specification . (Cables will be issued by NPCIL) | 100.00 | mtr |  | 330.00 | 33000.00 | 33000.00 | Prime Electriks and Machinery Services
4.00 | Supply and installation of 3Cx 150 Sqmm 11KV Heat Shirnkable end indoor kits suitable for 11KV, XLPE Aluminium Armoured cable and all as required to complete the job in all respects, all as per specification. | 2.00 | Nos. |  | 11800.00 | 23600.00 | 23600.00 | Prime Electriks and Machinery Services
5.00 | Supply and installation of 3Cx 150 Sqmm 11KV Heat Shrinkable end Outdoor kits suitable for 11KV, XLPE Aluminum Armoured cable and all as required to complete the job in all respects, all as per specification. | 1.00 | Nos. |  | 11800.00 | 11800.00 | 11800.00 | Prime Electriks and Machinery Services
6.00 | Transporation and laying of following sizes of 1100V grade XLPE Armoured cables .Scope includes laying of following size of Al/Cu cable in excavated trench / Hume pipes/wall/cable Tray and support structure, using Lead raw plugs for clamping of cable ,cable laying without any kinks and bend, aluminimum tag with identifcation for both side cable etc, and all as required as per specification .
6.10 | 3.5C x 400 Sqmm XLPE Aluminium Armoured Cable | 4000.00 | mtr |  | 360.00 | 1440000.00 | 1440000.00 | Prime Electriks and Machinery Services
6.20 | 4Cx50 Sqmm XLPE Aluminium Armoured Cable | 2000.00 | mtr |  | 186.00 | 372000.00 | 372000.00 | Prime Electriks and Machinery Services
6.30 | 4Cx25 Sqmm XLPE Aluminium Armoured Cable | 1250.00 | mtr |  | 96.00 | 120000.00 | 120000.00 | Prime Electriks and Machinery Services
6.40 | 4C x2.5 Sqmm XLPE copper Armoured Cable | 250.00 | mtr |  | 60.00 | 15000.00 | 15000.00 | Prime Electriks and Machinery Services
7.00 | Removal and relaying of 5C x 150 Sqmm unarmoured copper LT cable.Scope including removal from existing trench,shifting of cable from 0.00M el to 20M El height of UKC building, clamping of cable on wall using leadrawl plugs,cable laying without any kinks and bend, aluminimum tag with identifcation for both side cable etc, and all as required as per specification . | 200.00 | mtr |  | 330.00 | 66000.00 | 66000.00 | Prime Electriks and Machinery Services
8.00 | Glanding and termination following size Al armoured/Cu unarmoured Cable. Scope includes Supply and installation of double compression heavy duty brass cable gland with nickel plated and Suitable size Aluminium/copper Lugs, connection, bolt nut accessories etc, and all as required at site and all as per specification.
8.10 | 3.5C x 400 Sqmm XLPE Aluminium Armoured Cable | 60.00 | Nos. |  | 3850.00 | 231000.00 | 231000.00 | Prime Electriks and Machinery Services
8.20 | 4Cx50 Sqmm XLPE Aluminium Armoured Cable | 12.00 | Nos. |  | 2600.00 | 31200.00 | 31200.00 | Prime Electriks and Machinery Services
8.30 | 4Cx25 Sqmm XLPE Aluminium Armoured Cable | 30.00 | Nos. |  | 1960.00 | 58800.00 | 58800.00 | Prime Electriks and Machinery Services
8.40 | 4C x2.5 Sqmm XLPE copper Armoured Cable | 10.00 | Nos. |  | 1350.00 | 13500.00 | 13500.00 | Prime Electriks and Machinery Services
8.50 | 5C x150 Sqmm copper UnArmoured Cable | 10.00 | Nos. |  | 4200.00 | 42000.00 | 42000.00 | Prime Electriks and Machinery Services
9.00 | Transportation of 1.6 MVA 11KV /380V, 50 Hz transformer from kknpp 1&2 to transformer service factory and back to KKNPP 3&4 area , complete service of transformer, supply & filling of new Transformer Oil required qty, Oil filteration , Epoxy painting of Transformer, Installation, testing and commissioning . Scope includes supply and installation of OFF load Tap changer of transformer, replacement of all gaskets, Transformer tank patch work,Painting of transformer with one coat of epoxy primer and two coats of epoxy paint (colour as decided by ENC), testing and repair & service of Transformer as per IS, wiring work,faulty spare parts replacement etc. Installation scope includs assembly of the transformer, transformer positioning, alignment,welding of transformer to base plate on the foundation , (Transformer details available at tender specification). The rewinding of the transformer is covered under seperate item of the contract | 1.00 | Nos. |  | 240000.00 | 240000.00 | 240000.00 | Prime Electriks and Machinery Services
10.00 | Supply of Dual paper insulated copper wire for rewinding work of the outdoor ONAN type transformer of 1.6MVA, 11KV/380V ,50Hz. Scope include supply of copper wire, rewinding, and all the materials required for rewinding and installation on the transformer core and connections to the tap changer and terminals. The burnt copper winding shall be returned to NPCIL store. | 600.00 | kg |  | 420.00 | 252000.00 | 252000.00 | Prime Electriks and Machinery Services
11.00 | Fabrication ,supply and erection of transformer oil cooling Fins (Radiator) suitable for outdoor ONAN type transformer of 1.6MVA, 11KV/380V ,50Hz. Scope includes assembling, alignment,supply of necessary size of bolt & nuts, gaskets etc,all as per specification . | 2.00 | Sets |  | 24000.00 | 48000.00 | 48000.00 | Prime Electriks and Machinery Services
12.00 | Fabrication , assembling in existing oil type transformer repair work involving CRCA Sheet steel work materials for 1.6MVA oil type Transformer like conservator tank, HT &LT Cable terminal box, Explosive Vent pipe, transformer tank and other all type of supports as required for existing transformer. Scope includes welding ,cutting drilling,cleaning of transformer,transformer tank patching work,supply of necessary size of bolt & nuts, erection etc, all as per specification . | 500.00 | kg |  | 155.00 | 77500.00 | 77500.00 | Prime Electriks and Machinery Services
13.00 | Main LT Outdoor Panel Fabrication,Supply, installation, testing and commissioning of LT Outdoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant , Bureau of Indian Standards & as approved.(Incomming cable chamber Suitable for connecting 14nos,3.5Cx400Sqmm cable) Incomer Feeder : 1 No : 3200A 4P 50KA EDO ACB with all inbuilt protection, CT &PT , microprocessor numeric based OC and EF relay, control fuses, ammeter, voltmeter, LED indication lamps all as per IS. - 1 set Bus bar 3200A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 630A TPN Thermal magnetic MCCB -3Nos 400A TPN Thermal magnetic MCCB -2Nos 250ATPN Thermal magnetic MCCB -3No 100A TPN Thermal magnetic MCCB - 3No 63A TPN Thermal magnetic MCCB - 3No Scope includes installation of panel positioning in existing concrete pedestal, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification | 1.00 | Nos. |  | 2900000.00 | 2900000.00 | 2900000.00 | Prime Electriks and Machinery Services
14.00 | Fabrication,Supply, installation, testing and commissioning of LT Indoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification, conforming to latest edition of relevant, Bureau of Indian Standards & as approved. (Incoming Suitable for connecting 2nos, 3.5Cx400Sqmm cable) Incomer : 1 No : 630A TPN Thermal magnetic MCCB with CTs , control fuses, multifunction meter and LED indication Lamps. Bus bar 800A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 400A TPN Thermal magnetic MCCB -2Nos 100A TPN Thermal magnetic MCCB -4No 63A TPN Thermal magnetic MCCB - 2No Scope includes shifting of LT panel in 20Mtrs Elevation UKC-4 building, installation of panel positioning in existing Support structure/concrete pedestal, required size of anchnor, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification | 1.00 | Nos. |  | 420000.00 | 420000.00 | 420000.00 | Prime Electriks and Machinery Services
15.00 | Fabrication,Supply, installation, testing and commissioning of LT Indoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant , Bureau of Indian Standards & as approved.(Incoming Feeder Suitable for connecting 2nos, 3.5Cx400Sqmm cable) Incomer : 1 No : 630A TPN Thermal magnetic MCCB with CTs ,control fuses,multifunction meter and LED indication Lamps. Bus bar 800A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 400A TPN Thermal magnetic MCCB -1Nos 250A TPN Thermal magnetic MCCB -2Nos 100A TPN Thermal magnetic MCCB -3No 63A TPN Thermal magnetic MCCB - 2No | 1.00 | Nos. |  | 540000.00 | 540000.00 | 540000.00 | Prime Electriks and Machinery Services
16.00 | Fabrication, Supply, installation, testing and commissioning of wall mounted LT motor DOL stater panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant , Bureau of Indian Standards & as approved. Incomer 400A TPN Thermal magnetic MCCB -1No Bus bar 400A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: Outgoing feeders -132KW Dol Feeder arrangement with required rating of CTs, OLR , contactor, LT motor protection relay, single phase preventor ,Voltmeter, ammeter, LED indication lamps, ON/OFFpush button, outgoing busbar arrangement for two separate cable connection and other hardware accessories etc Scope includes installation of panel on wall/existing support structure, required size of anchnor fasteners Bolt nut accessories and all as required at site and all as per specification. panel alignment with existing panel, panel welding, painting, earth connection Bolt nut accessories and all as required at site and all as per specification | 1.00 | Nos. |  | 240000.00 | 240000.00 | 240000.00 | Prime Electriks and Machinery Services
17.00 | Fabrication, Supply, installation, testing and commissioning of wall mounted LT motor DOL stater panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant , Bureau of Indian Standards & as approved. Incomer 400A TPN Thermal magnetic MCCB -1No Bus bar 400A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: Outgoing feeders -132KW Dol Feeder arrangement with required rating of CTs, OLR , contactor, LT motor protection relay, single phase preventor ,Voltmeter, ammeter, LED indication lamps, ON/OFFpush button, outgoing busbar arrangement for two separate cable connection and other hardware accessories etc Scope includes installation of panel on wall/existing support structure, required size of anchnor fasteners Bolt nut accessories and all as required at site and all as per specification. panel alignment with existing panel, panel welding, painting, earth connection Bolt nut accessories and all as required at site and all as per specification | 2.00 | Nos. |  | 265000.00 | 530000.00 | 530000.00 | Prime Electriks and Machinery Services
18.00 | Supply & installation of 40 mm dia, 3 mtr long MS rod, directly driven in earth, Hole should be filled with bentonite powder and welding connection between the rod and earth flat, welding area painting, 2x2 feet square RCC concrete chamber with top cover for earth pit, painting of earth chamber, identification etc and all as per specification. | 4.00 | Nos. |  | 9000.00 | 36000.00 | 36000.00 | Prime Electriks and Machinery Services
19.00 | Supply and installation of following size GI flat. Installation includes welding of flats, clamping of flats in wall using anchor fastener, welding on support structure and welding area painting etc, all as per specification.
19.10 | 50X10mm GI Flat | 60.00 | mtr |  | 340.00 | 20400.00 | 20400.00 | Prime Electriks and Machinery Services
19.20 | 50x6mm GI Flat | 400.00 | mtr |  | 320.00 | 128000.00 | 128000.00 | Prime Electriks and Machinery Services
20.00 | Supply , Fabrication and erection of Structural steel members made put of M.S angles, ISMC channel, ISMC flats, chequred plates, pipes, channel , tubes , rods, , etc conforming to relevant IS etc, including anchor fasteners for support erection, cost of welding, welding rods, drilling holes, bolts / nuts wherever required and providing and applying two or more coats of approved quality synthetic enamel paint over a coat of zinc chromate yellow primer etc, as per drawing and specifications . | 3.00 | MT |  | 145000.00 | 435000.00 | 435000.00 | Prime Electriks and Machinery Services
21.00 | Supply and installation of 100mm Size of Heavy duty GI pipe for laying of cable . Scope also includes installation of pipe on wall,support by using GI clamps,laying already excavated trench all as per specification . | 50.00 | mtr |  | 680.00 | 34000.00 | 34000.00 | Prime Electriks and Machinery Services
22.00 | Supply and installation of NP -2 class RCC hume pipe of size 300 mm dia,with collars,cementing has to be done where ever collar is used etc, all as per specification . (excavation will be measured in respective item) | 60.00 | mtr |  | 1350.00 | 81000.00 | 81000.00 | Prime Electriks and Machinery Services
23.00 | Supply, fabrication and erection of various type supports for laying of cable from 0.00M El UKC to polar crane Busbar panel 20.00M El outside wall as per site requirement using various size of ISMC,ISA,Flats,MS plates . Scope includes erection of Fabricated supports in higher elevation every 0.75 Mtrs interival by using suitable size of anchnor fasteners, Scaffolding arrangement for support erection from 0.00M to 20.00M height elevation, all safety precaustions,welding ,cutting drilling,painting with single coat of red oxide primer & double coats of silver enamel paint,supply of necessary size of bolt & nuts, erection etc, all as per specification . (Anchnor fasteners measures respective item) | 3.00 | MT |  | 177000.00 | 531000.00 | 531000.00 | Prime Electriks and Machinery Services
24.00 | Providing and Laying plain cement concrete 1:2:4, using 20mm and down graded stone aggregate at all height including mechanical mixing levelling, compaction , vibrating, scaffolding, shuttering, finishing smooth the exposed surfaces of concrete , curing etc complete and all as required at site and standards specification | 21.00 | Cubic-m |  | 10800.00 | 226800.00 | 226800.00 | Prime Electriks and Machinery Services
25.00 | Providing cutting ,bending placing and tying mild steel, high yield steel reinforcement in RCC works including providing spacer blocks in CM 1:2, binding wires etc. complete at all elevations as per requirements including dewatering wherever necessary etc complete and all as required at site and specifications (Transformer plinth) | 1.00 | MT |  | 82000.00 | 82000.00 | 82000.00 | Prime Electriks and Machinery Services
26.00 | Supply and Installation 8mm anchor fasteners for already fabricated polar crane cable route support erection work and all as required to complete the job in all respects, suitable for concrete structures. | 1000.00 | Nos. |  | 144.00 | 144000.00 | 144000.00 | Prime Electriks and Machinery Services
27.00 | Dismantling, Shifting and Reinstallation of wall mounted panel. Scope includes dismantling from support structure/wall, installation of panel positioning in existing support structure or wall by using supply of 4 nos of required Size anchor fastener ,alignment ,panel welding, painting, hardware accessories and all as required at site Incomer : 1No.250A TPN SFU with HRC fuse links, Indication lamps ( LED type) and control fuses - 1 No Bus bars : 250 A TPN + Tinned copper busbars suitable for 35kA for 1 sec. Outgoing feeders 100A TPN Thermal magnetic MCCB with protection S/C, adjustable O/L and Earth fault release - 4 Nos 63A TPN Thermal magnetic MCCB with protection S/C, adjustable O/L and Earth fault release - 5 Nos | 2.00 | Nos. |  | 6000.00 | 12000.00 | 12000.00 | Prime Electriks and Machinery Services
28.00 | Supply and Laying of single core 16 sqmm flexible copper bare conductor for earthing. Scope includes laying of copper conductor wherever earthing point required like Junction box, Adopter box , LDB and wall mounted panels, and all as required to complete the job in all respects. | 50.00 | mtr |  | 233.00 | 11650.00 | 11650.00 | Prime Electriks and Machinery Services
29.00 | Termination of single core16 sqmm flexible copper conductor cable for earthing. Scope includes supply of 2nos ring type copper lugs each side for earth point connection, crimping of 16 sqmm lugs ,bolt nuts accessories etc, all as required to complete the job in all respects. | 60.00 | Nos. |  | 105.00 | 6300.00 | 6300.00 | Prime Electriks and Machinery Services
30.00 | Fabrication, supply and installation of following type Indoor wall mounted Main SFU feeder unit with HRC Fuse , powder coated CRCA sheet steel enclosure, sufficient space for 3.5cx400Sqmm Al armoured cable in and out termination work, earth point both side for external connection. Scope includes installation of Junction box on wall by using supply of 4 nos of required Size anchor fastener/welding on support structure , painting, hardware accessories and all as required at site as per specification.
30.10 | 250A Main SFU feeder with enclosure | 8.00 | Nos. |  | 43000.00 | 344000.00 | 344000.00 | Prime Electriks and Machinery Services
30.20 | 100A Main SFU feeder with enclosure | 8.00 | Nos. |  | 36000.00 | 288000.00 | 288000.00 | Prime Electriks and Machinery Services
31.00 | Supply and installation of Cable route markers with 35x35x6mm 1mtrs long angle and LT cable identification for underground cables routes. Scope includes supply and installation of cast iron route markers with 200x200x200mm size 1:2:4 concrete base, painting marker red background and white arrow identification and installation of route marker on existing cable route area etc, and all as required at site and as per specification.( LT Power Cable ) | 60.00 | Nos. |  | 960.00 | 57600.00 | 57600.00 | Prime Electriks and Machinery Services
32.00 | Providing and Fixing chain link fencing to M S Angle posts using PVC coated GI wire chain link fencing 50x50x9 G as per IS-2721 using TATA or equivalent make GI wire, with 6 mm dia MS rods tied vertically on posts including providing PVC coated 4 mm dia GI wire horizontally at top and bottom, 6mm dia MS rods tied vertically on posts using 16G G.I annealed binding wire etc., complete as per drawings and specifications | 300.00 | Square meter |  | 435.00 | 130500.00 | 130500.00 | Prime Electriks and Machinery Services
33.00 | Supply and installation of 1000mm wide 3mm thick rubber mats for maintenance of 33KV panels and LV panels as per IS15632. Installation scope includes cleaning the area, applying adhesive suitable for rubber mat, laying of rubber mat etc. and all as required at site and all as per specification. | 50.00 | Square meter |  | 3300.00 | 165000.00 | 165000.00 | Prime Electriks and Machinery Services
| Total in Figures |  |  |  |  | 11683650.00
Lowest Amount Quoted BY: Prime Electriks and Machinery Services(11683650.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension of 380V Power Supply to Polar Crane panel and 180T Crane in UMA at Unit 4 including supply of specified materials Tender ID: 2024_NPCIL_193972_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Prime Electriks and Machinery Services | 11683650.00 | L1