## BoQ1
Government eProcurement System Created By: HASTI MAL NAHAR Created Date/Time: 30-Jan-2025 04:18 PM Tender Title: Supply, installation, testing and commissioning of main Distribution electrical system of Type-II, Type-III, Type-IV and H2B quarters in Anukiran and Anuchhaya colonies including other miscellaneous work at RR site colonies. Tender ID: 2024_NPCIL_208271_1
Tender Inviting Authority:
Name of Work: Supply, installation, testing & commissioning of main Distribution electrical system of Type-II, Type-III, Type-IV and H2B quarters in Anukiran & Anuchhaya colonies including other miscellaneous work at RR site colonies.
Contract No: NPC/RRS/90/2024/CPP-PT-A2751R
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Aditya Techno Products Private Limited (GSTN-09AAGCA0910L1ZS) BID ID -752706 |  | JAGGI ELECTRICALS (GSTN-NA) BID ID -752978 |  | Vijayvargia Electricals (GSTN-NA) BID ID -752984
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply & Installation including testing & commissioning of double door type, outdoor, Main & sub-feeder distribution panel under item No. 1.1,1.2 & 1.3.
1.10 | Supply of double door, 3 phase 4 wire, 415V, 50Hz, main distribution panel out door type, made of 2mm thick CRCA / GP sheet and base frame ISMC -100. Having following components:- a) 1 No. 3 pole, 400Amp., 415V, 50Hz, 35KA, MCCB make Schneider/ Legrand/L&T/ Crompton Greaves make for incomer. b) 6 nos. 3 pole, 250 Amp, 415 V, 50 Hz, 35KA, MCCB Make: Schneider/ Legrand/L&T/ Crompton Greaves for outgoing. Note: For more details refer technical specification (section-V of tender). | 4.00 | Nos. |  | 277862.00 | 1111448.00 | 349999.50 | 1399998.00 | 446250.00 | 1785000.00 | 1111448.00 | Aditya Techno Products Private Limited
1.20 | Supply of double door, 3 phase 4 wire, 415V, 50Hz, outdoor type distribution panel, 2mm thick CRCA / GP sheet and base frame ISMC -100. having following components:- a) 1 No. 3 pole, 250Amp., 415 V, 50 Hz ,35KA, MCCB having adjustable thermal release setting with terminal spreaders make Schneider/ Legrand/L&T/ Crompton Greaves make for incomer. b) 7 nos. 3 pole, 100 Amp, 415 V, 50 Hz 35KA, MCCB Make: Schneider/ Legrand/L&T/ Crompton Greaves for outgoing. Note: For more details refer technical specification (section-V of tender). | 15.00 | Nos. |  | 197488.00 | 2962320.00 | 259999.00 | 3899985.00 | 312000.00 | 4680000.00 | 2962320.00 | Aditya Techno Products Private Limited
1.30 | Installation of main & sub-feeder panel includes preparation of 2 Nos. of RCC foundations having size- 500x300x1000 mm with required reinforcement, cement, coarse and aggregates in the ratio of 1:3:6, smooth plastering work all around the foundations with cement mortar ratio 1:4, MS EP 8 mm thick 500x200mm with legs 300 mm long and water curing etc. complete as per direction of EIC and technical specification. | 19.00 | Nos. |  | 5100.00 | 96900.00 | 9999.00 | 189981.00 | 6000.00 | 114000.00 | 96900.00 | Aditya Techno Products Private Limited
2.00 | Supply & Installation of ISI marked, 1.1 KV grade, PVC Insulated, Fire resistant sheathing, Aluminum Conductor, Steel Armoured (Galvanized flat steel strip) heavy duty power Cable PVC Sheathed cables confirm to IS: 1554 Part-I Make- Finolex / Polycab / Universal/ KEI / Havells/ NICCO/ RPG and laying in cable trenches/Hume pipes/GI pipes / on wall etc. The scope also includes removal of existing cable & deposited in sectional store etc. Cost of making trench and laying of GI pipes / Hume pipes have either been covered separately or already laid during construction of building/ road.
2.01 | Supply of 4 C x 10 sq. mm cable. | 2000.00 | M |  | 196.00 | 392000.00 | 159.00 | 318000.00 | 150.00 | 300000.00 | 300000.00 | Vijayvargia Electricals
2.02 | Supply of 4 C x 25 sq. mm cable. | 1500.00 | M |  | 263.00 | 394500.00 | 219.00 | 328500.00 | 210.00 | 315000.00 | 315000.00 | Vijayvargia Electricals
2.03 | Supply of 4 C x 35 sq. mm cable. | 6500.00 | M |  | 355.00 | 2307500.00 | 289.00 | 1878500.00 | 270.00 | 1755000.00 | 1755000.00 | Vijayvargia Electricals
2.04 | Supply of 3.5 C x 150 sq. mm cable. | 2000.00 | M |  | 1053.00 | 2106000.00 | 849.00 | 1698000.00 | 780.00 | 1560000.00 | 1560000.00 | Vijayvargia Electricals
2.05 | Supply of 3.5 C x 400 sq. mm cable. | 1250.00 | M |  | 2630.00 | 3287500.00 | 2199.00 | 2748750.00 | 1935.00 | 2418750.00 | 2418750.00 | Vijayvargia Electricals
2.06 | Installation of 4 C x 10 sq. mm cable. | 2000.00 | M |  | 7.00 | 14000.00 | 19.00 | 38000.00 | 20.00 | 40000.00 | 14000.00 | Aditya Techno Products Private Limited
2.07 | Installation of 4 C x 25 sq. mm cable. | 1500.00 | M |  | 10.00 | 15000.00 | 29.00 | 43500.00 | 30.00 | 45000.00 | 15000.00 | Aditya Techno Products Private Limited
2.08 | Installation of 4 C x 35 sq. mm cable. | 6500.00 | M | 1.00 | 12.00 | 78000.00 | 29.00 | 188500.00 | 40.00 | 260000.00 | 78000.00 | Aditya Techno Products Private Limited
2.09 | Installation of 3.5 C x 150 sq. mm cable. | 2000.00 | M | 2.00 | 22.00 | 44000.00 | 49.00 | 98000.00 | 50.00 | 100000.00 | 44000.00 | Aditya Techno Products Private Limited
2.10 | Installation of 3.5 C x 400 sq. mm cable. | 1250.00 | M | 3.00 | 35.00 | 43750.00 | 99.00 | 123750.00 | 65.00 | 81250.00 | 43750.00 | Aditya Techno Products Private Limited
3.00 | Supply & Installation of heavy Gauge G.I. Saddle & base with screw for following sizes of PVC insulated Aluminum armoured cables.
3.10 | 4C x 10 sq.mm | 300.00 | Nos. | 4.00 | 22.00 | 6600.00 | 19.00 | 5700.00 | 10.00 | 3000.00 | 3000.00 | Vijayvargia Electricals
3.20 | 4C x 25 sq.mm | 200.00 | Nos. | 5.00 | 23.00 | 4600.00 | 29.00 | 5800.00 | 15.00 | 3000.00 | 3000.00 | Vijayvargia Electricals
3.30 | 4C x 35 sq.mm | 200.00 | Nos. | 6.00 | 23.00 | 4600.00 | 29.00 | 5800.00 | 25.00 | 5000.00 | 4600.00 | Aditya Techno Products Private Limited
4.00 | Termination and connection of PVC insulated Aluminum armoured cable including supply of single compression nickel plated brass cable glands and crimping type aluminium lugs make Dowells / Comet Anti-oxidation compound and other consumables to complete the jobs are in the scope of contractor.
4.10 | 4 C x 10 sq. mm cable. | 100.00 | Nos. |  | 200.00 | 20000.00 | 309.00 | 30900.00 | 250.00 | 25000.00 | 20000.00 | Aditya Techno Products Private Limited
4.20 | 4 C x 25 sq. mm cable. | 40.00 | Nos. |  | 225.00 | 9000.00 | 349.00 | 13960.00 | 325.00 | 13000.00 | 9000.00 | Aditya Techno Products Private Limited
4.30 | 5 C x 35 sq. mm cable. | 130.00 | Nos. |  | 280.00 | 36400.00 | 379.00 | 49270.00 | 350.00 | 45500.00 | 36400.00 | Aditya Techno Products Private Limited
4.40 | 3.5 C x 150 sq. mm cable. | 30.00 | Nos. |  | 725.00 | 21750.00 | 629.00 | 18870.00 | 1000.00 | 30000.00 | 18870.00 | JAGGI ELECTRICALS
4.50 | 3.5 C x 400 sq. mm cable. | 8.00 | Nos. |  | 2150.00 | 17200.00 | 1249.00 | 9992.00 | 3000.00 | 24000.00 | 9992.00 | JAGGI ELECTRICALS
5.00 | Excavation for new cable trench in all types of soil (rocky, soft, road crossing) of size up to 500-600 mm deep. X 300 mm wide No payment will be made for excavation beyond above dimensions. Scope includes removal and refaxing of inter locking tiles and refaxing and back filling with selected excavated material, watering ramming & disposing off the surplus material as per direction of EIC. Note- Blasting is not permitted. Excavation elsewhere as required shall also be done. | 2200.00 | CuM |  | 350.00 | 770000.00 | 899.00 | 1977800.00 | 600.00 | 1320000.00 | 770000.00 | Aditya Techno Products Private Limited
6.00 | Supply & Laying of fine river bed sand cushion 75 mm before laying and 75 mm after laying of the cable as directed by EIC. | 550.00 | CuM | 7.00 | 1200.00 | 660000.00 | 1999.00 | 1099450.00 | 2300.00 | 1265000.00 | 660000.00 | Aditya Techno Products Private Limited
7.00 | Supply and placing of fully baked A-class standard clay bricks after laying cable and layers of sand. Sample of brick shall be approved by EIC. | 120000.00 | Nos. | 7.00 | 6.50 | 780000.00 | 9.00 | 1080000.00 | 10.00 | 1200000.00 | 780000.00 | Aditya Techno Products Private Limited
8.00 | Supply and installation of G.I. flat for earthing of distribution panels & poles. Scope also include Flat to be laid in ground 300 mm deep, full welding at joints by Lap /Tee/Cross type joints, Joint to be painted with 2 coats of red oxide primer and two coat of aluminium paint, Flat to be clamped on wall wherever required, @ 500mm interval with the help of GI clamps as approved by EIC and connected at both ends by using nut bolt and spring and plain washer.
8.10 | 25 x 3 mm G.I. flat. | 4000.00 | M | 7.00 | 55.00 | 220000.00 | 99.00 | 396000.00 | 90.00 | 360000.00 | 220000.00 | Aditya Techno Products Private Limited
8.20 | 50 x 6 mm G.I. flat. | 500.00 | M |  | 130.00 | 65000.00 | 309.00 | 154500.00 | 300.00 | 150000.00 | 65000.00 | Aditya Techno Products Private Limited
9.00 | Supply and installation of pipe earthing station. Scope of this work covers excavation of earth pit, removal of surplus material, installation pipe earthing station with 40 mm dia medium gauge G.I. pipe and back filling with salt, charcoal and black soil as directed and job also include measurement of earth resistance of each pit.
9.10 | Excavation of earth pit / pole pit 1.0 x1.0 x 1.7 to 2.0 M deep size. Blasting shall not be permitted. | 225.00 | CuM |  | 520.00 | 117000.00 | 899.00 | 202275.00 | 1500.00 | 337500.00 | 117000.00 | Aditya Techno Products Private Limited
9.20 | Supplying good quality black soil, filling in earth pit, watering & ramming as directed. | 200.00 | CuM |  | 1450.00 | 290000.00 | 699.00 | 139800.00 | 800.00 | 160000.00 | 139800.00 | JAGGI ELECTRICALS
9.30 | Supplying char-coal and filling in earth pit as directed. | 5000.00 | Kg |  | 10.00 | 50000.00 | 19.00 | 95000.00 | 16.00 | 80000.00 | 50000.00 | Aditya Techno Products Private Limited
9.40 | Supplying good quality ungrinded salt and filling in earth pit as directed. | 7500.00 | Kg |  | 8.00 | 60000.00 | 9.00 | 67500.00 | 11.00 | 82500.00 | 60000.00 | Aditya Techno Products Private Limited
9.50 | Construction of Brick masonry (A-Class bricks) chamber 350 x 350 x 600mm (Inside clear) of wall thickness 230mm in cement mortar 1 : 4 with removable RCC precast slab of thickness not less than 75mm and plastering smooth 15 mm thick inside and outsider sides of chamber etc. complete in all respect as per EIC. | 100.00 | Nos. |  | 550.00 | 55000.00 | 1199.00 | 119900.00 | 2000.00 | 200000.00 | 55000.00 | Aditya Techno Products Private Limited
9.60 | Supply and placing of 40 mm dia medium gauge G.I. Pipe 2.0 metre long with 1 no. G.I. reducer 50mm to 40mm & perforation at maximum distance of 150 mm throughout the length (other detail as per technical specification of as per instruction of EIC). | 100.00 | Nos. |  | 1000.00 | 100000.00 | 749.00 | 74900.00 | 1000.00 | 100000.00 | 74900.00 | JAGGI ELECTRICALS
10.00 | Making of Copping around the street light/ post top pole shall be made the size of 400mm dia and 450mm high above the ground level. Cement Concrete of 1:3:6 (1 Cement: 3 Coarse sand: 6 graded stone aggregate 20 mm nominal size) and finishing with plaster to be done on the copping surface & curing. | 50.00 | Nos. |  | 650.00 | 32500.00 | 399.00 | 19950.00 | 600.00 | 30000.00 | 19950.00 | JAGGI ELECTRICALS
11.00 | Supply & installation of non-pressure NP2 class (light duty) 150 mm dia R.C. Hume pipe of 2-meter length having collar. | 400.00 | M |  | 500.00 | 200000.00 | 429.00 | 171600.00 | 450.00 | 180000.00 | 171600.00 | JAGGI ELECTRICALS
12.00 | Supply & installation of Junction Boxes for Street light poles. The JBs shall be fabricated from 1.6 mm thick MS sheet in the size of 275 x 275 x 150 mm deep in full welded construction. Note: For more details refer technical specification (section-V of tender) | 50.00 | Nos. |  | 2200.00 | 110000.00 | 1399.00 | 69950.00 | 2500.00 | 125000.00 | 69950.00 | JAGGI ELECTRICALS
13.00 | Supply & installation of following block distribution panel.
13.10 | Supply & installation of double door SPN DB (Single phase distribution), 4 Module, IP 43 with 2 Nos. 6 Amp. Single pole MCB C curve 10KA breaking capacity. Make: Schneider/ Legrand/L&T/ Crompton Greaves. | 81.00 | Nos. |  | 1500.00 | 121500.00 | 2899.00 | 234819.00 | 1800.00 | 145800.00 | 121500.00 | Aditya Techno Products Private Limited
13.20 | Supply & installation of double door TPN DB (Three phase distribution) 8+12 Module, IP 43 with cable end box, 1 Nos. 63 Amp. four pole 415V, 4 module MCB and 6 nos. single pole + Neutral 240V, (2 Module) MCB C curve 10KA breaking capacity. The scope also includes removal of exiting block distribution board and cables deposit in sectional store. Make: Schneider/ Legrand/L&T/ Crompton Greaves. | 81.00 | Nos. |  | 7200.00 | 583200.00 | 13999.00 | 1133919.00 | 8200.00 | 664200.00 | 583200.00 | Aditya Techno Products Private Limited
14.00 | Supply & Installation of B class G.I. Pipe with accessories like bend and socket and required bending 120-degree long radius bends where ever required & clamping. Make PRAKASH SURYA / JINDAL. The pipe shall be of following size.
14.10 | 32mm | 200.00 | M |  | 320.00 | 64000.00 | 359.00 | 71800.00 | 375.00 | 75000.00 | 64000.00 | Aditya Techno Products Private Limited
14.20 | 50mm | 200.00 | M |  | 520.00 | 104000.00 | 449.00 | 89800.00 | 560.00 | 112000.00 | 89800.00 | JAGGI ELECTRICALS
15.00 | Providing and laying 80mm thick factory made cement concrete interlocking pavers block of M-30 grade made by block making machine with strong vibratory compaction and of approved size and design / shape laid in required colour (Yellow, Red and other as directed) and pattern over and including 50mm thick compacted bed of course sand, filling the joints with coarse sand etc. all complete as per the direction of Engineer-in-charge. | 200.00 | SqM |  | 700.00 | 140000.00 | 899.00 | 179800.00 | 800.00 | 160000.00 | 140000.00 | Aditya Techno Products Private Limited
16.00 | Providing and laying cement concrete of 1:3:6 ( 1 Cement :3 Coarse sand : 6 graded stone aggregate 20 mm nominal size) in pole pit, columns, coping, etc. at all level including transporting of concrete to site of laying, shuttering, cost of finishing, curing etc. Complete as per direction of Engineer-in-charge. | 30.00 | CuM |  | 2550.00 | 76500.00 | 6099.00 | 182970.00 | 7000.00 | 210000.00 | 76500.00 | Aditya Techno Products Private Limited
17.00 | Dismantling bituminous road for all thickness by mechanical means i.e. cutter including stacking of serviceable material and disposal of unserviceable material within 1000 metres lead as per direction of engineer-in-charge. The manual cutting of road at anywhere is not allowed. | 100.00 | Sqm |  | 900.00 | 90000.00 | 899.00 | 89900.00 | 500.00 | 50000.00 | 50000.00 | Vijayvargia Electricals
| Total in Figures |  |  |  |  | 17661768.00 |  | 20745389.00 |  | 20609500.00
Lowest Amount Quoted BY: Aditya Techno Products Private Limited(17661768.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply, installation, testing and commissioning of main Distribution electrical system of Type-II, Type-III, Type-IV and H2B quarters in Anukiran and Anuchhaya colonies including other miscellaneous work at RR site colonies. Tender ID: 2024_NPCIL_208271_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Aditya Techno Products Private Limited (BID ID -752706) | 17661768.00 | L1
| 2 | Vijayvargia Electricals (BID ID -752984) | 20609500.00 | L2
| 3 | JAGGI ELECTRICALS (BID ID -752978) | 20745389.00 | L3