## BoQ1
Government eProcurement System Created By: K G Krishnakumar Created Date/Time: 03-Jan-2025 05:23 PM Tender Title: Welding, Fabrication and Erection of Large diameter liquid Tender ID: 2024_NPCIL_212914_1
Tender Inviting Authority : Senior Maintenance Engineer(MMU), KGS 1&2
Name of Work: “Welding, Fabrication & Erection of Large diameter liquid waste storage tanks required for Waste Management Plant (WMP) in KGS #1&2 etc” on contract basis.
Contract No: NPCIL/KGS/CTC/MMU-1&2/2024/CPPP/006
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | OM SHAKTHI ENGINEERING (GSTN-NA) BID ID -768795 |  | S.M.ERECTORS (GSTN-NA) BID ID -769425
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Manufacture, assembly, inspection, testing, painting, packing & forwarding, supply transportation, delivery, erection,welding, commissioning, including Pipe & Pipe fittings and guarantee of Large diameter liquid waste storage tanks required for Waste Management Plant (WMP) tanks are to be erected at the Dyke area of WMP. The option of fabricating partially at shop and completing at site or fabricating fully at site as per IS : 803 : Code of practice for design, fabrication and erection of vertical mild steel cylindrical welded oil storage tanks, material as per IS 2062 Gr. E250 BR : Hot rolled low, medium and high tensile structural steel, ASTM A-106 : Seamless Carbon Steel Pipes for High Temperature services, IS : 1239 : Mild steel tubes, tubulars and other wrought steel fittings, ASTM A-105 : Specification for Carbon steel forgings, for piping components,ASTM A-234 : Specification for piping fittings of wrought carbon steel and alloy steel for moderate and elevated temperatures, welder qualification as applicable ASME Section IX : ASME Boiler and Pressure Vessel Code, Welding and Brazing Qualification, Testing requirements ASME Section V : ASME Boiler and Pressure Vessel Code, Non-destructive Examination shall be performed by ASNT/ISNT Level-II qualified personal : Liquid Penetrant Examination, Spot radiography – 10% in addition to all “T” joints, Hydro testing, Vaccum box testing for tank bottom plate. Painting All surfaces both inside and outside including spiral stairway, supporting structure, nozzles, vents etc. of all tanks shall be shot-blasted in accordance with IS:1477 Part – I, All inside surfaces shall have one coat of epoxy equivalent to Epilux 4 Z/R Primer (min DFT 50 micron per coat) followed by one coat of intermediate coat equivalent of Epilux 4 HB MIO (min DFT 75 micron ) and two coats equivalent of Epilux-5 coal tar epoxy (min DFT 80 micron per coat). All outer surfaces shall have one coat of Zinc Anode 304 NPC coating (min DFT 75 micron ) followed by one coat of intermediate coat equivalent of Epilux 4 HB MIO (min DFT 75 micron ) and two finish coats of PU (Glossy & min DFT 50 microns per coat) of grey colour. Bottom of bottom plate shall have one coat of epoxy equivalent to Epilux 4 Z/R Primer (min DFT 50 micron per coat) followed by one coat of intermediate coat equivalent of Epilux 4 HB MIO (min DFT 75 micron ) and two coats equivalent of Epilux-5 coal tar epoxy (min DFT 80 micron per coat). Refer drawing no: KGS-1&2/FCN/79220/S/2023/690/0,KAIGA 1,2/79224/8207/TD,KAIGA1&2/29530/8057/DD,KAIGA 1&2/29520/8022/DD, DATA SHEET NO. : FCN-690 KGS/79224/2018/DS,SPECIFICATION NO. : PC-E-676, | 1.00 | NO | 8850092.00 | 9252000.00 | 9252000.00 | 8755655.00 | 8755655.00 | 8755655.00 | S.M.ERECTORS
2.00 | Supply of Stainless Steel Pipe, Seamless, 25NB, Schedule-40,ANSI B 36.19, ASTM A-312 TP-304L including testing requirements as specified in technical specification, Material should be gone through IGC test with ASTM A262 “Practice-A”/ “Practice-E” shall be applicable on one sample per heat-treatment /batch/Lot.Mechanical and Chemical properties as per SA-312, TP 304L per batch/Lot etc, Pipe length shall be 5.5 to 6 metre (more than 6 metre length shall also be acceptable/as specified by Engineer-In-Charge) etc, | 160.00 | Meter | 2144.00 | 2160.00 | 345600.00 | 1755.00 | 280800.00 | 280800.00 | S.M.ERECTORS
3.00 | Supply of Stainless Steel Elbow, 25NB, Socket Weld, 3000 Lbs, ANSI B 16.11, ASTM A-182 TP-304L including testing requirements as specified in technical specification, Material should be gone through IGC test with ASTM A262 “Practice-A”/ “Practice-E” shall be applicable on one sample per heat-treatment /batch/Lot.Mechanical and Chemical properties as per SA-182, TP 304L per batch/Lot etc/as specified by Engineer-In-Charge etc. | 50.00 | Nos | 646.00 | 726.00 | 36300.00 | 688.00 | 34400.00 | 34400.00 | S.M.ERECTORS
4.00 | Supply of Stainless Steel Equal Tee, 25NB, Socket Weld, 3000 Lbs, ANSI B 16.11, ASTM A-182 TP-304L including testing requirements as specified in technical specification, Material should be gone through IGC test with ASTM A262 “Practice-A”/ “Practice-E” shall be applicable on one sample per heat-treatment /batch/Lot.Mechanical and Chemical properties as per SA-182, TP 304L per batch/Lot etc/as specified by Engineer-In-Charge etc. | 20.00 | Nos | 890.00 | 951.00 | 19020.00 | 908.00 | 18160.00 | 18160.00 | S.M.ERECTORS
| Total in Figures |  |  |  |  | 9652920.00 |  | 9089015.00
Lowest Amount Quoted BY: S.M.ERECTORS(9089015.00)

## BOQ Summary
BOQ Summary Details Tender Title: Welding, Fabrication and Erection of Large diameter liquid Tender ID: 2024_NPCIL_212914_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | S.M.ERECTORS (BID ID -769425) | 9089015.00 | L1
| 2 | OM SHAKTHI ENGINEERING (BID ID -768795) | 9652920.00 | L2