## BoQ1
Government eProcurement System Created By: RAKESH SHRIVASTAV Created Date/Time: 28-Mar-2025 11:57 AM Tender Title: Providing, installation, testing and commissioning of firefighting system (Down Comer) for NPCIL Guest House (Rajhans) and other work Tender ID: 2024_NPCIL_217417_1
Tender Inviting Authority: NUCLEAR POWER CORPORATION OF INDIA LIMITED
Name of Work: (1) Providing, installation, testing and commissioning of firefighting system (Down Comer) for NPCIL Guest House (Rajhans) and providing , installation, testing and commissioning of fire fighting pipes behind C,D,E and F blocks of NUB, Anushaktinagar, Mumbai-400094. (2) Dismantling of existing Kitchen Air Ventilation System of Gr. Floor, 1st floor kitchen of NUB and Gr. Floor kitchen of NPCIL Guest House (Mayur and Rajhans) and design, fabrication, supply, erection, testing and commissioning of Kitchen Air Ventilation System of NUB Kitchen (Gr. Floor and 1st floor) and Gr. Floor NPCIL Guest House Kitchen (Mayur) at Anushaktinagar, Mumbai-400094. (3) Providing and painting of fire fighting pipes and its supports, Air-Conditioners and its supports, safety grills, ducts supports, elevator traction motors and its supports etc. in NUB, VSB and NPCIL Guest House (Mayur and Rajhans) at Anushaktinagar, Mumbai-400094, NPCIL offices at T.V. Stores, Trombay, Mumbai-400088 and 16th Floor, WTC at Cuffe Parade, Mumbai-400005.
Tender No: NPCIL/HQ/CMM-WG/91/2024/PT/181
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AIRTEK HVAC LLP (GSTN-27ABCFA1858K1ZB) BID ID -793232 |  | WINTECH DEVELOPERS PRIVATE LIMITED (GSTN-NA) BID ID -795292
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Schedule-1 Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of Synthetic enamel paint of required shade complete as required :
1.10 | 80 mm dia. | 100.00 | Rmt | 1.25 | 2000.00 | 200000.00 | 2200.00 | 220000.00 | 200000.00 | AIRTEK HVAC LLP
1.20 | 100 mm dia. | 300.00 | Rmt | 0.00 | 2850.00 | 855000.00 | 2400.00 | 720000.00 | 720000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
1.30 | 150 mm dia. | 10.00 | Rmt | 100.00 | 4000.00 | 40000.00 | 2700.00 | 27000.00 | 27000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
2.00 | Schedule-1 Providing laying, testing & commissioning of 100mm dia 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. | 65.00 | Rmt | 53.00 | 3600.00 | 234000.00 | 2200.00 | 143000.00 | 143000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
3.00 | Schedule-1 Providing laying, testing & commissioning of 150mm dia 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. | 640.00 | Rmt | 10.00 | 4100.00 | 2624000.00 | 4500.00 | 2880000.00 | 2624000.00 | AIRTEK HVAC LLP
4.00 | Schedule-1 Providing, installation, testing and commissioning of stainless steel Y- strainer of 150mm dia. size fabricated out of 1.6mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange. | 2.00 | No | 11.00 | 11000.00 | 22000.00 | 200000.00 | 400000.00 | 22000.00 | AIRTEK HVAC LLP
5.00 | Schedule-1 Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required.
5.10 | 100mm dia | 7.00 | No. | 10.00 | 13500.00 | 94500.00 | 10000.00 | 70000.00 | 70000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
5.20 | 150mm dia | 2.00 | No. | 22.00 | 21000.00 | 42000.00 | 14000.00 | 28000.00 | 28000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
6.00 | Schedule-1 (a)Supplying, installation, testing and commissioning of electric driven terrace pump having 900lpm at 35 meter head, suitable for automatic operation and consisting of following, complete in all respects, as required: (Terrace Pump) (b) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical confirming to IS:1520 (c) Suitable HP squirrel cage induction motor TEFC type suitable for operation on 415 volts, 3 phase, 50 Hz, AC supply with IP55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (d) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (e) Suitable cement concrete foundation duly plastered and with anti vibration pads. | 2.00 | Set | 0.00 | 130000.00 | 260000.00 | 250000.00 | 500000.00 | 260000.00 | AIRTEK HVAC LLP
7.00 | Schedule-1 Providing, installation, testing and commissioning of cubicle type self standing type booster pump panel for two nos. of booster pump to be mounted at ground floor or terrace including all internal wiring, earthing etc. complete. | 1.00 | Set | 1.00 | 142000.00 | 142000.00 | 40000.00 | 40000.00 | 40000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
8.00 | Schedule-1 Providing installation, testing and commissioning of non-return valve of 100mm dia. sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required. | 2.00 | No. | 1.00 | 10000.00 | 20000.00 | 65000.00 | 130000.00 | 20000.00 | AIRTEK HVAC LLP
9.00 | Schedule-1 Providing and fixing in position the industrial type pressure gauges with gun metal/brass valves complete as required. | 2.00 | Set | 1.00 | 1700.00 | 3400.00 | 2000.00 | 4000.00 | 3400.00 | AIRTEK HVAC LLP
10.00 | Schedule-1 Supplying and fixing orifice plate made out of 6mm thick stainless steel (Grade 304) with orifice of required size to be fitted between flange & landing valve of external and internal hydrants to reduce pressure at the outlet to the level of 3.5 kg/cm2 complete as required. | 11.00 | Set | 1.00 | 1600.00 | 17600.00 | 15000.00 | 165000.00 | 17600.00 | AIRTEK HVAC LLP
11.00 | Schedule-1 Providing & fixing of pressure switch in M.S. pipe line including connection etc. as required. | 2.00 | Set | 1.00 | 2000.00 | 4000.00 | 2500.00 | 5000.00 | 4000.00 | AIRTEK HVAC LLP
12.00 | Schedule-1 Providing, installation, testing and commissioning weather proof standard internal fire hose cabinet suitable for accommodating 63 mm dia. X 15 mtr. Long Hoses - 2 nos. and branch pipe - 1 no. The hose cabinet shall be fabricated from 2 mm thick CRCA sheet, with locking arrangement, double glass doors, locking arrangement including fixing the same to walls, small hammer for breaking the glass etc. all complete with two coats of synthetic enamel post office red paint over two coats of primer of approved make. The words "Hose Cabinet" shall be written in paint/sticker pasted on the glass doors. | 7.00 | No. | 1.00 | 7300.00 | 51100.00 | 20000.00 | 140000.00 | 51100.00 | AIRTEK HVAC LLP
13.00 | Schedule-1 Providing, installation, testing and commissioning weather proof standard fire hose cabinet outdoor type suitable for accommodating 63 mm dia. X 15 mtr. Long Hoses - 2 nos. and branch pipe - 1 no. The hose cabinet shall be fabricated from 2 mm thick CRCA sheet with double glass doors, locking arrangement, small hammer for breaking the key glass etc. with two coats of post office synthetic enamel red paint over two coats of primer of approved makes, hose cabinet shall be fixed on MS angle of size 65 mm x 65 mm and thickness 6 mm, angle painted with two coats of synthetic enamel black paint over two coats of primer of approved makes including excavation, grouting, shifting excess soil etc. all complete as required. The words "Fire Hose Cabinet" shall be written in paint/sticker pasted on the glass doors. | 4.00 | No. | 1.00 | 7500.00 | 30000.00 | 10000.00 | 40000.00 | 30000.00 | AIRTEK HVAC LLP
14.00 | Schedule-1 Supplying and fixing 63 mm dia., 15 m long RRL hose pipe with 63 mm dia. male and female couplings of Stainless Steel (Grade 304) duly bound with GI wire, rivets etc. confirming to IS 636 (type-A) as required. | 22.00 | Each | 1.00 | 5500.00 | 121000.00 | 10000.00 | 220000.00 | 121000.00 | AIRTEK HVAC LLP
15.00 | Schedule-1 Supplying and fixing 63 mm dia. Stainless Steel (Grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required. | 11.00 | Each | 1.00 | 2200.00 | 24200.00 | 4000.00 | 44000.00 | 24200.00 | AIRTEK HVAC LLP
16.00 | Schedule-1 Supplying and fixing Single headed external yard hydrant valve of Stainless steel with 1 No. 63mm dia. instantaneous FM Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Stainless Steel cap and chain as required. | 11.00 | Set | 1.00 | 6500.00 | 71500.00 | 8000.00 | 88000.00 | 71500.00 | AIRTEK HVAC LLP
17.00 | Schedule-1 Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. (a)20mm nominal internal dia. water hose thermoplastic (Textile reinforced) type-2 as per IS : 12585 of 30 m length. (b) 20 mm nominal internal dia. gun metal globe valve & nozzle. (c) Drum and brackets for fixing the equipments on wall. (d) Connections from riser with 25 mm dia. stop gun metal valve & M.S. pipe and socket. | 7.00 | Each | 1.00 | 9000.00 | 63000.00 | 25000.00 | 175000.00 | 63000.00 | AIRTEK HVAC LLP
18.00 | Schedule-1 Supplying and fixing of 2 way-100 mm dia. M.S. Pipe fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as required for suitable dia. MS pipe connection conforming to IS 904 as required. | 2.00 | Set | 1.00 | 7500.00 | 15000.00 | 9000.00 | 18000.00 | 15000.00 | AIRTEK HVAC LLP
19.00 | Schedule-1 Providing and making drainage provision for the down comer with 25 mm dia. GI heavy pipe, 25 mm dia. ball valve, fittings etc. as required. Maximum length of pipe shall be 0.8 mtr. | 1.00 | Set | 1.00 | 3500.00 | 3500.00 | 1500.00 | 1500.00 | 1500.00 | WINTECH DEVELOPERS PRIVATE LIMITED
20.00 | Schedule-1 Providing, installation, testing and commissioning of Air-release valve (gate valve) of 25 mm dia. including 25mm dia. G.I. pipe of approx. 1 ft length to be fitted at both ends of gate valve, this valve to be installed at terrace. | 2.00 | Set | 1.00 | 4500.00 | 9000.00 | 2000.00 | 4000.00 | 4000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
21.00 | Schedule-2 Dismantling of existing kitchen ventilation system of Ground Floor & 1st floor kitchen of Nabhikiya Urja Bhavan and Ground Floor kitchen of NPCIL Guest House (Mayur and Rajhans) at Anushaktinagar, Mumbai-400094. The job includes dismantling of centrifugal blowers, tube axial fans, its M.S. support and concrete foundation, supply and exhaust ducts and its supports, SS hoods, grills etc. complete and depositing these to T.V. Stores at Trombay, Mumbai-400088. | 1.00 | Lot | 1.00 | 100000.00 | 100000.00 | 36000.00 | 36000.00 | 36000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
22.00 | Schedule-2 Providing, installation, testing and commissioning of Centrifugal Blower for exhaust system of Ground Floor kitchen of Nabhikiya Urja Bhavan, capacity – 7500 CFM, Pressure – 2” WG, Drive – Direct, Motor, 7.5HP/1440 RPM -3 phase suitable for oil extraction with Anti-vibration Pad, fixing Bolt, Mounting Frame, concrete foundation, Motor Guard cover, DOL Starter, etc. complete for satisfactory operation of the Kitchen Air Ventilation system. | 1.00 | No. | 1.00 | 220000.00 | 220000.00 | 200000.00 | 200000.00 | 200000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
23.00 | Schedule-2 Providing, installation, testing and commissioning of Centrifugal Blower for exhaust system of 1st floor kitchen of Nabhikiya Urja Bhavan and Ground Floor Kitchen of NPCIL Guest House (Mayur), capacity – 6500 CFM, Pressure – 2” WG, Drive – Direct, Motor, 5HP/1440 RPM -3 phase suitable for oil extraction with Anti-vibration Pad, fixing Bolt, Mounting Frame, concrete foundation, Motor Guard cover, DOL Starter, etc. complete for satisfactory operation of the Kitchen Air Ventilation system. | 2.00 | No. | 1.00 | 210000.00 | 420000.00 | 175000.00 | 350000.00 | 350000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
24.00 | Schedule-2 Providing, installation, testing and commissioning of Tube Axial Fan for fresh air supply system of Gr. floor kitchen of Nabhikiya Urja Bhavan, capacity – 6000 CFM, Drive – Direct, Motor – 5HP/1440rpm, 3 phase with anti vibration pad, fixing bolt, mounting frame, concrete foundation. Motor Guard cover, DOL Starter, etc., including providing 4 Nos. fresh air HDP filter of size 2ft x 2ft – 3 layer, washable type, down to 10 micron , with filter housing of size 2.5 ft x 2.5 ft x 2.5 ft made out of 16 G. G.I. sheet suitable for 4 nos. HDP filter. | 1.00 | No. | 1.00 | 215000.00 | 215000.00 | 200000.00 | 200000.00 | 200000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
25.00 | Schedule-2 Providing, installation, testing and commissioning of Tube Axial Fan for fresh air supply system of 1st floor kitchen of Nabhikiya Urja Bhavan and Gr. Floor Kitchen of NPCIL Guest House (Mayur),Capacity – 5500 CFM, Drive – Direct, Motor – 4 HP / 1440 rpm, 3 phase with anti vibration pad, fixing bolt, mounting frame, concrete foundation. Motor Guard cover, DOL Starter, etc., including providing 4 Nos. fresh air HDP filter of size 2ft x 2ft – 3 layer, washable type, down to 10 micron , with filter housing of size 2.5 ft x 2.5 ft x 2.5 ft made out of 16 G. G.I. sheet suitable for 4 nos. HDP filter. | 2.00 | No. | 1.00 | 215000.00 | 430000.00 | 175000.00 | 350000.00 | 350000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
26.00 | Schedule-2 Providing and installation of SS 18 Gauge SS304 Hood Mat finish with SS 304 grease filter made out of 20 G as follows for Kitchen Ventilation System of Nabhikiya Urja Bhavan and NPCIL Guest House (Mayur) at Anushaktinagar, Mumbai-400094.
26.10 | Size : 9ft x 2ft | 3.00 | No. | 1.00 | 65000.00 | 195000.00 | 12000.00 | 36000.00 | 36000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
26.20 | Size : 7ft x 3ft | 1.00 | No. | 1.00 | 60000.00 | 60000.00 | 10000.00 | 10000.00 | 10000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
26.30 | Size : 7ft x 2ft | 2.00 | No. | 1.00 | 60000.00 | 120000.00 | 10000.00 | 20000.00 | 20000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
26.40 | Size : 5ft x 2.5ft | 3.00 | No. | 1.00 | 55000.00 | 165000.00 | 9000.00 | 27000.00 | 27000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
27.00 | Schedule-2 Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular ducting of 0.8 mm sheet as per IS 655-2006 complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. complete as required. | 425.00 | per sqm | 1.00 | 1500.00 | 637500.00 | 2050.00 | 871250.00 | 637500.00 | AIRTEK HVAC LLP
28.00 | Schedule-2 Providing and installation of canvass connection between fresh air filter & fresh air duct and between centrifugal blower & exhaust air duct suitable for duct size. | 6.00 | No. | 1.00 | 3500.00 | 21000.00 | 7000.00 | 42000.00 | 21000.00 | AIRTEK HVAC LLP
29.00 | Schedule-2 Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc. as per specifications. | 2.00 | per sqm | 1.00 | 8000.00 | 16000.00 | 13000.00 | 26000.00 | 16000.00 | AIRTEK HVAC LLP
30.00 | Schedule-2 Supplying and fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications. | 7.00 | per sqm | 1.00 | 9000.00 | 63000.00 | 5000.00 | 35000.00 | 35000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
31.00 | Schedule-3 Painting Steel work with Deluxe Multi Surface Paint to give an even shade. Two or more coat applied @0.9 ltr/10 sqm over an under coat of primer applied @0.8 ltr/10 sqm of approved brand and manufacture. | 500.00 | sqm | 1.00 | 230.00 | 115000.00 | 100.00 | 50000.00 | 50000.00 | WINTECH DEVELOPERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 7724300.00 |  | 8315750.00
Lowest Amount Quoted BY: AIRTEK HVAC LLP(7724300.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing, installation, testing and commissioning of firefighting system (Down Comer) for NPCIL Guest House (Rajhans) and other work Tender ID: 2024_NPCIL_217417_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | AIRTEK HVAC LLP (BID ID -793232) | 7724300.00 | L1
| 2 | WINTECH DEVELOPERS PRIVATE LIMITED (BID ID -795292) | 8315750.00 | L2