## BoQ1
Government eProcurement System Created By: ANJANEE KUMARI Created Date/Time: 24-Jan-2025 05:06 PM Tender Title: Provision of internal and external Firefighting system at Solapur Airport. SH Construction of underground water tank, pump room, fire hydrants and other associated civil and electrical works at Solapur Airport. Tender ID: 2025_AAI_223178_1
Tender Inviting Authority: Asst. General Manager (Engg - Civil), Airports Authority of India, Solapur Airport, Solapur - 413224
Name of Work: Provision of internal and external Firefighting system at Solapur Airport. SH:- Construction of underground water tank, pumproom, fire hydrants and other associated civil and electrical works at Solapur Airport.
Contract No: AAI/SOLAPUR/ENGG-CIVIL/Fire Fighting/2024-25 (Tender ID: 2025_AAI_223178_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | OLO HOUSING INFRA LLP (GSTN-NA) BID ID -806315 |  | Yogesh builders (GSTN-NA) BID ID -808975
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SCHEDULE OF QUANTITY (CIVIL)
1.01 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-incharge. All kinds of soil | 1370.00 | Cum |  | 380.00 | 520600.00 | 90.00 | 123300.00 | 123300.00 | Yogesh builders
1.02 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-incharge. a) Ordinary rock | 1370.00 | Cum |  | 480.00 | 657600.00 | 110.00 | 150700.00 | 150700.00 | Yogesh builders
1.03 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) | 139.70 | Cum |  | 4800.00 | 670560.00 | 2500.00 | 349250.00 | 349250.00 | Yogesh builders
1.04 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 20.00 | Cum |  | 200.00 | 4000.00 | 200.00 | 4000.00 | 4000.00 | OLO HOUSING INFRA LLP, Yogesh builders
1.05 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:6 (1 cement : 6 coarse sand) | 32.35 | Cum |  | 5100.00 | 164985.00 | 5500.00 | 177925.00 | 164985.00 | OLO HOUSING INFRA LLP
1.06 | Brick work with common burnt clay FPS (non modular) bricks of class designation 3.5 I superstructure abvoe plinth level upto floor V level I all shapes and size in : Cement Mortar 1:6 (1 Cement : 6 Coarse Sand) | 29.40 | Cum |  | 5100.00 | 149940.00 | 5500.00 | 161700.00 | 149940.00 | OLO HOUSING INFRA LLP
1.07 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete. | 63.00 | Sqm |  | 1420.00 | 89460.00 | 800.00 | 50400.00 | 50400.00 | Yogesh builders
1.08 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 500.00 | Kg |  | 88.00 | 44000.00 | 82.00 | 41000.00 | 41000.00 | Yogesh builders
1.09 | Centering and shuttering including strutting, propping etc. and removal of form for Lintels, beams, plinth beams, girders, bressumers and cantilevers | 50.00 | Sqm |  | 520.00 | 26000.00 | 600.00 | 30000.00 | 26000.00 | OLO HOUSING INFRA LLP
1.10 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 10.00 | Cum |  | 5200.00 | 52000.00 | 6000.00 | 60000.00 | 52000.00 | OLO HOUSING INFRA LLP
1.11 | Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. | 21.00 | Sqm |  | 1200.00 | 25200.00 | 625.00 | 13125.00 | 13125.00 | Yogesh builders
1.12 | 12mm Cement Plaster of mix: 1 : 6 (1 Cement : 6 Coarse Sand) | 110.00 | Sqm |  | 240.00 | 26400.00 | 300.00 | 33000.00 | 26400.00 | OLO HOUSING INFRA LLP
1.13 | 18mm cement plaster in two coats under 12mm thick cement plaster 1:5 (1 Cement : 5 coarse sand) finished with a top layer 6mm thick cement plaster 1:6 (1 Cement : 6 Fine sand) | 110.00 | Sqm |  | 350.00 | 38500.00 | 400.00 | 44000.00 | 38500.00 | OLO HOUSING INFRA LLP
1.14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work 50 mm nominal dia Pipes | 200.00 | Meter |  | 761.00 | 152200.00 | 390.00 | 78000.00 | 78000.00 | Yogesh builders
1.15 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work 65 mm nominal dia Pipes | 200.00 | Meter |  | 1438.00 | 287600.00 | 775.00 | 155000.00 | 155000.00 | Yogesh builders
1.16 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work 100 mm nominal dia Pipes | 200.00 | Meter |  | 2047.00 | 409400.00 | 950.00 | 190000.00 | 190000.00 | Yogesh builders
1.17 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, to achieve even shade and colour. New work (two or more coat) over and including waer thinable priming coat with cement primer having VOC content less than 50 gram/ litre. | 188.00 | Sqm |  | 110.00 | 20680.00 | 80.00 | 15040.00 | 15040.00 | Yogesh builders
1.18 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 120.00 | Sqm |  | 190.00 | 22800.00 | 120.00 | 14400.00 | 14400.00 | Yogesh builders
1.19 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture | 50.00 | Sqm |  | 180.00 | 9000.00 | 150.00 | 7500.00 | 7500.00 | Yogesh builders
1.20 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level: 1:2:4 (1 Cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 40 mm nominal size derived from natural sources) | 100.00 | Cum |  | 5300.00 | 530000.00 | 5000.00 | 500000.00 | 500000.00 | Yogesh builders
1.21 | Providing and fixing pressed steel door frames conforming to IS: 4351, manufactured from commercial mild steel sheet of 1.60 mm thickness, including hinges, jamb, lock jamb, bead and if required angle threshold of mild steel angle of section 50x25 mm, or base ties of 1.60 mm, pressed mild steel welded or rigidly fixed together by mechanical means, including M.S. pressed butt hinges 2.5 mm thick with mortar guards, lock strike-plate and shock absorbers as specified and applying a coat of approved steel primer after pre-treatment of the surface as directed by Engineer-in-charge: Profile C Fixing with adjustable lugs with split end tail to each jamb | 30.00 | Meter |  | 228.00 | 6840.00 | 400.00 | 12000.00 | 6840.00 | OLO HOUSING INFRA LLP
1.22 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment). Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | 400.00 | Kg |  | 78.00 | 31200.00 | 160.00 | 64000.00 | 31200.00 | OLO HOUSING INFRA LLP
1.23 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished welded type tubes | 540.00 | Kg |  | 246.00 | 132840.00 | 110.00 | 59400.00 | 59400.00 | Yogesh builders
1.24 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50 mm (+ 0.05 %) total coated thickness with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineerin-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | 120.00 | Sqm |  | 580.00 | 69600.00 | 700.00 | 84000.00 | 69600.00 | OLO HOUSING INFRA LLP
1.25 | Supplying and filling in plinth with sand under floors, Underground Tank including watering, ramming, consolidating and dressing complete. | 846.30 | Cum |  | 1950.00 | 1650285.00 | 410.00 | 346983.00 | 346983.00 | Yogesh builders
1.26 | Supply, installation and commissioning of a 50,000-liter capacity Fiberglass Reinforced Plastic (FRP) underground water storage tank of approved make and size should be 12.80 meter in length and 2.40 meter in diameter. The tank should be Rustproof and leak-proof, Hygienic and suitable for potable water, Lightweight and easy to install, Durable and economical and should be made of 100% virgin material, Impermeable to roots of trees, etc. Specifications and materials include following components: 1. FRP Tank: A FRP tank of approved make with a capacity of 50,000 liters. 2. Concrete Base: Precast beam base for the tank for holding in a position. 3. Securing Elements: Tie belts and anchor fasteners to secure the tank in place. 4. Installation: Lowering the tank in a pit, installing on the foundation, and securing with tie belts and anchor fasteners. 5. The cost of excavation, backfilling, PCC, brickwork, sand filling will be paid extra in a relevant item. The rate is inclusive of transportation, loading, unloading, lowering and fixing in position etc complete as per direction and satisfaction of Engineer In-Charge. | 2.00 | Each |  | 958750.00 | 1917500.00 | 1500000.00 | 3000000.00 | 1917500.00 | OLO HOUSING INFRA LLP
2.00 | SCHEDULE OF QUANTITY (ELECTRICAL)
2.01 | Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable for automatic operation and consisting of following, complete in all respects, as required : (a) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (b) Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered with anti vibration pads Note: *The head of the pump is selected in a manner so as to give a minimum 3.5kgf/cm2 pressure at the highest/farthest point. 2280 lpm at 80 m Head | 1.00 | Set | 10.00 | 502272.00 | 502272.00 | 250000.00 | 250000.00 | 250000.00 | Yogesh builders
2.02 | Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following, complete in all respects, as per specifications : Horizontal type (Diesel Driven Pump), multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 /24 volts electric starting equipment, diesel tank as per OEM standard with suitable M.S. stand, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour including battery, battery stand, AVM pads etc. as required. M.S fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. Note: *The head of the pump is selected in a manner so as to give a minimum 3.5kgf/cm2 pressure at the highest / farthest point. 2280 lpm at 80 m Head | 1.00 | Set |  | 675796.00 | 675796.00 | 500000.00 | 500000.00 | 500000.00 | Yogesh builders
2.03 | Supplying, installation, testing and commissioning of electric driven pressurisation pump suitable for automatic operation and consisting of following, complete in all respects, as required : (Jockey Pump) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS : 1520. Suitable HP squirrel cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 180 lpm at 80 m Head | 1.00 | Set |  | 212395.00 | 212395.00 | 110000.00 | 110000.00 | 110000.00 | Yogesh builders
2.04 | Fabrication, supply, Installation testing & commissioning of Electrical control panel of cubical construction, floor mounted type, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection with suitable size copper conductor cable/solid copper strip, having switchgears and accessories, mountings and internal wiring, earth terminals, numbering etc. complete in all respect, suitable for main fire pump, pressurisation pump & diesel pump set complete as per CPWD specification with following in coming and Outgoings, suitable for operation on 415V, 3 phase, 50Hz Ac Supply with enclosure protection class IP 42 as required : INCOMING 250A, microprocessor based Over Load, Short circuit and Earth Fault Releases, 50kA 4 Pole MCCB, Ics=100% Icu rating Digital Voltmeter 0-500V with selector switch Digital Ammeter (0-250 A) with selector switch & CTsetc. LED type RYB phase indicating lamps, ON, OFF, trip indicating lamps. Set of Copper/Aluminium Bus Bar 300A | 1.00 | Set |  | 68000.00 | 68000.00 | 230000.00 | 230000.00 | 68000.00 | OLO HOUSING INFRA LLP
2.05 | Outgoing ( Note : All outgoing feeders for pumps should have digital Ammeter with selector switches, and LED type ON, OFF, trip indicating lamps) a) Main Fire Pump 125 A, microprocessor based Over Load, Short circuit and Earth Fault Releases ,50kA TPN MCCB, Ics=100% Icu, with fully automatic soft starter suitable for 60 HP pump with overload protection, current sensing type single phase preventer complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. b) Jockey Pump 63 A, microprocessor based Over Load, Short circuit and Earth Fault Releases, 50kA TPN MCCB, Ics=100% Icu, with suitable HP fully automatic soft starter with overload protection, current sensing type single phase preventer complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation c) DIESEL ENGINE CONTROL Control for diesel engine comprising - Automatic/Manual selector switch & 3 attempts starting device, timers and relays as required, push buttons, start/stop in manual mode Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication Battery charger suitable for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 0- 20 A DC Ammeter All standard relays and accessories for automatic operation of diesel engine System Controller Designing, Supply, Installation, Testing and commissioning of system controller to control operation of main electric fire pump, diesel pump, Pressurization pump, Terrace pump in sequence as per specification consisting of relays, timers. Sensors, annunciation window for fault indication, complete as per specification d) 4P, 63 Amps MCB - 04 No.
2.06 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the the trench etc. of following sizes complete as required. 150 mm. Dia | 140.00 | Meter |  | 2910.00 | 407400.00 | 2600.00 | 364000.00 | 364000.00 | Yogesh builders
2.07 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame/MS angle and painting with two or more coats of synthetic enamel paint of required shade complete as required : 65 mm dia | 40.00 | Meter |  | 980.00 | 39200.00 | 1300.00 | 52000.00 | 39200.00 | OLO HOUSING INFRA LLP
2.08 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame/MS angle and painting with two or more coats of synthetic enamel paint of required shade complete as required : 80 mm dia | 50.00 | Meter |  | 1090.00 | 54500.00 | 1200.00 | 60000.00 | 54500.00 | OLO HOUSING INFRA LLP
2.09 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame/MS angle and painting with two or more coats of synthetic enamel paint of required shade complete as required : 150 mm dia | 500.00 | Meter |  | 2770.00 | 1385000.00 | 2500.00 | 1250000.00 | 1250000.00 | Yogesh builders
2.10 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame/MS angle and painting with two or more coats of synthetic enamel paint of required shade complete as required : 200 mm dia | 15.00 | Meter |  | 3780.00 | 56700.00 | 3800.00 | 57000.00 | 56700.00 | OLO HOUSING INFRA LLP
2.11 | Supplying and fixing single headed Gunmetal internal hydrant valve with instantaneous Gunmetal coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required : | 6.00 | Set |  | 9200.00 | 55200.00 | 6500.00 | 39000.00 | 39000.00 | Yogesh builders
2.12 | Providing & fixing non-percolating rubber reinforced lined (RRL) fire hose pipe (as per IS : 636) of 63 mm dia and 15 meter length. The hose shall be rated for burst pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked gunmetal male & female coupling (IS:903) bound & riveted to hose pipe with copper rivets & 1.5 mm copper wire as required as per specifications. (Location : Internal fire hydrant) | 12.00 | Set |  | 5350.00 | 64200.00 | 5200.00 | 62400.00 | 62400.00 | Yogesh builders
2.13 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 with upto date amendments complete with the following as required. 30m x 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipment's on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket. | 6.00 | Set |  | 3900.00 | 23400.00 | 8000.00 | 48000.00 | 23400.00 | OLO HOUSING INFRA LLP
2.14 | Supplying and fixing of hose cabinet of size 0.9 x 0.6 x 0.5 mtr made out of SS sheet 2mm thick with 6 mm thick glazed glass doors i/c necessary locking arrangement suitable to accommodate Internal/external hydrant with butterfly valve, 2 no's 15mtr. long hose pipe, 1 no. branch pipe, mounted on wall OR raised brick platform & duly painted with post office red externally and white internally with synthetic enamel paint complete in all respect, for internal/external hydrant, as required. (Location : Internal/external fire hydrant) | 16.00 | Each |  | 24800.00 | 396800.00 | 4200.00 | 67200.00 | 67200.00 | Yogesh builders
2.15 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required : | 16.00 | Each |  | 2500.00 | 40000.00 | 3300.00 | 52800.00 | 40000.00 | OLO HOUSING INFRA LLP
2.16 | Supplying and fixing Single headed Gunmetal external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required : | 10.00 | Set |  | 9125.00 | 91250.00 | 6500.00 | 65000.00 | 65000.00 | Yogesh builders
2.17 | Providing & fixing controlled percolation fire hose pipe (as per IS:8423) of 63 mm dia and 15 meter length rated for burst pressure of 35.7 Kg/sqcm. The hose shall be tested for flame resistance test in accordance to IS:8423. Hose shall be complete with ISI marked GM male & female coupling (IS:903) bound & riveted to hose pipe with copper rivets & 1.5 mm copper wire as required as per specifications. (Location : External fire hydrant). | 20.00 | Set |  | 4275.00 | 85500.00 | 5200.00 | 104000.00 | 85500.00 | OLO HOUSING INFRA LLP
2.18 | Supplying, fixing, testing & commissioning of CI double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 14846 of following sizes as required : 80 mm dia | 2.00 | Each |  | 9906.00 | 19812.00 | 9500.00 | 19000.00 | 19000.00 | Yogesh builders
2.19 | Supplying, fixing, testing & commissioning of CI double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 14846 of following sizes as required : 150 mm dia | 4.00 | Each |  | 18552.00 | 74208.00 | 19000.00 | 76000.00 | 74208.00 | OLO HOUSING INFRA LLP
2.20 | Supplying, fixing, testing & commissioning of CI double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 14846 of following sizes as required : 200 mm dia | 6.00 | Each |  | 31574.00 | 189444.00 | 37500.00 | 225000.00 | 189444.00 | OLO HOUSING INFRA LLP
2.21 | Supplying, fixing, testing and commissioning of CI butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required : 65 mm dia | 10.00 | Each |  | 3357.00 | 33570.00 | 3500.00 | 35000.00 | 33570.00 | OLO HOUSING INFRA LLP
2.22 | Supplying, fixing, testing and commissioning of CI butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required : 80 mm dia | 10.00 | Each |  | 3293.00 | 32930.00 | 4200.00 | 42000.00 | 32930.00 | OLO HOUSING INFRA LLP
2.23 | Providing, installation, testing and commissioning of CI dual plate non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. conforming to IS 5312 of following sizes as required : 65 mm dia | 4.00 | Each |  | 3688.00 | 14752.00 | 5500.00 | 22000.00 | 14752.00 | OLO HOUSING INFRA LLP
2.24 | Providing, installation, testing and commissioning of CI dual plate non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. conforming to IS 5312 of following sizes as required : 80 mm dia | 1.00 | Each |  | 4728.00 | 4728.00 | 6000.00 | 6000.00 | 4728.00 | OLO HOUSING INFRA LLP
2.25 | Providing, installation, testing and commissioning of CI dual plate non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. conforming to IS 5312 of following sizes as required : 150 mm dia | 2.00 | Each |  | 7252.00 | 14504.00 | 9500.00 | 19000.00 | 14504.00 | OLO HOUSING INFRA LLP
2.26 | Providing, installation, testing & commissioning of PN 16 CI Y-Type strainer fabricated out of 1.6 mm thick stainless steel sheet with 3 mm dia holes with stainless steel flange. 200 mm dia | 2.00 | Each |  | 29868.00 | 59736.00 | 30000.00 | 60000.00 | 59736.00 | OLO HOUSING INFRA LLP
2.27 | Providing & fixing double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per specs including rubber gaskets, flanges, nuts, bolts and washers complete as required as per specifications. 80 mm dia | 2.00 | Each |  | 5150.00 | 10300.00 | 6000.00 | 12000.00 | 10300.00 | OLO HOUSING INFRA LLP
2.28 | Providing & fixing double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per specs including rubber gaskets, flanges, nuts, bolts and washers complete as required as per specifications. 150 mm dia | 2.00 | Each |  | 9399.00 | 18798.00 | 7800.00 | 15600.00 | 15600.00 | Yogesh builders
2.29 | Providing & fixing double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per specs including rubber gaskets, flanges, nuts, bolts and washers complete as required as per specifications. 200 mm dia | 2.00 | Each |  | 13049.00 | 26098.00 | 11000.00 | 22000.00 | 22000.00 | Yogesh builders
2.30 | Supplying and fixing orifice plate made out of 6 mm thick stainless steel (Grade 304) with orifice of required size to be fitted between flange & landing valve of external and internal hydrants to reduce pressure at the outlet to the level of 3.5 kg/cm2 complete as required. | 10.00 | Each |  | 1050.00 | 10500.00 | 1100.00 | 11000.00 | 10500.00 | OLO HOUSING INFRA LLP
2.31 | Providing and Fixing of pressure switches with isolation ball valve suitable for working pressure of 250 PSI for Main/Jockey/diesel pump complete with all required accessories required for operation. Model Danfoss KPI 35 or its equivalent) | 3.00 | Each |  | 4100.00 | 12300.00 | 5200.00 | 15600.00 | 12300.00 | OLO HOUSING INFRA LLP
2.32 | Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required : 4 way - 150 mm dia M.S. Pipe | 3.00 | Set |  | 8300.00 | 24900.00 | 12500.00 | 37500.00 | 24900.00 | OLO HOUSING INFRA LLP
2.33 | Providing & fixing MS cabinet to enclose fire brigade connection and draw out connection fabricated from MS sheet 2mm thick with 2mm thick MS sheet frame with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry platform as required as per specifications. (Approx. 0.6m x 0.6m x 0.45m) (Location : Fire brigade connection) | 3.00 | Set |  | 4200.00 | 12600.00 | 3200.00 | 9600.00 | 9600.00 | Yogesh builders
2.34 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | 1.00 | Set |  | 19200.00 | 19200.00 | 20000.00 | 20000.00 | 19200.00 | OLO HOUSING INFRA LLP
2.35 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI, short pieces, nipples, elbows, stainless steel 'U' tube & ball valve, etc. as required as per specifications | 4.00 | Each |  | 2800.00 | 11200.00 | 2100.00 | 8400.00 | 8400.00 | Yogesh builders
2.36 | Supply of following size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. 4Cx16 Sq.mm | 80.00 | Meter |  | 260.00 | 20800.00 | 150.00 | 12000.00 | 12000.00 | Yogesh builders
2.37 | Supply of following size DWC HDPE pipe, lSI marked along with all accessories like socket, couplers etc. conforming to IS 16205 Part 24 complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 250.00 | Meter |  | 150.00 | 37500.00 | 85.00 | 21250.00 | 21250.00 | Yogesh builders
2.38 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 250.00 | Meter |  | 325.00 | 81250.00 | 150.00 | 37500.00 | 37500.00 | Yogesh builders
2.39 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required. Above 95 sq. mm and upto 185 sq. mm | 280.00 | Meter |  | 1289.00 | 360920.00 | 68.00 | 19040.00 | 19040.00 | Yogesh builders
2.40 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 70.00 | Meter |  | 402.00 | 28140.00 | 40.00 | 2800.00 | 2800.00 | Yogesh builders
2.41 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 10.00 | Meter |  | 402.00 | 4020.00 | 80.00 | 800.00 | 800.00 | Yogesh builders
2.42 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. upto 35 sqmm (clamped with 1mm MS flat clamp) | 10.00 | Meter |  | 580.00 | 5800.00 | 50.00 | 500.00 | 500.00 | Yogesh builders
2.43 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 30.00 | Meter |  | 1450.00 | 43500.00 | 650.00 | 19500.00 | 19500.00 | Yogesh builders
2.44 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C X 70 sq. mm (38mm) | 2.00 | Each |  | 1250.00 | 2500.00 | 500.00 | 1000.00 | 1000.00 | Yogesh builders
2.45 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4X 16 sq. mm (28mm) | 8.00 | Each |  | 2250.00 | 18000.00 | 450.00 | 3600.00 | 3600.00 | Yogesh builders
2.46 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 8.00 | Set |  | 2250.00 | 18000.00 | 6000.00 | 48000.00 | 18000.00 | OLO HOUSING INFRA LLP
2.47 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 50.00 | Meter |  | 192.00 | 9600.00 | 220.00 | 11000.00 | 9600.00 | OLO HOUSING INFRA LLP
2.48 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 24.00 | Meter |  | 192.00 | 4608.00 | 600.00 | 14400.00 | 4608.00 | OLO HOUSING INFRA LLP
2.49 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 20.00 | Meter |  | 22.00 | 440.00 | 45.00 | 900.00 | 440.00 | OLO HOUSING INFRA LLP
2.50 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator). 6 way (8 + 18), Double door | 1.00 | Each |  | 7231.00 | 7231.00 | 7500.00 | 7500.00 | 7231.00 | OLO HOUSING INFRA LLP
2.51 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way , Double door | 1.00 | Each |  | 6480.00 | 6480.00 | 3300.00 | 3300.00 | 3300.00 | Yogesh builders
2.52 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole (6 amps-12 no) MCB | 12.00 | Each |  | 380.00 | 4560.00 | 450.00 | 5400.00 | 4560.00 | OLO HOUSING INFRA LLP
2.53 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Double pole (32amp ) | 1.00 | Each |  | 650.00 | 650.00 | 1200.00 | 1200.00 | 650.00 | OLO HOUSING INFRA LLP
2.54 | Supplying and fixing 4 pole, 63 A MCB rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each |  | 450.00 | 450.00 | 3800.00 | 3800.00 | 450.00 | OLO HOUSING INFRA LLP
2.55 | Supplying and fixing 4 pole, 63 A RCCB with 100 mA sensitivity, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each |  | 450.00 | 450.00 | 6500.00 | 6500.00 | 450.00 | OLO HOUSING INFRA LLP
2.56 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 12.00 | Point |  | 250.00 | 3000.00 | 1900.00 | 22800.00 | 3000.00 | OLO HOUSING INFRA LLP
2.57 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 15.00 | Point |  | 250.00 | 3750.00 | 1100.00 | 16500.00 | 3750.00 | OLO HOUSING INFRA LLP
2.58 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 40.00 | Meter |  | 264.00 | 10560.00 | 350.00 | 14000.00 | 10560.00 | OLO HOUSING INFRA LLP
2.59 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 30.00 | Meter |  | 357.00 | 10710.00 | 450.00 | 13500.00 | 10710.00 | OLO HOUSING INFRA LLP
2.60 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing of 2 No. 6 pin 5/6 & 15/16 A modular socket outlet and 2 no. 15/16 A modular switch, connections etc. as required. | 8.00 | Each |  | 850.00 | 6800.00 | 1550.00 | 12400.00 | 6800.00 | OLO HOUSING INFRA LLP
2.61 | Supply of 4 feet, 20 W, 6500K, extruded polycarbonate LED batten suitable to operate on single phase 240V supply | 12.00 | Each |  | 180.00 | 2160.00 | 200.00 | 2400.00 | 2160.00 | OLO HOUSING INFRA LLP
2.62 | Supply of 10 W, 6500K, IP 65, extruded polycarbonate bulk head light fitting suitable to operate on single phase 240V supply | 10.00 | Each |  | 1450.00 | 14500.00 | 1100.00 | 11000.00 | 11000.00 | Yogesh builders
2.63 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 22.00 | Each |  | 300.00 | 6600.00 | 190.00 | 4180.00 | 4180.00 | Yogesh builders
2.64 | Supply of 450 mm Sweep heavy duty exhaust fan, totally enclosed, highly efficient heavy duty motor with pressure die cast aluminium rotor mounted on ball bearings, IP 55, 1400 r/min, confirming to IS: 2312 -1967 suitable for operation on 230 / 240V 50 Hz single phase AC supply complete etc. as required. | 4.00 | Each |  | 6200.00 | 24800.00 | 7500.00 | 30000.00 | 24800.00 | OLO HOUSING INFRA LLP
2.65 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep | 4.00 | Each |  | 350.00 | 1400.00 | 190.00 | 760.00 | 760.00 | Yogesh builders
2.66 | Supply and fixing of 450 mm Sweep, 1440 r/min pedestal fan suitable for operation on 230 / 240V 50 Hz single phase AC supply complete etc. as required. | 2.00 | Each |  | 6500.00 | 13000.00 | 9000.00 | 18000.00 | 13000.00 | OLO HOUSING INFRA LLP
2.67 | SITC of 2 KVA Online UPS with SMF batteries, 30 minutes of battery backup with each UPS. | 1.00 | Job |  | 72000.00 | 72000.00 | 58647.00 | 58647.00 | 58647.00 | Yogesh builders
2.68 | Excavation of the cable trenches in hard rock/bitumen road/concrete pavement/paver block not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 100.00 | Cum |  | 650.00 | 65000.00 | 240.00 | 24000.00 | 24000.00 | Yogesh builders
| Total in Figures |  |  |  |  | 13345562.00 |  | 10180000.00
Lowest Amount Quoted BY: Yogesh builders(10180000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of internal and external Firefighting system at Solapur Airport. SH Construction of underground water tank, pump room, fire hydrants and other associated civil and electrical works at Solapur Airport. Tender ID: 2025_AAI_223178_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Yogesh builders (BID ID -808975) | 10180000.00 | L1
| 2 | OLO HOUSING INFRA LLP (BID ID -806315) | 13345562.00 | L2