## BoQ1
Government eProcurement System Created By: Sujit Karmakar Created Date/Time: 21-Feb-2025 05:06 PM Tender Title: New Construction of Standalone MSSR Antenna Tower in Badu at NSCBI Airport, Kolkata (SH Electrical Works) Tender ID: 2025_AAI_223539_1
Tender Inviting Authority: SM(E-E), AAI, RHQ, ER
Name of Work: New Construction of Standalone MSSR Antenna Tower in Badu at NSCBI Airport, Kolkata (SH-Electrical Works).
Contract No: AAI/ER/KOL/EE/NIT-09/2024-25
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders (GSTN-19AEIPB6323B1ZZ) BID ID -813530 |  | M/s J.K. Electric Engineering Works (GSTN-19AAHFJ4404E1ZL) BID ID -814531 |  | SAHA COMMERCIAL CONSTRUCTION (GSTN-19AASFS6288A1ZN) BID ID -814846 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -815000 |  | RELIABLE CONSTRUCTIONS (GSTN-NA) BID ID -814239
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing & commissioning of Machine Room Less electric traction type Lifts of 08 passengers, 544 KG Capacity,04 Stops, 04 openings and entrance at front sideon all the serving floors, automatic centre opening Stainless Steel Hairline finish door, car enclosure provided with Stainless Steel Hairline finish panel on sides and with travel height of 30 mtrs. (Approx). and type suitable for operation on 415 V, 3 phase, 50 Hz AC supply, having AC Variable Voltage and Variable Frequency type traction control, minimum speed of 1.0 Mtr/Sec, electromagnetic brake system, simplex mode operations, operating panel with luminous buttons, overload warning indicator, battery operated alarm bell, LED type emergency light, intercom suitable for hook up to AAI’s EPABX, infrared ray sensing door protection for full height, reverse phase relay on controller, fireman’s switch at ground floor, digital car positions indicator in car and at all positions indicator in car and at all floors with UP / DOWN direction, light fixtures, ventilation fan, etc complete with all accessories including Automatic Rescue Device (ARD) and Manual Rescue Device (MRD) in the event of power failure etc., as required. The traction motor of machine room less Lift shall be of gearless type and placed inside the Lift hoist way. Elevators shall be BMS compatible and cost should includes for obtainig necessary Licence from regulatory authority. | 1.00 | Job | 0.00 | 1650000.00 | 1650000.00 | 1400000.00 | 1400000.00 | 1725000.00 | 1725000.00 | 1775000.00 | 1775000.00 | 1685000.00 | 1685000.00 | 1400000.00 | M/s J.K. Electric Engineering Works
2.00 | Supply of 1 Phase, 1 TR, 5 star rating, Inverter type Split Air-conditioners whjich has high wall type indoor unit suitable for operation on 230±10%, 50 Hz, 1 phase power supply (along with necessary wiring from nearest power source to the required outdoor and indoor units) having high EER Compressor with Indoor & Outdoor Copper coil,refrigeration having aluminum fins firmly bonded to copper pipe and copper pipe insulation assembled in zinc coated steel frame with Eco friendly R-32 or equivalent refrigeration Gas alongwith copper conductor PVC insulated PVC sheathed multicore power cable from indoor to outdoor unit. The indoor unit should have real time clock, operating facility from cordless remote, along with time and temperature display. Outdoor unit to be installed as Directed by Engineer-in-Charge. | 2.00 | Each | 0.00 | 32000.00 | 64000.00 | 34000.00 | 68000.00 | 30000.00 | 60000.00 | 32000.00 | 64000.00 | 35000.00 | 70000.00 | 60000.00 | SAHA COMMERCIAL CONSTRUCTION
3.00 | Supply of floor mounted high performance Precision AC cooling unit of 3.5 TR with hermetic sealed Fixed Scroll Single Compressor suitable for Critical Technology/Equipment room fan section with dynamically balanced centrifugal fan driven by electronically communicated fan motor, fan shall be composite blade multi rows deep cooling coil of copper tubes & aluminium fins, remote aircooled condenser with copper tubes & aluminium fins, with electronic communicated fan with speed controller electronic / thermostatic expansion valve, insulated drain pan, SNMP/Modbus Card for remote monitoring, microprocessor based programmable logic controller including providing RS485 port for LAN monitoring of Humidity and Temperature of room , Infra Red / steam electrode humidifier, heaters, complete in a unit as per specifications enclosed in a factory fabricated & painted to smooth finish enclosure. Each unit shall facilitate installation in Small Areas, shall feature robust design to run 24x7. The precision packaged unit shall be complete with auto sequencing arrangement as required and shipped out of factory with full refrigerant charge. The compressor shall be suitable for operation on 415 +/- 10%, 50 Hz, 3 phase A.C. power supply, Inside Temperature 21 degree C ± 1 degree C, RH 50 ± 5% as required per NIT Technical specification and AAI approved make. | 3.00 | Job | 0.00 | 405000.00 | 1215000.00 | 453612.00 | 1360836.00 | 195000.00 | 585000.00 | 440000.00 | 1320000.00 | 435000.00 | 1305000.00 | 585000.00 | SAHA COMMERCIAL CONSTRUCTION
4.00 | Installation, testing & commissioning of 3.3 TR Precision AC as mentioned above in Item no.3
4.01 | Installation, testing & commissioning including Loading & Unloading Charges | 3.00 | Each | 0.00 | 35000.00 | 105000.00 | 37760.00 | 113280.00 | 15000.00 | 45000.00 | 78000.00 | 234000.00 | 40000.00 | 120000.00 | 45000.00 | SAHA COMMERCIAL CONSTRUCTION
4.02 | Supply and laying of the size of 18G hard drawn copper pipe 7/8 & 5/8 between PAC & outdoor unit with fitting, bends, brazing work etc., as required. | 60.00 | Mtr. | 0.00 | 4000.00 | 240000.00 | 1283.00 | 76980.00 | 950.00 | 57000.00 | 1790.00 | 107400.00 | 5000.00 | 300000.00 | 57000.00 | SAHA COMMERCIAL CONSTRUCTION
4.03 | Supply and laying of the copper pipe insulation- 9mm | 60.00 | Mtr. | 0.00 | 380.00 | 22800.00 | 1632.00 | 97920.00 | 350.00 | 21000.00 | 1500.00 | 90000.00 | 400.00 | 24000.00 | 21000.00 | SAHA COMMERCIAL CONSTRUCTION
4.04 | Supply & installation of 1.5 Sqmmx2 core copper armoured cable for cabling between indoor to outdoor unit Without cable tray. | 65.00 | Mtr. | 0.00 | 350.00 | 22750.00 | 594.00 | 38610.00 | 170.00 | 11050.00 | 85.00 | 5525.00 | 400.00 | 26000.00 | 5525.00 | Awasthi Electric Works
4.05 | Supply & installation of connecting incoming MAIN copper cable 4 x16 sq.mm from incoming isolator to PAC units | 120.00 | Mtr. | 0.00 | 1500.00 | 180000.00 | 260.00 | 31200.00 | 750.00 | 90000.00 | 820.00 | 98400.00 | 1800.00 | 216000.00 | 31200.00 | M/s J.K. Electric Engineering Works
4.06 | Supply and fixing of MS stands suitable for housing Indoor units,(40 x 40 x 5mm angle) | 3.00 | Each | 0.00 | 10500.00 | 31500.00 | 6000.00 | 18000.00 | 650.00 | 1950.00 | 3500.00 | 10500.00 | 12000.00 | 36000.00 | 1950.00 | SAHA COMMERCIAL CONSTRUCTION
4.07 | Supply and fixing of MS stands suitable for condenser units (40 x 40 x 5 mm angle) | 3.00 | Each | 0.00 | 10500.00 | 31500.00 | 6000.00 | 18000.00 | 850.00 | 2550.00 | 3500.00 | 10500.00 | 12000.00 | 36000.00 | 2550.00 | SAHA COMMERCIAL CONSTRUCTION
4.08 | Supply & Installation of CPVC Drain piping , clamps and supports, U trap has to be provided near all the units, 32/40mm dia as per site requirement, with Insulation | 20.00 | Mtr. | 0.00 | 1200.00 | 24000.00 | 907.00 | 18140.00 | 350.00 | 7000.00 | 560.00 | 11200.00 | 1500.00 | 30000.00 | 7000.00 | SAHA COMMERCIAL CONSTRUCTION
4.09 | Supply & Installation of CPVC humidifier piping, 25mm dia as per site requirement. | 20.00 | Mtr. | 0.00 | 1200.00 | 24000.00 | 552.00 | 11040.00 | 450.00 | 9000.00 | 250.00 | 5000.00 | 1500.00 | 30000.00 | 5000.00 | Awasthi Electric Works
4.10 | Supply & fixing of Ball Valves | 2.00 | Lot | 0.00 | 1300.00 | 2600.00 | 1150.00 | 2300.00 | 3000.00 | 6000.00 | 440.00 | 880.00 | 1600.00 | 3200.00 | 880.00 | Awasthi Electric Works
4.11 | Supply & charging of Gas R 407 C | 40.00 | Kg. | 0.00 | 1600.00 | 64000.00 | 500.00 | 20000.00 | 650.00 | 26000.00 | 1250.00 | 50000.00 | 1800.00 | 72000.00 | 20000.00 | M/s J.K. Electric Engineering Works
4.12 | Supply & fixing 2 core x 1 sq mm flexible communication cable between PAC units for sequencing | 20.00 | Mtr. | 0.00 | 300.00 | 6000.00 | 220.00 | 4400.00 | 250.00 | 5000.00 | 75.00 | 1500.00 | 500.00 | 10000.00 | 1500.00 | Awasthi Electric Works
5.00 | Supply, Installation ,Testing, Commissioning of FK-5-1-12 with min. 25 BAR total floding Gas Suppression System consisting of PESO Approved 120 ltr.capacity primary Cylinder and 120 ltr. tertiary cylinder with all accessories complete with UL / VDS / PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure,a pressure guage with a safety burst disc,4 channel Aspiration system with minimum pipining capacity 200 meter cover area with room dimention 25.58ft x 18.75ft x 10.5ft., electric/mannual actuator, pressure operated control, head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos of Nozzles (UL / VDS listed), Piping, Manifold etc. complete as required.CLEAN AGENT (FK-5-1-12)must be U/L certified and quantity would be as per the UL certification. CLEAN AGENT (FK-5-1-12) at Badu MSSR Equipment Room as per attached Technical Specification. Note: The Cylinder, Volume of Gas, Nos. of Nozzles, piping design and pressure calculations using manufacturer design software for a given dimension of room duly approved by manufacturer (OEM) shall be submitted prior to starting of the works for Equipment room at Badu MSSR. | 1.00 | Job | 0.00 | 1525000.00 | 1525000.00 | 1320000.00 | 1320000.00 | 900000.00 | 900000.00 | 1590000.00 | 1590000.00 | 1550000.00 | 1550000.00 | 900000.00 | SAHA COMMERCIAL CONSTRUCTION
6.00 | Supply, Installation ,Testing, Commissioning of FK-5-1-12 with min. 25 BAR Gas Suppression System consisting of PESO Approved 80ltr.capacity primary Cylinder with all accessories complete with UL / VDS / PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure,a pressure guage with a safety burst disc,4 channel Aspiration system with minimum pipining capacity 200 meter cover area with room dimention 15.83ft x 11.42ft x 9.25ft.,, electric/mannual actuator, head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos of Nozzles (UL / VDS listed), Piping, Manifold etc. complete as required .Gas (Quantity would be as per the volume given below and as per the UL / VDS certification.) CLEAN AGENT (FK-5-1-12) at Badu MSSR UPS Room as per attached Technical Specification. Note: The Cylinder, Volume of Gas, Nos. of Nozzles, piping design and pressure calculations using manufacturer design software for a given dimension of room duly approved by manufacturer (OEM) shall be submitted prior to starting of the works for UPS room at Badu MSSR. | 1.00 | Job | 0.00 | 650000.00 | 650000.00 | 660000.00 | 660000.00 | 845000.00 | 845000.00 | 730000.00 | 730000.00 | 600000.00 | 600000.00 | 600000.00 | RELIABLE CONSTRUCTIONS
7.00 | Supply of 18-20 W Indoor Surface mounted Integrated LED 4ft. long tube fitting , having lumen output more than 1800 Lumens , CCT from 5700 to 6000K, CRI >80, inbuild surge protection of minimum 4 kV suitable for indoor applications and 5 years warranty complete as per NIT LED technical specifications. (Similar to Bajaj make model no.BCLAB 20W CW LED EM or Equivalent) | 70.00 | Each | 0.00 | 400.00 | 28000.00 | 550.00 | 38500.00 | 450.00 | 31500.00 | 800.00 | 56000.00 | 450.00 | 31500.00 | 28000.00 | Youngmen Traders
8.00 | Supply of 34W-36W 2' x 2' recess Mounted LED fixture with high efficiency PMMA diffuser with CRCA housing complete with driver and accessories having lumen output more than 3400 Lumens with luminaire efficacy not less than 100 Lumens / watt, CCT from 6000K to 6500K, CRI>80, surge protection inbuild 4kV suitable for indoor applications and 5 years warranty complete as per NIT LED technical specifications.(Similar to Bajaj make model no.BZRSQL 36L LED GX or Equivalent) | 10.00 | Each | 0.00 | 1700.00 | 17000.00 | 2650.00 | 26500.00 | 4000.00 | 40000.00 | 1250.00 | 12500.00 | 1800.00 | 18000.00 | 12500.00 | Awasthi Electric Works
9.00 | Supply & fixing of LED aviation obstruction light with Die-cast aluminum housing with Red polycarbonate dome for better illumination, Integral driver suitable for outdoor applications Red Colour, Medium Intensity Aviation Light as per ICAO with IP 65 continuously glowing type with operating voltage of 230 V AC and 5 Years Warranty, complete as per technical specifications. (Similar to Bajaj make model no.BGAV 302 LED or Equivalent) | 2.00 | Each | 0.00 | 4000.00 | 8000.00 | 4500.00 | 9000.00 | 12000.00 | 24000.00 | 4750.00 | 9500.00 | 4500.00 | 9000.00 | 8000.00 | Youngmen Traders
10.00 | Supply of 150W±5% having high luminous efficiency Symmetric type LED flood light with medium beam angle ashetically designed housing with grey colour corrosion resistant Al. pressure die-cast housing with IP 66 protection or more, min. efficacy 120lm/W, CCT 6500K ± 5%, IK 08, min. CRI> 70 and having suitable LED array with dedicated lense ensuring uniform distribution of light including suitable electronic driver with overall min. surge protection of 10kV with necessary mounting bracket arrangement, 5 years warranty as complete as required, as per NIT LED technical specification. (Similar to Bajaj make model no.PRAZE F 180L WH NB-A5 TG SD or Equivalent) | 16.00 | Each | 0.00 | 5300.00 | 84800.00 | 5500.00 | 88000.00 | 6000.00 | 96000.00 | 5900.00 | 94400.00 | 5500.00 | 88000.00 | 84800.00 | Youngmen Traders
11.00 | Supply of 120W±5% having high luminous efficiency LED Street light with aesthetically designed housing with grey colour corrosion resistant Al. pressure die-cast housing with IP 66 protection or more, min. efficacy 120lm/W, CCT 6500K ± 5%, IK 08, min. CRI >70 and having suitable LED array ensuring uniform distribution of light including suitable electronic driver with overall min. surge protection of 10kV with necessary mounting arrangement, 5 years warranty as complete as required, as per NIT LED technical specification. (Similar to Bajaj make model no.ZELA P 144L WH PO TG SD or Equivalent) | 7.00 | Each | 0.00 | 3800.00 | 26600.00 | 3600.00 | 25200.00 | 3500.00 | 24500.00 | 4625.00 | 32375.00 | 4000.00 | 28000.00 | 24500.00 | SAHA COMMERCIAL CONSTRUCTION
12.00 | Supply Erection Installation Testing & Commissioning of 9 Mtr. Octagonal Pole with top mounted galvanized single cross arm for fixing of street light fixtures. The pole shaft shall be made from hot rolled steel plate and provided with the rigid base plate manufactured from MS steel confirming to relevant IS standard of suitable thickness with provision for fixing min. 4 nos. of foundation bolts. The base plate shall be fillet welded to the pole shaft at two locations i.e. from inside and outside. The pole shaft shall have octagonal cross section and shall be continuously tapered with single longitudinal welding. There shall not be any circumferential welding. The octagonal Poles shall have door of approximate 500 mm height at the elevation of 500 mm from the base plate. The hinged door shall be flush with the exterior surface and shall have suitable locking arrangement. There shall also be suitable arrangement for the purpose of earthing. Provision should be provided in the bottom compartment to mount PVC /Bakelite sheet along with connectors for cable looping and single pole MCB to isolate individual luminaire. | 5.00 | Each | 0.00 | 15000.00 | 75000.00 | 15500.00 | 77500.00 | 13000.00 | 65000.00 | 19500.00 | 97500.00 | 17000.00 | 85000.00 | 65000.00 | SAHA COMMERCIAL CONSTRUCTION
13.00 | ITC of pre-wired, LED fitting of all types, complete with all accessories etc. directly on ceiling/wall, including connection with 1.5 sqmm FR PVC insulated copper conductor with PVC flexible, single core cable and earthing making the installation as good as possible etc. as complete as required. | 103.00 | Each | 0.00 | 150.00 | 15450.00 | 150.00 | 15450.00 | 300.00 | 30900.00 | 250.00 | 25750.00 | 170.00 | 17510.00 | 15450.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
14.00 | Design, manufacture supply, installation, testing and commissioning of Wall mounted Indoore type LT Panel, cubicle type, front access structure having rotary handle with necessary interlocking for all the MCCBs made of 2 mm thick sheet steel for frame work and covers, 3mm thick Al. gland plates, totally enclosed, IP 42, wall mounting, dust and vermin proof, indoor type, compartmentalized, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Alluminium busbars extensible on both sides, fabrication shall be done in transportation sections, control wiring with 2.5 sq.mm. PVC insulated flexible copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items and as per technical specification: A) Incomer i) MCCB,415V, 3 Phase, 125 Amp, 50kA ,4P - 01 Sets with Thermal magnatic release having Over Current and , Short Circuit Current Settings ATM (TM) Release (Adjustable O/L 80%-100% & Adjustable S/C 5-10 In type), 4P (set of 4) Spreder Terminals suitable for 125Amp MCCB with Extended rotary Handle & 220V AC shunt release suitable for MCCB. ii) Indication Lamps, LED type for Red,Yellow,Blue with suitable Neutral link, 6A 1P 240V 10kA C-curve MCB 03Nos. iii)Three Phase Digital Multifunctional Meter for monitoring with all necessary accessories Relay Door Mounted-01Set. B) Bus Bars High conductivity 150 Amp Alluminium Electrolyte grade bus bars suitable for TPN system -01 Set. C) Outgoing i) MCCB, 100A, 25 kA, Four Pole, with Thermal magnetic release having Over Current and , Short Circuit Current Settings, (Ics=Icu)-2 Nos. ATM (TM) Release (Adjustable O/L 80%-100% & Adjustable S/C 5-10 In type), 4P (set of 4) Spreder Terminals suitable for 100A MCCB, Auxiliary Contact & Extended rotary Handle suitable for MCCB, RED & GREEN indication Lamp suitable for 240V, Neutral link, 6A 1P 10kA C-curve MCB 04Nos. ii) MCCB, 63A, 25 kA, Four Pole, with Thermal magnetic release having Over Current and , Short Circuit Current Settings, (Ics=Icu)-2 Nos. ATM (TM) Release (Adjustable O/L 80%-100% & Adjustable S/C 5-10 In type), 4P (set of 4) Spreder Terminals suitable for 63A MCCB, Auxiliary Contact & Extended rotary Handle suitable for MCCB, RED & GREEN indication Lamp suitable for 240V, Neutral link, 6A 1P 10kA C-curve MCB 04Nos. iii) 25x6 mm GI Strip for connection on Earth Electrode at both side of Panel and all MCCB are provided with exteded rotary handle & speader link) | 1.00 | Job | 0.00 | 125000.00 | 125000.00 | 105500.00 | 105500.00 | 250000.00 | 250000.00 | 130000.00 | 130000.00 | 135000.00 | 135000.00 | 105500.00 | M/s J.K. Electric Engineering Works
15.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable etc. as required.
15.10 | Group C | 45.00 | Point | 0.00 | 1200.00 | 54000.00 | 1200.00 | 54000.00 | 1700.00 | 76500.00 | 1500.00 | 67500.00 | 1300.00 | 58500.00 | 54000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
16.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required.
16.10 | Group C | 30.00 | Point | 0.00 | 750.00 | 22500.00 | 800.00 | 24000.00 | 1800.00 | 54000.00 | 850.00 | 25500.00 | 770.00 | 23100.00 | 22500.00 | Youngmen Traders
17.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/recessed steel conduit as required
17.10 | 2 x 2.5 sq. mm + 1 x 2.5 sq. mm earth wire | 150.00 | Metre | 0.00 | 195.00 | 29250.00 | 270.00 | 40500.00 | 350.00 | 52500.00 | 300.00 | 45000.00 | 200.00 | 30000.00 | 29250.00 | Youngmen Traders
17.20 | 2 x 4 sq. mm + 1 x 4 sq. mm earth wire | 100.00 | Metre | 0.00 | 290.00 | 29000.00 | 300.00 | 30000.00 | 400.00 | 40000.00 | 350.00 | 35000.00 | 300.00 | 30000.00 | 29000.00 | Youngmen Traders
17.30 | 2 x 6 sq. mm + 1 x 6 sq. mm earth wire | 50.00 | Metre | 0.00 | 325.00 | 16250.00 | 430.00 | 21500.00 | 500.00 | 25000.00 | 450.00 | 22500.00 | 340.00 | 17000.00 | 16250.00 | Youngmen Traders
18.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
18.10 | 20 mm | 50.00 | Metre | 0.00 | 75.00 | 3750.00 | 180.00 | 9000.00 | 215.00 | 10750.00 | 128.00 | 6400.00 | 80.00 | 4000.00 | 3750.00 | Youngmen Traders
18.20 | 25 mm | 50.00 | Metre | 0.00 | 95.00 | 4750.00 | 206.00 | 10300.00 | 250.00 | 12500.00 | 175.00 | 8750.00 | 98.00 | 4900.00 | 4750.00 | Youngmen Traders
18.30 | 32 mm | 50.00 | Metre | 0.00 | 115.00 | 5750.00 | 260.00 | 13000.00 | 300.00 | 15000.00 | 240.00 | 12000.00 | 120.00 | 6000.00 | 5750.00 | Youngmen Traders
19.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, three core cable in the existing surface/ recessed steel/ PVC conduit as required.
19.10 | 3 x 2.5 sq. mm flexible cable confirming to IS 694 | 170.00 | Metre | 0.00 | 115.00 | 19550.00 | 160.00 | 27200.00 | 125.00 | 21250.00 | 125.00 | 21250.00 | 125.00 | 21250.00 | 19550.00 | Youngmen Traders
20.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required.
20.10 | 3 Module (100mmX75mm) | 20.00 | Each | 0.00 | 125.00 | 2500.00 | 105.00 | 2100.00 | 325.00 | 6500.00 | 180.00 | 3600.00 | 130.00 | 2600.00 | 2100.00 | M/s J.K. Electric Engineering Works
20.20 | 4 Module (125mmX75mm) | 20.00 | Each | 0.00 | 135.00 | 2700.00 | 125.00 | 2500.00 | 335.00 | 6700.00 | 215.00 | 4300.00 | 140.00 | 2800.00 | 2500.00 | M/s J.K. Electric Engineering Works
20.30 | 6 Module (200mmX75mm) | 20.00 | Each | 0.00 | 295.00 | 5900.00 | 325.00 | 6500.00 | 375.00 | 7500.00 | 350.00 | 7000.00 | 300.00 | 6000.00 | 5900.00 | Youngmen Traders
20.40 | 8 Module (125mmX125mm) | 20.00 | Each | 0.00 | 350.00 | 7000.00 | 285.00 | 5700.00 | 425.00 | 8500.00 | 445.00 | 8900.00 | 380.00 | 7600.00 | 5700.00 | M/s J.K. Electric Engineering Works
21.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
21.10 | 5/6 amps switch | 20.00 | Each | 0.00 | 90.00 | 1800.00 | 95.00 | 1900.00 | 100.00 | 2000.00 | 70.00 | 1400.00 | 100.00 | 2000.00 | 1400.00 | Awasthi Electric Works
21.20 | 15/16 A switch | 40.00 | Each | 0.00 | 115.00 | 4600.00 | 140.00 | 5600.00 | 150.00 | 6000.00 | 135.00 | 5400.00 | 120.00 | 4800.00 | 4600.00 | Youngmen Traders
21.30 | 3 pin 5/6 A socket outlet | 20.00 | Each | 0.00 | 125.00 | 2500.00 | 130.00 | 2600.00 | 120.00 | 2400.00 | 115.00 | 2300.00 | 130.00 | 2600.00 | 2300.00 | Awasthi Electric Works
21.40 | 6 pin 15/16 A socket outlet | 40.00 | Each | 0.00 | 150.00 | 6000.00 | 175.00 | 7000.00 | 175.00 | 7000.00 | 215.00 | 8600.00 | 160.00 | 6400.00 | 6000.00 | Youngmen Traders
22.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 10.00 | Each | 0.00 | 425.00 | 4250.00 | 500.00 | 5000.00 | 400.00 | 4000.00 | 545.00 | 5450.00 | 430.00 | 4300.00 | 4000.00 | SAHA COMMERCIAL CONSTRUCTION
23.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 10.00 | Each | 0.00 | 25.00 | 250.00 | 35.00 | 350.00 | 20.00 | 200.00 | 28.00 | 280.00 | 28.00 | 280.00 | 200.00 | SAHA COMMERCIAL CONSTRUCTION
24.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required .
24.10 | 8 way (4 + 24), Double door | 3.00 | Each | 0.00 | 2800.00 | 8400.00 | 6300.00 | 18900.00 | 9500.00 | 28500.00 | 8875.00 | 26625.00 | 2850.00 | 8550.00 | 8400.00 | Youngmen Traders
25.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
25.10 | Single pole | 40.00 | Each | 0.00 | 165.00 | 6600.00 | 250.00 | 10000.00 | 150.00 | 6000.00 | 170.00 | 6800.00 | 170.00 | 6800.00 | 6000.00 | SAHA COMMERCIAL CONSTRUCTION
25.20 | Four Pole | 6.00 | Each | 0.00 | 950.00 | 5700.00 | 1450.00 | 8700.00 | 550.00 | 3300.00 | 1450.00 | 8700.00 | 980.00 | 5880.00 | 3300.00 | SAHA COMMERCIAL CONSTRUCTION
26.00 | Providing and fixing following rating and breaking capacity and pole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
26.10 | 63A, FP,10kA | 4.00 | Each | 0.00 | 1800.00 | 7200.00 | 1950.00 | 7800.00 | 1200.00 | 4800.00 | 6500.00 | 26000.00 | 2000.00 | 8000.00 | 4800.00 | SAHA COMMERCIAL CONSTRUCTION
27.00 | Supply & fixing of 4way CRCA powder coated Sheet Steel MCB Enclosure , suitable for surface and flush mountiug conforming to IS8623-1 | 2.00 | Each | 0.00 | 550.00 | 1100.00 | 650.00 | 1300.00 | 950.00 | 1900.00 | 475.00 | 950.00 | 600.00 | 1200.00 | 950.00 | Awasthi Electric Works
28.00 | Supply & fixing of CRCA powder coated Sheet Steel MCCB Enclosure with in build neutral link and IK08 and IP30 protection | 1.00 | Each | 0.00 | 1600.00 | 1600.00 | 1800.00 | 1800.00 | 1050.00 | 1050.00 | 5200.00 | 5200.00 | 1800.00 | 1800.00 | 1050.00 | SAHA COMMERCIAL CONSTRUCTION
29.00 | Supply of following sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date.
29.10 | 4 Core, 35 Sq.mm. | 250.00 | Metre | 0.00 | 230.00 | 57500.00 | 285.00 | 71250.00 | 400.00 | 100000.00 | 275.00 | 68750.00 | 250.00 | 62500.00 | 57500.00 | Youngmen Traders
29.20 | 3.5 Core, 70 Sq.mm. | 400.00 | Metre | 0.00 | 365.00 | 146000.00 | 470.00 | 188000.00 | 625.00 | 250000.00 | 400.00 | 160000.00 | 380.00 | 152000.00 | 146000.00 | Youngmen Traders
30.00 | Supply of following sizes of Single Core Copper Conductor PVC Cables (Unsheathed) of 1.1 KV grade conforming to IS 694 amended upto date.
30.10 | 16 Sq.mm | 50.00 | Metre | 0.00 | 190.00 | 9500.00 | 280.00 | 14000.00 | 200.00 | 10000.00 | 210.00 | 10500.00 | 200.00 | 10000.00 | 9500.00 | Youngmen Traders
31.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
31.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 150.00 | Metre | 0.00 | 45.00 | 6750.00 | 38.00 | 5700.00 | 50.00 | 7500.00 | 120.00 | 18000.00 | 50.00 | 7500.00 | 5700.00 | M/s J.K. Electric Engineering Works
31.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 300.00 | Metre | 0.00 | 95.00 | 28500.00 | 95.00 | 28500.00 | 65.00 | 19500.00 | 140.00 | 42000.00 | 98.00 | 29400.00 | 19500.00 | SAHA COMMERCIAL CONSTRUCTION
32.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ STONEWARE/ METAL/CORRUGATED PIPE as required.
32.10 | Upto 35 sq. mm | 50.00 | Metre | 0.00 | 35.00 | 1750.00 | 16.00 | 800.00 | 30.00 | 1500.00 | 40.00 | 2000.00 | 40.00 | 2000.00 | 800.00 | M/s J.K. Electric Engineering Works
32.20 | Above 35 sq. mm and upto 95 sq. mm | 50.00 | Metre | 0.00 | 45.00 | 2250.00 | 16.00 | 800.00 | 40.00 | 2000.00 | 70.00 | 3500.00 | 55.00 | 2750.00 | 800.00 | M/s J.K. Electric Engineering Works
33.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
33.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Metre | 0.00 | 40.00 | 2000.00 | 35.00 | 1750.00 | 35.00 | 1750.00 | 120.00 | 6000.00 | 45.00 | 2250.00 | 1750.00 | M/s J.K. Electric Engineering Works, SAHA COMMERCIAL CONSTRUCTION
33.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 50.00 | Metre | 0.00 | 75.00 | 3750.00 | 50.00 | 2500.00 | 45.00 | 2250.00 | 140.00 | 7000.00 | 85.00 | 4250.00 | 2250.00 | SAHA COMMERCIAL CONSTRUCTION
34.00 | Supplying and making end termination with brass compression gland and Aluminum lugs for following size of XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade as required.
34.10 | 4 Core 35 Sq.mm. | 6.00 | Sets | 0.00 | 325.00 | 1950.00 | 350.00 | 2100.00 | 250.00 | 1500.00 | 290.00 | 1740.00 | 330.00 | 1980.00 | 1500.00 | SAHA COMMERCIAL CONSTRUCTION
34.20 | 3.5 Core 70 Sq.mm. | 6.00 | Sets | 0.00 | 350.00 | 2100.00 | 380.00 | 2280.00 | 450.00 | 2700.00 | 450.00 | 2700.00 | 380.00 | 2280.00 | 2100.00 | Youngmen Traders
35.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Sets | 0.00 | 12500.00 | 50000.00 | 12000.00 | 48000.00 | 15500.00 | 62000.00 | 20000.00 | 80000.00 | 13000.00 | 52000.00 | 48000.00 | M/s J.K. Electric Engineering Works
36.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Sets | 0.00 | 8000.00 | 16000.00 | 5500.00 | 11000.00 | 8000.00 | 16000.00 | 14000.00 | 28000.00 | 9000.00 | 18000.00 | 11000.00 | M/s J.K. Electric Engineering Works
37.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but with charcoal/ coke and salt ) as required. | 2.00 | Sets | 0.00 | 7000.00 | 14000.00 | 4500.00 | 9000.00 | 5000.00 | 10000.00 | 10000.00 | 20000.00 | 8000.00 | 16000.00 | 9000.00 | M/s J.K. Electric Engineering Works
38.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Metre | 0.00 | 1290.00 | 129000.00 | 1225.00 | 122500.00 | 1250.00 | 125000.00 | 1550.00 | 155000.00 | 1400.00 | 140000.00 | 122500.00 | M/s J.K. Electric Engineering Works
39.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 50.00 | Metre | 0.00 | 125.00 | 6250.00 | 115.00 | 5750.00 | 500.00 | 25000.00 | 170.00 | 8500.00 | 130.00 | 6500.00 | 5750.00 | M/s J.K. Electric Engineering Works
40.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc.as required. | 60.00 | Metre | 0.00 | 475.00 | 28500.00 | 560.00 | 33600.00 | 450.00 | 27000.00 | 620.00 | 37200.00 | 490.00 | 29400.00 | 27000.00 | SAHA COMMERCIAL CONSTRUCTION
41.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Metre | 0.00 | 175.00 | 8750.00 | 195.00 | 9750.00 | 100.00 | 5000.00 | 160.00 | 8000.00 | 180.00 | 9000.00 | 5000.00 | SAHA COMMERCIAL CONSTRUCTION
42.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 210.00 | Metre | 0.00 | 25.00 | 5250.00 | 32.00 | 6720.00 | 70.00 | 14700.00 | 30.00 | 6300.00 | 30.00 | 6300.00 | 5250.00 | Youngmen Traders
43.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
43.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 340.00 | Metre | 0.00 | 575.00 | 195500.00 | 540.00 | 183600.00 | 400.00 | 136000.00 | 550.00 | 187000.00 | 550.00 | 187000.00 | 136000.00 | SAHA COMMERCIAL CONSTRUCTION
44.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
44.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 40.00 | Each | 0.00 | 1075.00 | 43000.00 | 850.00 | 34000.00 | 475.00 | 19000.00 | 950.00 | 38000.00 | 1100.00 | 44000.00 | 19000.00 | SAHA COMMERCIAL CONSTRUCTION
45.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
45.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 30.00 | Each | 0.00 | 1600.00 | 48000.00 | 1200.00 | 36000.00 | 485.00 | 14550.00 | 1400.00 | 42000.00 | 1650.00 | 49500.00 | 14550.00 | SAHA COMMERCIAL CONSTRUCTION
46.00 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 4.00 | Each | 0.00 | 450.00 | 1800.00 | 495.00 | 1980.00 | 750.00 | 3000.00 | 1500.00 | 6000.00 | 480.00 | 1920.00 | 1800.00 | Youngmen Traders
47.00 | Providing and fixing Copper tape 20 mm X 3 mm thick on parapet or surface of wall with GI saddle, PVC fastener etc for lightning conductor as complete as required.(For horizontal run) | 50.00 | Metre | 0.00 | 625.00 | 31250.00 | 460.00 | 23000.00 | 500.00 | 25000.00 | 1340.00 | 67000.00 | 630.00 | 31500.00 | 23000.00 | M/s J.K. Electric Engineering Works
48.00 | Providing and fixing Copper tape 20 mm X 3 mm thick on parapet or surface of wall with GI saddle, PVC fastener etc for lightning conductor as complete as required.(For vertical run) | 150.00 | Metre | 0.00 | 690.00 | 103500.00 | 530.00 | 79500.00 | 525.00 | 78750.00 | 1340.00 | 201000.00 | 695.00 | 104250.00 | 78750.00 | SAHA COMMERCIAL CONSTRUCTION
49.00 | ITC of the following TR split type of Inverter Air-conditioners along with Outdoor/ Indoor unit suitable to operate on 1/3 Phase Power supply.
49.10 | 1 TR Split Inverter AC | 2.00 | Each | 0.00 | 1200.00 | 2400.00 | 3000.00 | 6000.00 | 2500.00 | 5000.00 | 3500.00 | 7000.00 | 1250.00 | 2500.00 | 2400.00 | Youngmen Traders
50.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
50.10 | 50mm dia | 72.00 | Metre | 0.00 | 590.00 | 42480.00 | 595.00 | 42840.00 | 450.00 | 32400.00 | 550.00 | 39600.00 | 600.00 | 43200.00 | 32400.00 | SAHA COMMERCIAL CONSTRUCTION
51.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 40.00 | Cum | 0.00 | 950.00 | 38000.00 | 300.00 | 12000.00 | 1250.00 | 50000.00 | 1200.00 | 48000.00 | 980.00 | 39200.00 | 12000.00 | M/s J.K. Electric Engineering Works
| Total in Figures |  |  |  |  | 7516630.00 |  | 6944526.00 |  | 6409400.00 |  | 8228125.00 |  | 7848750.00
Lowest Amount Quoted BY: SAHA COMMERCIAL CONSTRUCTION(6409400.00)

## BOQ Summary
BOQ Summary Details Tender Title: New Construction of Standalone MSSR Antenna Tower in Badu at NSCBI Airport, Kolkata (SH Electrical Works) Tender ID: 2025_AAI_223539_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAHA COMMERCIAL CONSTRUCTION (BID ID -814846) | 6409400.00 | L1
| 2 | M/s J.K. Electric Engineering Works (BID ID -814531) | 6944526.00 | L2
| 3 | Youngmen Traders (BID ID -813530) | 7516630.00 | L3
| 4 | RELIABLE CONSTRUCTIONS (BID ID -814239) | 7848750.00 | L4
| 5 | Awasthi Electric Works (BID ID -815000) | 8228125.00 | L5