## BoQ1
Government eProcurement System Created By: SOLOMON PRABHAKAR Created Date/Time: 18-Feb-2025 12:52 PM Tender Title: Replacememt of Fire Detection and alarm system at Tuticorin Airport Tender ID: 2025_AAI_224309_1
Tender Inviting Authority: SM (E-E), Airports Authority of India, Tuticorin Airport.
Name of Work: Replacement of fire detection and alarm system at Tuticorin Airport.
Contract No: 2025_AAI_224309_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -814133 |  | Ponmani International (India) Pvt Ltd (GSTN-33AADCP6242R2ZZ) BID ID -814250 |  | ILLUMECH ENGINEERING (GSTN-NA) BID ID -815054 |  | DElite System Engineering (India) Pvt. Ltd. (GSTN-NA) BID ID -814933
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply installation testing and commissioning of Two Loop microprocessor based intelligent addressable main fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices(including detectors)and minimum 120 detectors per loop and loop length up to 2km, network communication card, minimum 320 graphics/LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit(230+/-5%,50Hz), 48Hrs backup with 24volt sealed maintenance free batteries with automatic charger having facility to connect printer to printout log and facility to have seamless integration with analogy/digital voice evacuation system and shall be complete with all accessories. The panel shall be compatible for IBMS system with open protocol BAC net/Modbus over IP complete as per specification. | 1.00 | Job | 10.00 | 249000.00 | 249000.00 | 174978.00 | 174978.00 | 249587.00 | 249587.00 | 246999.00 | 246999.00 | 174978.00 | Ponmani International (India) Pvt Ltd
2.00 | Multi Sensor Detector :Supply, Installation, Testing and Commissioning of PHOTO-THERMAL MULTI CRITERIA DETECTOR with indicating lamp, complete as required. | 50.00 | Job | 10.00 | 2490.00 | 124500.00 | 2550.00 | 127500.00 | 3264.00 | 163200.00 | 3499.00 | 174950.00 | 124500.00 | CENTRE TAP ENGINEERING
3.00 | Supply, Installation, mounting base for detector complete as required. | 50.00 | Job | 10.00 | 415.00 | 20750.00 | 287.00 | 14350.00 | 425.00 | 21250.00 | 499.00 | 24950.00 | 14350.00 | Ponmani International (India) Pvt Ltd
4.00 | Supply, Installation, testing and commissioning of Isolator Module with indicating lamp, mounting base and all other mounting accessories complete as required. | 5.00 | Job | 10.00 | 2490.00 | 12450.00 | 2740.00 | 13700.00 | 3856.00 | 19280.00 | 2989.00 | 14945.00 | 12450.00 | CENTRE TAP ENGINEERING
5.00 | Supply, Installation, testing and commissioning of Addressable Control Modules with all the mounting accessories complete as required. | 5.00 | Job | 10.00 | 2905.00 | 14525.00 | 3440.00 | 17200.00 | 4376.00 | 21880.00 | 3989.00 | 19945.00 | 14525.00 | CENTRE TAP ENGINEERING
6.00 | Supply, Installation, testing and commissioning of Addressable Hooter with relay Modules all the mounting accessories complete as required. | 4.00 | Job | 10.00 | 2905.00 | 11620.00 | 5050.00 | 20200.00 | 6587.00 | 26348.00 | 3989.00 | 15956.00 | 11620.00 | CENTRE TAP ENGINEERING
7.00 | Supply Installation testing and commissioning of intelligent addressable programmable manual call point as required. | 6.00 | Job | 10.00 | 3735.00 | 22410.00 | 4050.00 | 24300.00 | 4582.00 | 27492.00 | 4215.00 | 25290.00 | 22410.00 | CENTRE TAP ENGINEERING
8.00 | Supply Installation testing and commissioning of intelligent addressable mini monitor modules with all accessories complete as required. | 6.00 | Job | 10.00 | 3735.00 | 22410.00 | 2690.00 | 16140.00 | 3295.00 | 19770.00 | 4215.00 | 25290.00 | 16140.00 | Ponmani International (India) Pvt Ltd
9.00 | Supply Installation testing and commissioning of intelligent addressable monitor modules with all accessories complete as required. | 4.00 | Job | 10.00 | 3320.00 | 13280.00 | 2690.00 | 10760.00 | 3295.00 | 13180.00 | 4215.00 | 16860.00 | 10760.00 | Ponmani International (India) Pvt Ltd
10.00 | Supply of 2X1.5Sqmm fire alarm armoured cable 1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring and FRLS outer sheath complete as required. | 500.00 | Metre | 10.00 | 125.00 | 62500.00 | 80.00 | 40000.00 | 86.00 | 43000.00 | 89.00 | 44500.00 | 40000.00 | Ponmani International (India) Pvt Ltd
11.00 | Laying of 2X1.5Sqmm fire alarm armoured cable on surface using suitable size wire clip etc as required. | 100.00 | Metre | 10.00 | 50.00 | 5000.00 | 45.00 | 4500.00 | 40.00 | 4000.00 | 99.00 | 9900.00 | 4000.00 | ILLUMECH ENGINEERING
12.00 | Drawing of 2X1.5Sqmm fire alarm armoured cable in existing HDPE/PVC/HUME/MS pipe etc as required. | 400.00 | Metre | 10.00 | 65.00 | 26000.00 | 60.00 | 24000.00 | 60.00 | 24000.00 | 99.00 | 39600.00 | 24000.00 | Ponmani International (India) Pvt Ltd, ILLUMECH ENGINEERING
13.00 | Supply and laying of 50mmdia GI pipe in ground complete with GI fitting including trenching and refilling etc as required. | 40.00 | Metre | 10.00 | 1250.00 | 50000.00 | 1800.00 | 72000.00 | 650.00 | 26000.00 | 999.00 | 39960.00 | 26000.00 | ILLUMECH ENGINEERING
14.00 | Dismantling of bituminous road manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. | 1.00 | Cum | 10.00 | 1250.00 | 1250.00 | 17000.00 | 17000.00 | 15973.00 | 15973.00 | 7000.00 | 7000.00 | 1250.00 | CENTRE TAP ENGINEERING
15.00 | Providing and laying cement concrete of grade 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 3.00 | Cum | 10.00 | 2490.00 | 7470.00 | 25000.00 | 75000.00 | 5500.00 | 16500.00 | 11000.00 | 33000.00 | 7470.00 | CENTRE TAP ENGINEERING
16.00 | Dismantling of existing detector, fire alarm panel, hooter, cable,etc,and shifting to AAI store as per direction of Engineer-in-charge. | 1.00 | Job | 10.00 | 41500.00 | 41500.00 | 95800.00 | 95800.00 | 52768.00 | 52768.00 | 15000.00 | 15000.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd.
| Total in Figures |  |  |  |  | 684665.00 |  | 747428.00 |  | 744228.00 |  | 754145.00
Lowest Amount Quoted BY: CENTRE TAP ENGINEERING(684665.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacememt of Fire Detection and alarm system at Tuticorin Airport Tender ID: 2025_AAI_224309_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CENTRE TAP ENGINEERING (BID ID -814133) | 684665.00 | L1
| 2 | ILLUMECH ENGINEERING (BID ID -815054) | 744228.00 | L2
| 3 | Ponmani International (India) Pvt Ltd (BID ID -814250) | 747428.00 | L3
| 4 | DElite System Engineering (India) Pvt. Ltd. (BID ID -814933) | 754145.00 | L4