## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 07-Mar-2025 03:52 PM Tender Title: Installation of new stand alone MSSR Building at Maharana Pratap Airport, Udaipur. SH - SITC of Air-conditioning system. Tender ID: 2025_AAI_224543_1
Tender Inviting Authority: SM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: Installation of new stand alone MSSR Building at Maharana Pratap Airport, Udaipur. SH- SITC of Air-conditioning system.
Contract No: AAI/UDR/ENGG(E)/2024-25/MSSR/AC
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Comfort systems (GSTN-07AACPT8904A1ZV) BID ID -817003 |  | Utility Services (GSTN-06AABFU8051C1ZG) BID ID -817104 |  | vinayak cooling services (GSTN-08AXJPS5197G1ZT) BID ID -817188 |  | NAQVI BROTHERS (GSTN-09ADHPN6210D1ZT) BID ID -817567 |  | AirBizz AirConditioning Pvt. Ltd. (GSTN-NA) BID ID -812128
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 12 TR Floor Mounted, Bottom discharge, Top suction, Air Cooled DX type PRECISION AC Units for Equipment room application suitable to maintain equipment room temperature at 20°C ± 1°C for precise control of Equipment room,suitable for 415 Volts, 50 Hz, 3 Phase Power Supply. The units shall be selected on the basis of following parameters: i) Not Less then 12TR @ min. 12000 CMH and external static pressure 20 Pa. | 2.00 | Each | 0.00 | 954500.00 | 1909000.00 | 1017595.00 | 2035190.00 | 950000.00 | 1900000.00 | 1000000.00 | 2000000.00 | 1071400.00 | 2142800.00 | 1900000.00 | vinayak cooling services
1.10 | The Indoor unit shall comprise of Variable capacity Inverter Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, Thermostatic/Electronic Expansion valves, Driers, EU4/G4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crank case heaters, infrared/steam Electrode Humidifier, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories. Each unit shall be BMS compatible and shall have inbuilt software to faciliate BMS connectivity through RS485 Modbus Protocol and Ethernet with Modbus Protocol and HTTP Protocol. Each unit shal have individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values etc. as per the specifications considered excluding initial gas charge. The Outdoor Condenser unit shall have IP 54 protection and shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminum fins), automatic Fan speed controller, Isolator switch.Complete as per OEMs specifications.
2.00 | Installation, tensting and commisiooning of Floor Mounted, Bottom discharge, Air Cooled DX type Precision AC Units (Indoor & Outdoor) for Equipment room application, including Lifting, shifting & positioning of Indoor and outdoor units, Pressure testing, Vacumzing, charging, communication cabling, integration, interfacing, sequential operation, testing Commissioning of the system by OEM engineer, including providing of suitable MS stand for Indoor and Outdoor units as per OEM, Initial charge of R-410A refrigerant gas, including minor civil work complete as per site requirement. | 2.00 | Job | 0.00 | 29900.00 | 59800.00 | 53000.00 | 106000.00 | 40000.00 | 80000.00 | 90000.00 | 180000.00 | 100000.00 | 200000.00 | 59800.00 | Comfort systems
3.00 | Supply & fixing of 18 gauge Hard Drawn Copper Pipe Refrigerant piping duly complete with all insulation, supports, clamps, fittings, connections, sleevs etc fittings and finished with two coated of enamel paint of approved colour code including suitable thickness as per OEM closed cell elastromeric insulation with Class 'O' fire retardent properties for piping the air conditioned space. | 80.00 | Metre | 0.00 | 1870.00 | 149600.00 | 2182.00 | 174560.00 | 1900.00 | 152000.00 | 2500.00 | 200000.00 | 2800.00 | 224000.00 | 149600.00 | Comfort systems
4.00 | Supply & Installation of Electrical PVC INSULATED & FRLS MULTI CORE copper cable (as per IS 694) on surface, cable tray, pipe as per site requirement (Cable size-4x2.5 Sq.mm.). | 50.00 | Metre | 0.00 | 160.00 | 8000.00 | 361.00 | 18050.00 | 530.00 | 26500.00 | 200.00 | 10000.00 | 230.00 | 11500.00 | 8000.00 | Comfort systems
5.00 | Supply & Installation of Electrical PVC INSULATED & FRLS MULTI CORE copper cable (as per IS 694) on surface, cable tray, pipe as per site requirement (Cable size-4 x 25 Sq.mm.). | 50.00 | Metre | 0.00 | 1550.00 | 77500.00 | 2599.00 | 129950.00 | 530.00 | 26500.00 | 1500.00 | 75000.00 | 230.00 | 11500.00 | 11500.00 | AirBizz AirConditioning Pvt. Ltd.
6.00 | Providing & fixing GI sheet cover over the cable trays on the cable trays of size 300 mm width X 50 mm depth by using 2 mm thick GI sheet including bending as per required size, fixing securely over the cable trays to give a finished look complete as required as per site requirement. | 50.00 | Metre | 0.00 | 500.00 | 25000.00 | 1102.00 | 55100.00 | 280.00 | 14000.00 | 1500.00 | 75000.00 | 1550.00 | 77500.00 | 14000.00 | vinayak cooling services
7.00 | Supply and fixing of 25 mm dia CPVC Pipe for humidifier inlet. Complete with fittings supports, valves, 6 mm thick nitrile rubber insulation as required. | 30.00 | Metre | 0.00 | 160.00 | 4800.00 | 327.00 | 9810.00 | 100.00 | 3000.00 | 250.00 | 7500.00 | 260.00 | 7800.00 | 3000.00 | vinayak cooling services
8.00 | Supply and fixing of 40 mm dia CPVC Pipe for drain pipe. Complete with fittings supports, valves, 6 mm thick nitrile rubber insulation as required. | 30.00 | Metre | 0.00 | 400.00 | 12000.00 | 589.00 | 17670.00 | 250.00 | 7500.00 | 400.00 | 12000.00 | 410.00 | 12300.00 | 7500.00 | vinayak cooling services
9.00 | Supply, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
9.10 | For 0.63mm thick | 10.00 | Sqm | 0.00 | 1000.00 | 10000.00 | 960.00 | 9600.00 | 1050.00 | 10500.00 | 1200.00 | 12000.00 | 1315.00 | 13150.00 | 9600.00 | Utility Services
9.20 | For 0.8 mm thick | 10.00 | Sqm | 0.00 | 1100.00 | 11000.00 | 1077.00 | 10770.00 | 1185.00 | 11850.00 | 1300.00 | 13000.00 | 1450.00 | 14500.00 | 10770.00 | Utility Services
9.30 | For 1.0mm thick | 10.00 | Sqm | 0.00 | 1300.00 | 13000.00 | 1303.00 | 13030.00 | 1350.00 | 13500.00 | 1400.00 | 14000.00 | 1585.00 | 15850.00 | 13000.00 | Comfort systems
9.40 | For 1.25 mm thick | 10.00 | Sqm | 0.00 | 1400.00 | 14000.00 | 1510.00 | 15100.00 | 1520.00 | 15200.00 | 1500.00 | 15000.00 | 1790.00 | 17900.00 | 14000.00 | Comfort systems
10.00 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications.
10.10 | GI volume control damper | 3.00 | Sqm | 0.00 | 6000.00 | 18000.00 | 5978.00 | 17934.00 | 7540.00 | 22620.00 | 8000.00 | 24000.00 | 8675.00 | 26025.00 | 17934.00 | Utility Services
11.00 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers (600mmX600mm) | 3.00 | Sqm | 0.00 | 7500.00 | 22500.00 | 9485.00 | 28455.00 | 6900.00 | 20700.00 | 15000.00 | 45000.00 | 12560.00 | 37680.00 | 20700.00 | vinayak cooling services
12.00 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete as required. | 5.00 | Sqm | 0.00 | 5000.00 | 25000.00 | 5374.00 | 26870.00 | 6500.00 | 32500.00 | 5000.00 | 25000.00 | 7150.00 | 35750.00 | 25000.00 | Comfort systems, NAQVI BROTHERS
13.00 | Supplying, Fixing, testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring, the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
13.10 | Fire damper | 3.00 | Sqm | 0.00 | 6900.00 | 20700.00 | 9540.00 | 28620.00 | 6500.00 | 19500.00 | 10000.00 | 30000.00 | 20150.00 | 60450.00 | 19500.00 | vinayak cooling services
13.20 | Actuator | 2.00 | Each | 0.00 | 8000.00 | 16000.00 | 11607.00 | 23214.00 | 8500.00 | 17000.00 | 10000.00 | 20000.00 | 20150.00 | 40300.00 | 16000.00 | Comfort systems
14.00 | Supply & fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m3, with 25 mmX 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with reinforced plastic tissue paper and 0.5 mm thick perforated aluminium sheet fixed to inside surface of ducts with cadmium plated nuts, bolts , stick pins ,CPRX compound etc.complete as required and as per specifications.
14.10 | Acoustic lining of supply air duct and plenum with 25mm thick resin bonded glass wool having density of 32kg/m3 | 30.00 | Sqm | 0.00 | 1200.00 | 36000.00 | 1335.00 | 40050.00 | 2600.00 | 78000.00 | 1000.00 | 30000.00 | 845.00 | 25350.00 | 25350.00 | AirBizz AirConditioning Pvt. Ltd.
15.00 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (class “O”) insulation on existing duct / area under false flooring after applying two coats of cold setting adhesive (CPRX compound). The joints shall sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
15.10 | Nitrile rubber insulation - 19 mm | 200.00 | Sqm | 0.00 | 550.00 | 110000.00 | 717.00 | 143400.00 | 760.00 | 152000.00 | 750.00 | 150000.00 | 755.00 | 151000.00 | 110000.00 | Comfort systems
16.00 | Supply of following capacity 5 Star Inverter technology Split type Air-Conditioner unit fitted with hermetically sealed compressors operating on refrigerant R-410A or equivalent green gas suitable for wall mounting and suitable for operating on 230V +_10%, 50Hz, Single Phase, AC Supply
16.10 | 1.5 TR | 2.00 | Each | 0.00 | 38000.00 | 76000.00 | 34782.00 | 69564.00 | 33984.37 | 67968.74 | 35000.00 | 70000.00 | 47800.00 | 95600.00 | 67968.74 | vinayak cooling services
16.20 | 2 TR | 8.00 | Each | 0.00 | 49000.00 | 392000.00 | 43890.00 | 351120.00 | 42578.00 | 340624.00 | 45000.00 | 360000.00 | 54320.00 | 434560.00 | 340624.00 | vinayak cooling services
17.00 | Supply of Cassette Type Air Conditioner, inside Equipment room with 100% copper condensing unit comprising of sealed twin rotary/Scroll/BLDC type compressor with Inverter Technology and Non CFC refrigerant like R410A suitable for stabilizer free operation at 3ph, 415V , 50Hz AC supply as required of following capacities
17.10 | 3 TR Four way, 4 star rated | 4.00 | Each | 0.00 | 125000.00 | 500000.00 | 80560.00 | 322240.00 | 78515.62 | 314062.50 | 90000.00 | 360000.00 | 141650.00 | 566600.00 | 314062.50 | vinayak cooling services
17.20 | ITC of 3 TR cassette ac including 3 metre refrigerant piping ,drain pipe etc. enclosing in with nitrile rubber insulation including wrapping in white vinyl tape, etc. as required, cabling,related civil works and including first charge of refrigerant &providing & fixing of Iron stand for outdoor unit etc. complete as required. | 4.00 | Job | 0.00 | 5800.00 | 23200.00 | 11331.00 | 45324.00 | 3500.00 | 14000.00 | 3000.00 | 12000.00 | 5850.00 | 23400.00 | 12000.00 | NAQVI BROTHERS
18.00 | ITC of 1.5/2 TR Split airconditioners including 3 metre refrigerant piping,cabling for quantity as per site requirement between condenser and evaporator unit ,enclosing in with nitrile rubber insulation including wrapping in white vinyl tape, etc. as requiredcabling,related civil works and including first charge of refrigerant &providing & fixing of Iron stand for outdoor unit etc. complete as required. | 10.00 | Job | 0.00 | 4000.00 | 40000.00 | 6636.00 | 66360.00 | 1650.00 | 16500.00 | 2000.00 | 20000.00 | 3800.00 | 38000.00 | 16500.00 | vinayak cooling services
19.00 | SITC of extra length of copper pipe for quantity in excess of 3 metres which is already taken in item no. 17 & 18 (suction & discharge together)as per design of OEM between condenser and evaporator unit enclosing in with nitrile rubber insulation including wrapping in white vinyl tape etc. as required
19.10 | For 1.5 TR & 2 TR AC | 30.00 | Metre | 0.00 | 660.00 | 19800.00 | 873.00 | 26190.00 | 740.00 | 22200.00 | 1500.00 | 45000.00 | 960.00 | 28800.00 | 19800.00 | Comfort systems
19.20 | For 3 TR Cassette AC | 30.00 | Metre | 0.00 | 960.00 | 28800.00 | 1264.00 | 37920.00 | 924.00 | 27720.00 | 2500.00 | 75000.00 | 1040.00 | 31200.00 | 27720.00 | vinayak cooling services
20.00 | SITC of extra length of drain pipe for quantity in excess of 3 metres from evaporator to a suitable location for 1.5 TR ,2 TR & 3 TR AC's as per design of OEM etc as required. | 50.00 | Metre | 0.00 | 500.00 | 25000.00 | 98.00 | 4900.00 | 181.00 | 9050.00 | 150.00 | 7500.00 | 320.00 | 16000.00 | 4900.00 | Utility Services
21.00 | Supply of Induction Cook top of 1500 W nominal capacity with push button controls, suitable for single phase 230 volt, 50Hz AC supply etc with all accessories as required. (Make: Philips/Havells/Usha/Bajaj/Prestige) | 1.00 | Each | 0.00 | 2000.00 | 2000.00 | 3895.00 | 3895.00 | 3000.00 | 3000.00 | 3000.00 | 3000.00 | 2200.00 | 2200.00 | 2000.00 | Comfort systems
22.00 | Supply of Stainless Steel 1.5 ltrs nominal capacity electrical kettel of 1500 W ,suitable for single phase 230 volt, 50Hz AC supply etc with all accessories as required. (Make: Philips/Bajaj/Havells/Inalsa) | 1.00 | Each | 0.00 | 1150.00 | 1150.00 | 3339.00 | 3339.00 | 650.00 | 650.00 | 3000.00 | 3000.00 | 1650.00 | 1650.00 | 650.00 | vinayak cooling services
23.00 | Supply & Installation of nominal screen size of 42 inch LED Type Smart TV,suitable for single phase 230 volt, 50Hz AC supply etc with all accessories including DTH connection as required. (Make: Sony/LG/Samsung/Philips) | 1.00 | Each | 0.00 | 35000.00 | 35000.00 | 90720.00 | 90720.00 | 26554.60 | 26554.60 | 30000.00 | 30000.00 | 38500.00 | 38500.00 | 26554.60 | vinayak cooling services
24.00 | Supply of 25 ltr nominal capacity microwaveoven with 3 pin plug top and three core lead of Cu wire as per OEM suitable for single phase 230 volt, 50Hz AC supply etc with all accessories as required. (Make: IFB/LG/Samsung/Panasonic) | 1.00 | Each | 0.00 | 15000.00 | 15000.00 | 17013.00 | 17013.00 | 12500.00 | 12500.00 | 10000.00 | 10000.00 | 13200.00 | 13200.00 | 10000.00 | NAQVI BROTHERS
25.00 | Supply of 183/185 ltr nominal capacity 5 star rated single compartment portable refrigerator with compressor,thermostate,indication with 3 Pin plug top and three core lead of Cu wire as per OEM suitable for single phase 230 volt, 50Hz AC supply etc with all accessories as required. (Make: Whirlpool/LG/Samsung/Godrej) | 1.00 | Each | 0.00 | 29000.00 | 29000.00 | 26076.00 | 26076.00 | 14453.00 | 14453.00 | 25000.00 | 25000.00 | 19935.00 | 19935.00 | 14453.00 | vinayak cooling services
26.00 | Supply and fixing of cyclic timers for 1.5 Tr/2.0 Tr Split Air conditioners for single phase 230 volt, 50Hz AC supply | 4.00 | Each | 0.00 | 12000.00 | 48000.00 | 5724.00 | 22896.00 | 3515.62 | 14062.50 | 2000.00 | 8000.00 | 14000.00 | 56000.00 | 8000.00 | NAQVI BROTHERS
| Total in Figures |  |  |  |  | 3776850.00 |  | 3990930.00 |  | 3486215.34 |  | 3966000.00 |  | 4491000.00
Lowest Amount Quoted BY: vinayak cooling services(3486215.34)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of new stand alone MSSR Building at Maharana Pratap Airport, Udaipur. SH - SITC of Air-conditioning system. Tender ID: 2025_AAI_224543_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | vinayak cooling services (BID ID -817188) | 3486215.34 | L1
| 2 | Comfort systems (BID ID -817003) | 3776850.00 | L2
| 3 | NAQVI BROTHERS (BID ID -817567) | 3966000.00 | L3
| 4 | Utility Services (BID ID -817104) | 3990930.00 | L4
| 5 | AirBizz AirConditioning Pvt. Ltd. (BID ID -812128) | 4491000.00 | L5