## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 24-Feb-2025 03:59 PM Tender Title: Installation of new Stand alone MSSR at Maharana Pratap Airport, Udaipur. SH- SITC of Integrated lightning protection system. Tender ID: 2025_AAI_224549_1
Tender Inviting Authority: SM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: Installation of new Stand alone MSSR at Maharana Pratap Airport , Udaipur SH: SITC of Integrated lightning protection system.
Contract No: AAI/UDR/ENGG(E)/2024-25/MSSR/LPS
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SPRINT INTEGRATED SOLUTIONS PVT LTD (GSTN-NA) BID ID -817485 |  | Nexpo Power Solutions Pvt Ltd (GSTN-NA) BID ID -817587
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 8mm dia Aluminum alloy Solid Round Conductor of material AlMgSi used in air termination system . Cross sectional area of conductor should be 50 mm². Test Parameter: a.Lightning impulse current of 100kA for 10/350 µs b.Electrical resistivity - 0.036 µΩm, Tensile strength - 120 to 240 MPa or N/mm², Salt spray - No Sign of Corrosion. Tested as per IEC 62561-2. (CAPE Type: SRC 8–AL or equivalent) | 210.00 | Mtr | 0.00 | 174.00 | 36540.00 | 265.00 | 55650.00 | 36540.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
2.00 | SITC of SS Holder for 8-10 mm dia Aluminium Solid Round Conductor for horizontal Air terminal on concrete parapet with fixing screws. (CAPE Type: MCH or equivalent) | 180.00 | Nos | 0.00 | 101.00 | 18180.00 | 110.00 | 19800.00 | 18180.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
3.00 | SITC of UV resistance Nylon/PU roof conductor holder for flat roof with concrete block for fixing 8 mm dia Aluminium alloy Solid Round Conductor in the terrace flat surface at every 1 mtr. (CAPE Type: MBPCH8L or equivalent) | 15.00 | Nos | 0.00 | 265.00 | 3975.00 | 130.00 | 1950.00 | 1950.00 | Nexpo Power Solutions Pvt Ltd
4.00 | SITC of Stainless steel Cross Connector for 8 mm dia Aluminium alloy round conductor & 10 mm Copper bonded conductor at cross junction. Test Parameter Salt Spray Test ( IEC 62561-1) - No sign of Corrosion (CAPE Type:CCSS 8-10 or equivalent) | 44.00 | Nos | 0.00 | 405.00 | 17820.00 | 265.00 | 11660.00 | 11660.00 | Nexpo Power Solutions Pvt Ltd
5.00 | SITC of Expansion Piece with connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations.Expansion piece should be consider at every 20 mtr length of straight horizontal air termination and connected at both the end with use of straight connector conductor . Test Parameter: Electrical Resistivity Test-0.036 µΩm Salt Spray Test - No Sign of Corrosion Tested as per IEC 62561-1 (CAPE Type: EPC 8 or equivalent) | 9.00 | Nos | 0.00 | 532.00 | 4788.00 | 530.00 | 4770.00 | 4770.00 | Nexpo Power Solutions Pvt Ltd
6.00 | SITC, of Aluminium Straight connector for interconnecting 8mm Aluminium conductor to meets the requirement of IS/IEC 62305. Test Parameter Electrical Resistivity Test-0.15 µΩm Tested as perIEC 62561-1 (CAPE Type : CJ 8 or equivalent) | 10.00 | Nos | 0.00 | 295.00 | 2950.00 | 230.00 | 2300.00 | 2300.00 | Nexpo Power Solutions Pvt Ltd
7.00 | SITC of air termination rod of 3 mtr length of material AlMgSi of diametre ø 16/10 mm crimped on both the ends (Tappered Type). The rod shall be mounted with stainless steel clamp and fixing accessories . Test Parameter: Mechanical Load Test for individual aluminium alloy rods - 120 to 280 N/mm² Salt Spray Test-No sign of corrosion Tested as per IEC 62561-1&2 (CAPE Type VATW3 or equivalent) | 8.00 | Nos | 0.00 | 5207.00 | 41656.00 | 11465.00 | 91720.00 | 41656.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
8.00 | SITC of air termination rod of 2 mtr length of material AlMgSi of diametre ø 16/10 mm crimped on both the ends ( Tappered one). The rod shall be mounted with concrete stone and fixing accessories. Test Parameter: Mechanical Load Test for individual aluminium alloy rods - 120 to 280 N/mm² Salt Spray Test-No sign of corrosion Tested as per IEC 62561-1&2 (CAPE Type VATF2 or equivalent) | 1.00 | Nos | 0.00 | 6567.00 | 6567.00 | 7500.00 | 7500.00 | 6567.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
9.00 | SITC of Vertical airterminal of 1 mtr with SS stand arrangements to protect the corners and edges of terrace area and to avoid direct strike & side flashes (CAPE Type: VAT P1 or equivalent) | 3.00 | Nos | 0.00 | 3468.00 | 10404.00 | 42000.00 | 126000.00 | 10404.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
10.00 | SITC of Lightnig counter - LCD screen shows the number of lightning strikes, hour and date of lightning events Buttons enable TIME/DATE setting and log viewing.Replaceable battery, working life minimum five years, meet the requirements for IS/IEC 62305 and IEC 62561-2.Tested for Electrical ,Mechanical and Chemical as per IEC 62561. (CAPE Type No. PROLER or equivalent) | 2.00 | Nos | 0.00 | 43367.00 | 86734.00 | 35750.00 | 71500.00 | 71500.00 | Nexpo Power Solutions Pvt Ltd
11.00 | SITC of stainless steel Earth stud of dimension 69 x 69 mm integrated inside concrete and should be tested for electrical resistivity, salt spray and humidity test & short circuit to meet the requirements of IS/IEC 62305 and IEC 62561-1&2. (Cape Type No. ES 1 RA1 or equivalent) | 16.00 | Nos | 0.00 | 1788.00 | 28608.00 | 1650.00 | 26400.00 | 26400.00 | Nexpo Power Solutions Pvt Ltd
12.00 | SITC of connecting point made of stainless steel for terminating 10mm copper conductor. (CAPE Type: CPES 10 or equivalent) | 16.00 | Nos | 0.00 | 413.00 | 6608.00 | 1130.00 | 18080.00 | 6608.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
13.00 | SITC of Aluminuim folding seam conductor holder asper sheet profile for an 8 mm dia aluminium alloy solid round conductor for fixing a horizontal air terminal above the metal sheet to meet the requirements for IS/IEC 62305 and tested as per IEC 62561-4 (CAPE Type : FSCH 14-8 or equivalent) | 10.00 | Nos | 0.00 | 437.00 | 4370.00 | 550.00 | 5500.00 | 4370.00 | SPRINT INTEGRATED SOLUTIONS PVT LTD
14.00 | SITC of 10 mm dia Copper bonded round conductor used for Earth termination inside the concrete and soil. Test parameter: Short circuit current test for copper bonded conductor:Test 6 kA ratings, as per cross sectional area for 1 sec(IS3043/IEEE80); Electrical Resistivity before & after salt mist spray test: 0.25µΩm max. Tensile Test 290 to 510 N/mm². Adhesion no peel or crack & Bend test no seperation of Cu, Cu Coating thickness min. 70µm. Tested as per IEC 62561-2. (CAPE Type : SRC 10 Cu or equivalent) | 505.00 | Mtr | 0.00 | 483.00 | 243915.00 | 300.00 | 151500.00 | 151500.00 | Nexpo Power Solutions Pvt Ltd
15.00 | SITC of Multi conductor Bonding clamp for interconnecting 10 mm Round Conductor with reinforcement rebar at every 3Mtr inside the concrete to meet the requirements of IS/IEC 62305. (CAPE Type: MCBC-101832 or equivalent) | 168.00 | Nos | 0.00 | 344.00 | 57792.00 | 250.00 | 42000.00 | 42000.00 | Nexpo Power Solutions Pvt Ltd
16.00 | SITC of Stainless steel Straight Connector for interconnecting 10 mm dia copper bonded round conductor at straight connection to meets the requirement of IS/IEC 62305. Test Parametres: a) Static Mechanical Test b) Environmental Test Tested as per IEC 62561-1 (CAPE Type: SC 8-10 or equivalent) | 101.00 | Nos | 0.00 | 294.00 | 29694.00 | 230.00 | 23230.00 | 23230.00 | Nexpo Power Solutions Pvt Ltd
17.00 | SITC of stainless steel Earth stud of dimension 69 x 69 mm integrated inside concrete and should be tested for electrical resistivity, salt spray and humidity test & short circuit to meet the requirements of IS/IEC 62305 and IEC 62561-1&2. (Cape Type No. ES 1 RA1 or equivalent) | 16.00 | Nos | 0.00 | 1788.00 | 28608.00 | 1660.00 | 26560.00 | 26560.00 | Nexpo Power Solutions Pvt Ltd
18.00 | SITC of 10 mm dia Copper bonded round conductor used for Earth termination inside the concrete and soil. Test parameter: Short circuit current test for copper bonded conductor:Test 6 kA ratings, as per cross sectional area for 1 sec(IS3043/IEEE80); Electrical Resistivity before & after salt mist spray test: 0.25µΩm max. Tensile Test 290 to 510 N/mm². Adhesion no peel or crack & Bend test no seperation of Cu, Cu Coating thickness min. 70µm. Tested as per IEC 62561-2. (CAPE Type : SRC 10 Cu or equivalent) | 250.00 | Mtr | 0.00 | 454.00 | 113500.00 | 450.00 | 112500.00 | 112500.00 | Nexpo Power Solutions Pvt Ltd
19.00 | SITC of Stainless steel Straight Connector for interconnecting 10 mm dia copper bonded round conductor at straight connection to meets the requirement of IS/IEC 62305. Test Parametres: a) Static Mechanical Test b) Environmental Test Tested as per IEC 62561-1 (CAPE Type: SC 8-10 or equivalent) | 7.00 | Nos | 0.00 | 618.00 | 4326.00 | 235.00 | 1645.00 | 1645.00 | Nexpo Power Solutions Pvt Ltd
20.00 | SITC of Exothermic Welding - Including welding mould and other accessories for welding confirms the requirements of IEEE 837:2014 : T-Joint, X-Joint, L-Joint , Straight joint (CAPE Article: 400 880 or equivalent) | 20.00 | Nos | 0.00 | 4504.00 | 90080.00 | 300.00 | 6000.00 | 6000.00 | Nexpo Power Solutions Pvt Ltd
| Total in Figures |  |  |  |  | 837115.00 |  | 806265.00
Lowest Amount Quoted BY: Nexpo Power Solutions Pvt Ltd(806265.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of new Stand alone MSSR at Maharana Pratap Airport, Udaipur. SH- SITC of Integrated lightning protection system. Tender ID: 2025_AAI_224549_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexpo Power Solutions Pvt Ltd (BID ID -817587) | 806265.00 | L1
| 2 | SPRINT INTEGRATED SOLUTIONS PVT LTD (BID ID -817485) | 837115.00 | L2