## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 25-Feb-2025 05:35 PM Tender Title: Replacement of Perimeter Cables and LED Light Fixtures at B.M.Airport, Ranchi. Tender ID: 2025_AAI_225256_1
Tender Inviting Authority: SM (E-E), AAI, B.M.Airport, Ranchi
Name of Work: Replacement of Perimeter Cables and LED Light Fixtures at B.M.Airport, Ranchi.
Contract No: 2025_AAI_225256_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -820042 |  | Industrial Traders (GSTN-09ACJPC1773F1ZQ) BID ID -820119 |  | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -820207 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -820330 |  | M/s CGPL ELECTROMECH PVT LTD (GSTN-07AAGCC8228F1ZO) BID ID -820496 |  | Shiva Enterprises (GSTN-NA) BID ID -820466 |  | SAURABH ENTERPRISES (GSTN-NA) BID ID -820027 |  | waystone engicon private limited (GSTN-NA) BID ID -819696
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following sizes of aluminium conductor XLPE insulated and PVC sheathed armoured cable conforming to IS 7098(Part-I)1988 with up to date amendments.
1.01 | 3½ X 185sq. mm | 2730.00 | Meter | 850.00 | 809.00 | 2208570.00 | 812.00 | 2216760.00 | 750.00 | 2047500.00 | 875.00 | 2388750.00 | 825.00 | 2252250.00 | 835.00 | 2279550.00 | 870.00 | 2375100.00 | 750.00 | 2047500.00 | 2047500.00 | waystone engicon private limited, M/S AMAR ENTERPRISES
1.02 | 4 X 25 sq. mm | 6972.00 | Meter | 225.00 | 167.00 | 1164324.00 | 160.00 | 1115520.00 | 154.00 | 1073688.00 | 190.00 | 1324680.00 | 195.00 | 1359540.00 | 165.00 | 1150380.00 | 280.00 | 1952160.00 | 170.00 | 1185240.00 | 1073688.00 | M/S AMAR ENTERPRISES
2.00 | Supply of 50 mm dia OD ISI marked HDPE Pipe as per IS :4984:2016 of PE 80 grade and PN 6 rating complete as required. | 6308.00 | Meter | 60.00 | 72.00 | 454176.00 | 64.00 | 403712.00 | 38.00 | 239704.00 | 66.00 | 416328.00 | 55.00 | 346940.00 | 65.00 | 410020.00 | 100.00 | 630800.00 | 65.00 | 410020.00 | 239704.00 | M/S AMAR ENTERPRISES
3.00 | Supply of 110 mm dia OD ISI marked HDPE Pipe as per IS :4984:2016 of PE 80 grade and PN 8 rating complete as required. | 2600.00 | Meter | 288.00 | 330.00 | 858000.00 | 370.00 | 962000.00 | 187.00 | 486200.00 | 384.00 | 998400.00 | 275.00 | 715000.00 | 370.00 | 962000.00 | 430.00 | 1118000.00 | 280.00 | 728000.00 | 486200.00 | M/S AMAR ENTERPRISES
4.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
4.01 | 3½ X 185 sq. mm | 10.00 | Set | 824.00 | 2035.00 | 20350.00 | 828.00 | 8280.00 | 535.00 | 5350.00 | 737.00 | 7370.00 | 550.00 | 5500.00 | 1350.00 | 13500.00 | 500.00 | 5000.00 | 1000.00 | 10000.00 | 5000.00 | SAURABH ENTERPRISES
4.02 | 4 X 25 sq. mm | 664.00 | Set | 313.00 | 715.00 | 474760.00 | 348.00 | 231072.00 | 202.00 | 134128.00 | 340.00 | 225760.00 | 125.00 | 83000.00 | 390.00 | 258960.00 | 350.00 | 232400.00 | 200.00 | 132800.00 | 83000.00 | M/s CGPL ELECTROMECH PVT LTD
5.00 | Supply of LED Street Light fitting having system lumen output not less than 4950 Lumens with system efficacy of not less than 110 lumens per watt, Power Factor≥0.95 & THD<10%, CRI of Min. 70, CCT : 5700K - 6500K, made of high pressure die cast Aluminium/ standard alloy housing , toughened glass protector, operating voltage range 140 – 270V,50 Hz AC supply , surge protection>4KV with minimum IP-65 Protection complete with electronic driver and accessories etc suitable for outdoor applications. LM 79 report to be submitted for luminaire from NABL accredited lab and LM 80 for LED source issued by LED manufacture. | 334.00 | Nos. | 2650.00 | 1155.00 | 385770.00 | 960.00 | 320640.00 | 1520.00 | 507680.00 | 1017.00 | 339678.00 | 1800.00 | 601200.00 | 2500.00 | 835000.00 | 3000.00 | 1002000.00 | 3800.00 | 1269200.00 | 320640.00 | Industrial Traders
6.00 | Supply and Fixing of street light pole Cable Juction Box with locking arrangement and suitabe for outdoor application(min IP 65) containing terminal plate and 4 way heavy duty connector for loop-in loop-out cable termination and suitable for upto 02 Nos 4C X 25sq.mm. cable provision for mounting single pole MCB inside cable junction box alongwith supply and fixing of pole mounting bracket/clamp, incoming & outgoing cable glands, fastnerners etc including neccessary interconnection of wires complete as required.(Make: Hensel or equivalent) | 334.00 | Job | 2346.00 | 1495.00 | 499330.00 | 1440.00 | 480960.00 | 1400.00 | 467600.00 | 2093.00 | 699062.00 | 1200.00 | 400800.00 | 1400.00 | 467600.00 | 4200.00 | 1402800.00 | 900.00 | 300600.00 | 300600.00 | waystone engicon private limited
7.00 | Supply & Fixing of 6A rating, 240/415 V, 10 kA, "C" curve, MCB suitable for inductive load of Double Pole in the existing Street Light Junction Box, connections etc. complete as required. | 334.00 | Each | 583.00 | 633.00 | 211422.00 | 540.00 | 180360.00 | 100.00 | 33400.00 | 565.00 | 188710.00 | 125.00 | 41750.00 | 182.00 | 60788.00 | 135.00 | 45090.00 | 400.00 | 133600.00 | 33400.00 | M/S AMAR ENTERPRISES
8.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel/ Outdoor feeder pillar, IP42 protection in case of indoor panel and IP-54 in case of outdoor feeder pillar, suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 36 KA for 1 sec, bottom base channel of MS section suitable to withold the load of the panel, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with suitable size of PVC insulated copper conductor S/C cable, cable alleys, cable gland plates , i/c providing following switch gears :- All live accessible parts shall be shrouded and all equipment shall be finger touch proof. SMC shrouds busbar supports shall be used. Padlocking facility shall be provided on all MCCB feeder doors and switch handles shall be locakble in OFF position. Sealing Arrangement:- PE Foam Rubber Gasket Bus Bars Supports - Non-Hygroscopic, Non Carbonising, Corrosion Resistant, SMC Supports 1Set of connector (Phase+Neutral) shall be provided in cable alley for all outgoing with interconnection wires between MCB and Connector. Minimum Air Clearances between bus bars; P-P=32mm, P-N=32mm,P-E=26mm and N-E=26mm Panel Power and control Wiring shall be with FRLS PVC insulated cable AC voltage circuit-1.5 sqmm Red,Yellow,Blue &Black Current circuit-1.5 sqmm Red,Yellow,Blue &Black AC Control circuit-1.5 sqmm White for Phase & Black for Neutral DC Control circuit-2.5 sqmm Grey Power circuit- Red,Yellow,Blue for Phase &Black for Neutral Labelling- Computerised Laminated Aluminium Name Plate with White letters on Blue/Black Background For Each Feeder and Panel Itself. All indicating lamps shall be LED type with 2 amp protection MCB All ammeter/ volt meter/MFM shall be digital type of size 96 mm x 96 mm Note: If mentioned fault rating is unavailable consider nearby upside rating Note: All outgoing MCCB shall be with adjustable O/L protection All outgoing MCCB shall have 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. All incomers and Buscoupler breakers shall be electrical and mechanical interlocked with suitable accessories.
8.01 | Main Feeder Pillar Incomer- 2 Nos.250A, 4P MCCB, 25 KA, Microprocessor based release (Ics = Icu = 100%) with inbuilt O/L , S/C & E/F protection with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB Each Incomer shall have one set of the following items: 1 No. Digital MFM meter and 3 nos. CTs of ratio250/5A , Class 0.5 accuracy and 10 VA burden. digital multifunction meter suitable to measure voltage, Ampere, Frequency, Power Factor 1 Set of ON/ OFF/TRIP Indicating LED Lamps with 2 Amp MCB. 1 Set of phase indicating LED lamps with 2 amp back up MCB. Buscoupler 1 No. 250A, 4P MCCB, 25 KA, Microprocessor based release (Ics = Icu = 100%) with inbuilt O/L , S/C & E/F protection with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. Busbars 4P aluminium bus bars of 315 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec. Outgoing 4 Nos. 125 A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu = 25 KA) 2 Nos. 63 A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu = 25 KA) 2 No. 40A 4P MCB C- CURV with built in thermal magnetic release with adjustable thermal setting 2 Nos. Type-C SPD . Contactor with timer ( Astronomical time switch) assembly of suitable rating for On/Off push botton for mannual operation, A/M selector switch.- 01 set | 2.00 | Job | 452093.00 | 454250.00 | 908500.00 | 411221.63 | 822443.26 | 200000.00 | 400000.00 | 158400.00 | 316800.00 | 357500.00 | 715000.00 | 390000.00 | 780000.00 | 20647.00 | 41294.00 | 180000.00 | 360000.00 | 41294.00 | SAURABH ENTERPRISES
8.02 | Outdoor feeder pillar Incomer 1 Nos. 100A, 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu = 25 KA) with inbuilt O/L , S/C & E/F protection with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB Each Incomer shall have one set of the following items: 1 No. Analog ammeter and 1 No. Analog voltmeter 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. 1 Set of phase indicating LED lamps with 2 amp back up MCB. Busbars 4P aluminium bus bars of 125 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec. Outgoing 4 Nos. 63A TPN MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu = 25 KA) 2 Nos. 40A TPN MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu = 25 KA) 1 Nos. Type-C SPD with fuse shall be provided Contactor with timer ( Astronomical time switch) assembly of suitable rating for On/Off push botton for mannual operation, A/M selector switch.- 01 set | 3.00 | Job | 201000.00 | 172500.00 | 517500.00 | 172034.00 | 516102.00 | 160000.00 | 480000.00 | 79300.00 | 237900.00 | 157000.00 | 471000.00 | 140000.00 | 420000.00 | 18000.00 | 54000.00 | 46000.00 | 138000.00 | 54000.00 | SAURABH ENTERPRISES
9.00 | Laying of following Outer dia HDPE pipe along with all accessories like socket, bend , couplers etc. complete with fitting and cutting, jointing etc. direct in ground(75 cm below level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required.
9.01 | 50mm dia | 6308.00 | Meter | 42.00 | 173.00 | 1091284.00 | 96.00 | 605568.00 | 50.00 | 315400.00 | 46.00 | 290168.00 | 15.00 | 94620.00 | 75.00 | 473100.00 | 50.00 | 315400.00 | 70.00 | 441560.00 | 94620.00 | M/s CGPL ELECTROMECH PVT LTD
9.02 | 110mm dia | 2600.00 | Meter | 58.00 | 173.00 | 449800.00 | 120.00 | 312000.00 | 37.00 | 96200.00 | 56.00 | 145600.00 | 20.00 | 52000.00 | 80.00 | 208000.00 | 70.00 | 182000.00 | 160.00 | 416000.00 | 52000.00 | M/s CGPL ELECTROMECH PVT LTD
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE/Masonary Open Duct pipe as required.
10.01 | upto 35 sq mm | 6500.00 | Meter | 34.00 | 58.00 | 377000.00 | 24.00 | 156000.00 | 22.00 | 143000.00 | 74.00 | 481000.00 | 20.00 | 130000.00 | 45.00 | 292500.00 | 20.00 | 130000.00 | 80.00 | 520000.00 | 130000.00 | SAURABH ENTERPRISES, M/s CGPL ELECTROMECH PVT LTD
10.02 | Above 95 sq. mm and upto 185 sq. mm | 2400.00 | Meter | 58.00 | 115.00 | 276000.00 | 36.00 | 86400.00 | 37.00 | 88800.00 | 159.00 | 381600.00 | 25.00 | 60000.00 | 68.00 | 163200.00 | 40.00 | 96000.00 | 170.00 | 408000.00 | 60000.00 | M/s CGPL ELECTROMECH PVT LTD
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
11.01 | upto 35 sq mm | 500.00 | Meter | 52.00 | 58.00 | 29000.00 | 108.00 | 54000.00 | 33.00 | 16500.00 | 71.00 | 35500.00 | 30.00 | 15000.00 | 55.00 | 27500.00 | 20.00 | 10000.00 | 100.00 | 50000.00 | 10000.00 | SAURABH ENTERPRISES
11.02 | Above 95 sq. mm and upto 185 sq. mm | 100.00 | Meter | 129.00 | 115.00 | 11500.00 | 144.00 | 14400.00 | 83.00 | 8300.00 | 143.00 | 14300.00 | 75.00 | 7500.00 | 70.00 | 7000.00 | 40.00 | 4000.00 | 500.00 | 50000.00 | 4000.00 | SAURABH ENTERPRISES
12.00 | Laying of following Outer dia HDPE pipe along with all accessories like socket, bend , couplers etc. complete with fitting and cutting, jointing etc. in cement concrete / bitumen surface i/c cutting cement concrete / bitumen surface and finishing with good surface after laying HDPE pipe etc. as required:
12.01 | 50mm dia | 20.00 | Meter | 211.00 | 690.00 | 13800.00 | 516.00 | 10320.00 | 137.00 | 2740.00 | 920.00 | 18400.00 | 150.00 | 3000.00 | 340.00 | 6800.00 | 200.00 | 4000.00 | 500.00 | 10000.00 | 2740.00 | M/S AMAR ENTERPRISES
12.02 | 110mm dia | 100.00 | Meter | 235.00 | 1035.00 | 103500.00 | 672.00 | 67200.00 | 152.00 | 15200.00 | 1150.00 | 115000.00 | 200.00 | 20000.00 | 400.00 | 40000.00 | 300.00 | 30000.00 | 500.00 | 50000.00 | 15200.00 | M/S AMAR ENTERPRISES
13.00 | Laying of 110 mm Outer dia (PE-80 & PN-8) HDPE pipe through trenchless technology by drilling the bore (HDD) of suitable dia directly in ground upto the depth of 3 meters from the ground level including necessary jointing coupling, splicing etc as required. | 350.00 | Meter | 829.00 | 978.00 | 342300.00 | 360.00 | 126000.00 | 300.00 | 105000.00 | 1380.00 | 483000.00 | 510.00 | 178500.00 | 850.00 | 297500.00 | 425.00 | 148750.00 | 1260.00 | 441000.00 | 105000.00 | M/S AMAR ENTERPRISES
14.00 | Installation, Testing & commissioning of LED type fitting on 6mtr (approx) Octagonal pole i/c wiring with 3C X1.5 sqmm PVC insulated & PVC round sheathed copper conductor cable of suitable length upto loop in loop out box including necessary connection etc complete as required. | 81.00 | Job | 92.00 | 345.00 | 27945.00 | 600.00 | 48600.00 | 59.00 | 4779.00 | 1840.00 | 149040.00 | 50.00 | 4050.00 | 550.00 | 44550.00 | 200.00 | 16200.00 | 500.00 | 40500.00 | 4050.00 | M/s CGPL ELECTROMECH PVT LTD
15.00 | Installation, Testing & commissioning of LED type fitting on 3mtr (approx) Octagonal pole i/c wiring with 3C X2.5 sqmm PVC insulated & PVC round sheathed copper conductor cable of suitable length upto loop in loop out box including necessary connection etc complete as required. | 253.00 | Job | 73.00 | 403.00 | 101959.00 | 600.00 | 151800.00 | 47.00 | 11891.00 | 1610.00 | 407330.00 | 35.00 | 8855.00 | 450.00 | 113850.00 | 200.00 | 50600.00 | 500.00 | 126500.00 | 8855.00 | M/s CGPL ELECTROMECH PVT LTD
16.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories,and providing masonry enclosure with cover plate having locking arrangement andwatering pipe of 2.7 metre long etc. (but without charcoal/ coke and salt ) as required. | 8.00 | Each | 4424.00 | 10350.00 | 82800.00 | 9600.00 | 76800.00 | 4000.00 | 32000.00 | 13786.00 | 110288.00 | 3000.00 | 24000.00 | 11500.00 | 92000.00 | 7500.00 | 60000.00 | 10000.00 | 80000.00 | 24000.00 | M/s CGPL ELECTROMECH PVT LTD
17.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 200.00 | Meter | 657.00 | 633.00 | 126600.00 | 660.00 | 132000.00 | 427.00 | 85400.00 | 283.00 | 56600.00 | 220.00 | 44000.00 | 550.00 | 110000.00 | 470.00 | 94000.00 | 100.00 | 20000.00 | 20000.00 | waystone engicon private limited
18.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Meter | 246.00 | 144.00 | 7200.00 | 192.00 | 9600.00 | 159.00 | 7950.00 | 226.00 | 11300.00 | 135.00 | 6750.00 | 250.00 | 12500.00 | 125.00 | 6250.00 | 100.00 | 5000.00 | 5000.00 | waystone engicon private limited
19.00 | Earthing with GI pipe 4.5 mtr long X40 mm dia including accessories, and providing masnory enclosure with cover plate having locking arrangement and watering pipe etc.(with charcoal or coke and salt) complete as required. | 30.00 | Each | 5043.00 | 9200.00 | 276000.00 | 8640.00 | 259200.00 | 3277.00 | 98310.00 | 5085.00 | 152550.00 | 4500.00 | 135000.00 | 8000.00 | 240000.00 | 5500.00 | 165000.00 | 12000.00 | 360000.00 | 98310.00 | M/S AMAR ENTERPRISES
20.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 200.00 | Meter | 267.00 | 92.00 | 18400.00 | 456.00 | 91200.00 | 100.00 | 20000.00 | 22.00 | 4400.00 | 145.00 | 29000.00 | 395.00 | 79000.00 | 150.00 | 30000.00 | 100.00 | 20000.00 | 4400.00 | Instapower Ltd
21.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required | 200.00 | Meter | 65.00 | 35.00 | 7000.00 | 60.00 | 12000.00 | 20.00 | 4000.00 | 21.00 | 4200.00 | 35.00 | 7000.00 | 23.00 | 4600.00 | 25.00 | 5000.00 | 100.00 | 20000.00 | 4000.00 | M/S AMAR ENTERPRISES
22.00 | Providing and laying of 6 SWG dia G.I. wire on the existing HDPE/GI/DWC Pipe etc as required | 7500.00 | Meter | 87.00 | 35.00 | 262500.00 | 36.00 | 270000.00 | 10.00 | 75000.00 | 20.00 | 150000.00 | 10.00 | 75000.00 | 23.00 | 172500.00 | 20.00 | 150000.00 | 15.00 | 112500.00 | 75000.00 | M/S AMAR ENTERPRISES, M/s CGPL ELECTROMECH PVT LTD
23.00 | Dismantling of existing Street light Fitting from the Street Light Pole of upto 7 Mtrs Height and shifting it to AAI Stores complete as required | 334.00 | Each | 174.00 | 805.00 | 268870.00 | 36.00 | 12024.00 | 20.00 | 6680.00 | 115.00 | 38410.00 | 40.00 | 13360.00 | 285.00 | 95190.00 | 400.00 | 133600.00 | 400.00 | 133600.00 | 6680.00 | M/S AMAR ENTERPRISES
24.00 | Dismantling of existing LT panel available at Operational area of Ranchi Airport including disconnection & dismantling of control and power cabling, earthing etc, disassembling the Panel from the PCC/metal structure alongwith shifting and transporting of LT Panel to AAI Stores etc and handing over the same to AAI, complete as arequired and as per the instructions of the Engineer-In-Charge.
24.01 | Main Feeder Pillar (Incomer upto 250 A) | 1.00 | Job | 5808.00 | 3450.00 | 3450.00 | 2401.00 | 2401.00 | 3000.00 | 3000.00 | 5750.00 | 5750.00 | 2000.00 | 2000.00 | 7500.00 | 7500.00 | 15000.00 | 15000.00 | 500.00 | 500.00 | 500.00 | waystone engicon private limited
24.02 | Sub-Feeder Pillar (Incomer upto 100 A) | 4.00 | Job | 4065.00 | 2300.00 | 9200.00 | 1920.00 | 7680.00 | 2000.00 | 8000.00 | 5750.00 | 23000.00 | 1500.00 | 6000.00 | 6000.00 | 24000.00 | 10000.00 | 40000.00 | 500.00 | 2000.00 | 2000.00 | waystone engicon private limited
25.00 | Dismantling the existing upto 9 m perimeter pole from the existing location etc as required. | 173.00 | Job | 520.00 | 1725.00 | 298425.00 | 360.00 | 62280.00 | 300.00 | 51900.00 | 575.00 | 99475.00 | 250.00 | 43250.00 | 750.00 | 129750.00 | 500.00 | 86500.00 | 1000.00 | 173000.00 | 43250.00 | M/s CGPL ELECTROMECH PVT LTD
26.00 | ITC of existing pole upto 9 m high with all accessories and supply & making foundation of reinforced cement concrete 1:3:6 (1 cement :3 coarse sand : 6 graded stone aggregate 40mm nominal size) including excavation and refilling, including positioning of template & foundations bolts complete as required and as per technical specification and as per direction of EIC. | 173.00 | Job | 3200.00 | 5175.00 | 895275.00 | 2641.00 | 456893.00 | 1400.00 | 242200.00 | 6325.00 | 1094225.00 | 2400.00 | 415200.00 | 3200.00 | 553600.00 | 4500.00 | 778500.00 | 3800.00 | 657400.00 | 242200.00 | M/S AMAR ENTERPRISES
27.00 | Providing & fixing pole arm made of 32/40 mm dia. GI pipe a suitable for existing pole i/c clamping etc. as reuired as per direction of EIC. | 70.00 | Job | 1150.00 | 748.00 | 52360.00 | 1080.00 | 75600.00 | 400.00 | 28000.00 | 1048.00 | 73360.00 | 800.00 | 56000.00 | 650.00 | 45500.00 | 500.00 | 35000.00 | 1000.00 | 70000.00 | 28000.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 12834870.00 |  | 10357815.26 |  | 7345500.00 |  | 11487934.00 |  | 8422065.00 |  | 10877938.00 |  | 11444444.00 |  | 10922520.00
Lowest Amount Quoted BY: M/S AMAR ENTERPRISES(7345500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Perimeter Cables and LED Light Fixtures at B.M.Airport, Ranchi. Tender ID: 2025_AAI_225256_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S AMAR ENTERPRISES (BID ID -820207) | 7345500.00 | L1
| 2 | M/s CGPL ELECTROMECH PVT LTD (BID ID -820496) | 8422065.00 | L2
| 3 | Industrial Traders (BID ID -820119) | 10357815.26 | L3
| 4 | Shiva Enterprises (BID ID -820466) | 10877938.00 | L4
| 5 | waystone engicon private limited (BID ID -819696) | 10922520.00 | L5
| 6 | SAURABH ENTERPRISES (BID ID -820027) | 11444444.00 | L6
| 7 | Instapower Ltd (BID ID -820330) | 11487934.00 | L7
| 8 | Yash Energy Pvt. Ltd (BID ID -820042) | 12834870.00 | L8