## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 11-Mar-2025 01:07 PM Tender Title: Installation of new stand alone MSSR at Maharana Pratap Airport, Udaipur. SH- SITC of Gas based Fire Suppression System and Fire Detection and Alarm System Tender ID: 2025_AAI_225449_1
Tender Inviting Authority: SM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: Installation of new stand alone MSSR at Maharana Pratap Airport, Udaipur. SH: SITC of Gas based Fire Suppression System & Fire Detection and Alarm System.
Contract No: AAI/UDR/ENGG(E)/2024-25/MSSR/FSS
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -818297 |  | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -820017 |  | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -821198 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -821258 |  | Vasu Infosec Pvt Ltd (GSTN-27AABCV6080D1ZE) BID ID -821589
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of automatic fire gas (FK-5-1-12), at 4.5% design concentration, flooding system comprising of the following as per NFPA 2001 & Up to date amended standards including providing and fixing of Class-C heavy duty M.S. seamless pipe ASTM A-106(Sch 40) complete with all fittings painting with one coat of red oxide and 2 coats of enamel paint; piping to be fixed on ceiling with MS suspended supports, clamps anchor fastners, cutting chases / holes in valve ceiling and making good the same as required,piping sizes shall be as per flow calculation and as per site requirment and complete as per tender specifications.
1.10 | Seamless storage 80L cylinder suitable for FK-5-1-12 fire suppresion fluid with complete valve assembly, pressure gauge with all safety features and pressure switch and other standard accessories including cylinder strap. (Cylinders Shall Be UL listed & PESO Approved). | 3.00 | Each | 0.00 | 157000.00 | 471000.00 | 127577.00 | 382731.00 | 159780.00 | 479340.00 | 161040.00 | 483120.00 | 150650.00 | 451950.00 | 382731.00 | Nexus Fire And Security Systems
1.20 | Seamless storage 120L suitable for FK-5-1-12 fire suppresion fluid with complete valve assembly, pressure gauge with all safety features and other standard accessories including cylinder strap. (Cylinders Shall Be UL listed & PESO Approved). | 2.00 | Each | 0.00 | 170000.00 | 340000.00 | 134696.00 | 269392.00 | 171780.00 | 343560.00 | 180950.00 | 361900.00 | 167050.00 | 334100.00 | 269392.00 | Nexus Fire And Security Systems
1.30 | Seamless storage 140L suitable for FK-5-1-12 fire suppresion fluid with complete valve assembly, pressure gauge with all safety features and other standard accessories including cylinder strap. (Cylinders Shall Be UL listed & PESO Approved). | 3.00 | Each | 0.00 | 170000.00 | 510000.00 | 137295.00 | 411885.00 | 175740.00 | 527220.00 | 195800.00 | 587400.00 | 172050.00 | 516150.00 | 411885.00 | Nexus Fire And Security Systems
2.00 | Supply & filling of clean, odourless, colour less, UL listed and suitable for fire class - A, B & C fire suppression agent (FK-5-1-12 fire suppresion fluid) for item no 1. etc. complete as per tender specification, as per site requirment .( Gas shall be UL Listed and Chromatography Report is required). | 700.00 | Kg | 0.00 | 1500.00 | 1050000.00 | 1790.00 | 1253000.00 | 1750.00 | 1225000.00 | 2310.00 | 1617000.00 | 1500.00 | 1050000.00 | 1050000.00 | advent electric technologies pvt. ltd., Vasu Infosec Pvt Ltd
3.00 | Supply, Installation, Testing and commissioning of single loop intelligent addressable panel with 24 hour battery backup having modbus/ backnet facility to connect with graphic software confirming to UL/EN54 and suitable for connecting all the devices including detectors of MSSR building and antenna room. | 1.00 | Each | 0.00 | 70000.00 | 70000.00 | 71000.00 | 71000.00 | 57600.00 | 57600.00 | 111100.00 | 111100.00 | 205500.00 | 205500.00 | 57600.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
4.00 | Supply, Installation, Testing & Commissioning of Electrical cum Manual actuator to operate the gas manually from the cylinder with all accessories complete as per tender specification and as per site requirment. | 5.00 | Each | 0.00 | 18000.00 | 90000.00 | 32000.00 | 160000.00 | 16800.00 | 84000.00 | 40910.00 | 204550.00 | 14927.00 | 74635.00 | 74635.00 | Vasu Infosec Pvt Ltd
5.00 | Supply, Installation, Testing & Commissioning of Pneumatic actuator valve 1.2bar-6bar 24V or 230V AC for triggering the cylinder assembly complete as requirement complete as per tender specification and as per site requirment. | 3.00 | Each | 0.00 | 6000.00 | 18000.00 | 20000.00 | 60000.00 | 9520.00 | 28560.00 | 13970.00 | 41910.00 | 14827.00 | 44481.00 | 18000.00 | advent electric technologies pvt. ltd.
6.00 | Supply, Installation, Testing & Commissioning of High pressure flexible rubber discharge hose with braided reinforcement to route the FK 5-1-12 gas from storage cylinders to the discharge piping complete as required & as per technical specification (shall be UL listed). | 8.00 | Each | 0.00 | 6000.00 | 48000.00 | 6500.00 | 52000.00 | 14000.00 | 112000.00 | 28600.00 | 228800.00 | 13160.00 | 105280.00 | 48000.00 | advent electric technologies pvt. ltd.
7.00 | Supply, Installation, Testing & Commissioning of Discharge nozzles designed to provide the proper flow and distribution of gas to flood hazard area at - 360 degrees/as per tender specification and as per site requirment (shall be UL listed). | 18.00 | Each | 0.00 | 3000.00 | 54000.00 | 3540.00 | 63720.00 | 5500.00 | 99000.00 | 6710.00 | 120780.00 | 8100.00 | 145800.00 | 54000.00 | advent electric technologies pvt. ltd.
8.00 | Supply, Installation, Testing & Commissioning of Gas discharge pressure switch to trip A.C., electrical equip. etc for FK 5-1-12 System complete as per tender specification and as per site requirment (shall be UL listed). | 5.00 | Each | 0.00 | 6800.00 | 34000.00 | 11500.00 | 57500.00 | 9120.00 | 45600.00 | 22275.00 | 111375.00 | 21430.00 | 107150.00 | 34000.00 | advent electric technologies pvt. ltd.
9.00 | Supply, Installation, Testing & Commissioning of Manifold check valve to permit removal of individual FM storage cylinders as per requirement for FK 5-1-12 System complete as per tender specification and as per site requirment (shall be UL listed). | 2.00 | Each | 0.00 | 7200.00 | 14400.00 | 11700.00 | 23400.00 | 9950.00 | 19900.00 | 34210.00 | 68420.00 | 22450.00 | 44900.00 | 14400.00 | advent electric technologies pvt. ltd.
10.00 | Supply, Installation, Testing & Commissioning of Manual gas release station having manual break glass push button type call points with auxiliary contacts, hammer etc for FK 5-1-12 System complete as per tender specification and as per site requirment. | 5.00 | Each | 0.00 | 1100.00 | 5500.00 | 1200.00 | 6000.00 | 3540.00 | 17700.00 | 3025.00 | 15125.00 | 4200.00 | 21000.00 | 5500.00 | advent electric technologies pvt. ltd.
11.00 | Supply, Installation, Testing & Commissioning of Manual gas abort station having manual break glass push button type call points with auxiliary contacts, hammer gland etc for FK 5-1-12 System complete as per tender specification and as per site requirment. | 5.00 | Each | 0.00 | 1100.00 | 5500.00 | 1200.00 | 6000.00 | 3540.00 | 17700.00 | 3025.00 | 15125.00 | 4200.00 | 21000.00 | 5500.00 | advent electric technologies pvt. ltd.
12.00 | Supply, Installation, Testing & Commissioning of Hooter cum strobe having min 80DB sound type for FK 5-1-12 System complete as per tender specification and as per site requirment. | 5.00 | Each | 0.00 | 600.00 | 3000.00 | 1500.00 | 7500.00 | 3320.00 | 16600.00 | 2310.00 | 11550.00 | 4200.00 | 21000.00 | 3000.00 | advent electric technologies pvt. ltd.
13.00 | Supply, Installation, Testing & Commissioning of Fire Alarm Gas release panel with built in time relay, auto/manual selector switch, housed in a suitable 16 SWG M.S. Sheet panel for succesful auto operation of FK 5-1-12 System during fire condition. ) Audio / Visual indications by dual lamps LED's for fire and fault in each zone with lamp test facility. The control panel shall be provided with standby power supply of 2 x 12 volts, 7 AH sealed maintenance free batteries complete with circuit wiring etc., as per IS : 2189 & uptodate Amendment and have Provision for testing each circuit separately including resetting complete as per tender specification and as per site requirment. | 5.00 | Each | 0.00 | 18000.00 | 90000.00 | 14200.00 | 71000.00 | 39000.00 | 195000.00 | 28050.00 | 140250.00 | 23250.00 | 116250.00 | 71000.00 | Nexus Fire And Security Systems
14.00 | Supply, installation, testing and commissioning of Autodialer suitable for interfacing with Fire Alarm Panel with complete programming complete as required. | 1.00 | Each | 0.00 | 3000.00 | 3000.00 | 9500.00 | 9500.00 | 16250.00 | 16250.00 | 9075.00 | 9075.00 | 14550.00 | 14550.00 | 3000.00 | advent electric technologies pvt. ltd.
15.00 | Supplying, installation , testing and commissioning of addressable multisensor type smoke detector, conforming to UL/LPCB/FMI/EN-54, with all accessories viz : indicator, base, base box etc. to be installed on ceiling / false ceiling etc. complete as per site requirment. | 30.00 | Each | 0.00 | 2200.00 | 66000.00 | 2210.00 | 66300.00 | 2540.00 | 76200.00 | 3025.00 | 90750.00 | 2700.00 | 81000.00 | 66000.00 | advent electric technologies pvt. ltd.
16.00 | Supplying, installation , testing and commissioning of conventional multisensor type smoke detector, conforming to UL/LPCB/FMI/EN-54, with all accessories viz : indicator, base, base box etc. to be installed on ceiling / false ceiling etc. complete as per site requirment. | 15.00 | Each | 0.00 | 1200.00 | 18000.00 | 1200.00 | 18000.00 | 2540.00 | 38100.00 | 1540.00 | 23100.00 | 1125.00 | 16875.00 | 16875.00 | Vasu Infosec Pvt Ltd
17.00 | Supply , Installation & comissioning of Monitor Module or Single Input Module for tripping confirming to UL/LPCB/EN-54. | 5.00 | Each | 0.00 | 3400.00 | 17000.00 | 2850.00 | 14250.00 | 4490.00 | 22450.00 | 3510.00 | 17550.00 | 2650.00 | 13250.00 | 13250.00 | Vasu Infosec Pvt Ltd
18.00 | Supply , Installation & comissioning of addressable Fire Control Relay Module for tripping confirming to UL/LPCB/EN-54. | 2.00 | Each | 0.00 | 4000.00 | 8000.00 | 3450.00 | 6900.00 | 3370.00 | 6740.00 | 3905.00 | 7810.00 | 2700.00 | 5400.00 | 5400.00 | Vasu Infosec Pvt Ltd
19.00 | Supply , Installation & comissioning of Addressable Hooter cum strobe confirming to UL/LPCB/EN-54. | 2.00 | Each | 0.00 | 3400.00 | 6800.00 | 3900.00 | 7800.00 | 3970.00 | 7940.00 | 5885.00 | 11770.00 | 5500.00 | 11000.00 | 6800.00 | advent electric technologies pvt. ltd.
20.00 | Supply, Installation, Testing & Commissioning of addressable Manual call point station having manual break glass with auxiliary contacts, hammer gland etc for System complete as per tender specification, as per site requirment confirming to UL/LPCB/EN54. | 2.00 | Each | 0.00 | 2600.00 | 5200.00 | 3900.00 | 7800.00 | 3240.00 | 6480.00 | 4510.00 | 9020.00 | 3500.00 | 7000.00 | 5200.00 | advent electric technologies pvt. ltd.
21.00 | Supply and laying of PVC insulated, PVC sheathed, FRLS armored copper conductor of cable as per IS 1554- Part- I of size 2x1.5 sq. mm complete as per site requirment. | 700.00 | Mtr | 0.00 | 140.00 | 98000.00 | 112.00 | 78400.00 | 110.00 | 77000.00 | 125.00 | 87500.00 | 186.00 | 130200.00 | 77000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
22.00 | Supply & Fixing ISI marked (IS:2878) Portable fire Extinguisher, Carbon-dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307-1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 4.5 Kg. | 10.00 | Each | 0.00 | 4500.00 | 45000.00 | 4800.00 | 48000.00 | 5760.00 | 57600.00 | 5610.00 | 56100.00 | 5250.00 | 52500.00 | 45000.00 | advent electric technologies pvt. ltd.
23.00 | Supply, installation, testing and commisioning of loop isolators to protect one area or a number of devices with complete set to be installed under and above false ceiling, roof, conceled space, wall, etc. interconnecting to loop cable complete as required. | 5.00 | Each | 0.00 | 1050.00 | 5250.00 | 4200.00 | 21000.00 | 1410.00 | 7050.00 | 3245.00 | 16225.00 | 2650.00 | 13250.00 | 5250.00 | advent electric technologies pvt. ltd.
24.00 | Supply, installation, testing and commissioning of Response Indicator for all detectors located above false ceiling with GI Junction box, screws, cable end terminations, lugs, ferruls, other hardwares etc. complete as per technical specifications. | 10.00 | Each | 0.00 | 1050.00 | 10500.00 | 110.00 | 1100.00 | 100.00 | 1000.00 | 150.00 | 1500.00 | 250.00 | 2500.00 | 1000.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 3086150.00 |  | 3174178.00 |  | 3585590.00 |  | 4448805.00 |  | 3606721.00
Lowest Amount Quoted BY: advent electric technologies pvt. ltd.(3086150.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of new stand alone MSSR at Maharana Pratap Airport, Udaipur. SH- SITC of Gas based Fire Suppression System and Fire Detection and Alarm System Tender ID: 2025_AAI_225449_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | advent electric technologies pvt. ltd. (BID ID -818297) | 3086150.00 | L1
| 2 | Nexus Fire And Security Systems (BID ID -820017) | 3174178.00 | L2
| 3 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -821198) | 3585590.00 | L3
| 4 | Vasu Infosec Pvt Ltd (BID ID -821589) | 3606721.00 | L4
| 5 | Yash Energy Pvt. Ltd (BID ID -821258) | 4448805.00 | L5