## BoQ1
Government eProcurement System Created By: Pushkar Pagnis Created Date/Time: 07-Apr-2025 06:54 PM Tender Title: Augmentation of 33 KV HT Power Supply System for Incomer side at Devi Ahilya Bai Holkar Airport, Indore Tender ID: 2025_AAI_226274_1
Tender Inviting Authority: <Asst.General Manager (Engg.-E), AAI, DABH Airport, Indore.>
Name of Work: <Augmentation of 33KV HT power supply system for incomer side at DABH Airport, Indore >
Contract No: <Tender ID No. 2025_AAI_226274_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -825034 |  | RASS CONTRACTOR AND ENGINEERS (GSTN-09AFIPR1600N1Z7) BID ID -825450 |  | S.L. ELECTROMECH PVT. LTD. (GSTN-07AAACR1317E2ZW) BID ID -825724 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -825885 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -825919 |  | SAPPHIRE ENGINEERS (GSTN-NA) BID ID -825882 |  | Shiva Enterprises (GSTN-NA) BID ID -825458 |  | VASUDEV ELECTRICAL SYSTEMS PVT. LTD. (GSTN-NA) BID ID -825612
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following sizes of XLPE insulated PVC sheathed aluminium conductor armoured power cable of (33KV) grade ((33KV) ( Unearthed for 33 KV ) conforming to IS: 7098 (Part-II) amended upto date. 3Cx300 Sq.mm. | 600.00 | Meter | 100.00 | 2500.00 | 1500000.00 | 3350.00 | 2010000.00 | 3208.00 | 1924800.00 | 2390.00 | 1434000.00 | 2543.00 | 1525800.00 | 2750.00 | 1650000.00 | 2800.00 | 1680000.00 | 3000.00 | 1800000.00 | 1434000.00 | Awasthi Electric Works
2.00 | Supplying of following sizes of HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:1985, PE 100 grade, PN10 rating complete as required. 160 mm dia (OD) | 650.00 | Meter | 100.00 | 900.00 | 585000.00 | 395.00 | 256750.00 | 843.00 | 547950.00 | 790.00 | 513500.00 | 745.00 | 484250.00 | 1150.00 | 747500.00 | 735.00 | 477750.00 | 500.00 | 325000.00 | 256750.00 | RASS CONTRACTOR AND ENGINEERS
3.00 | Laying of 160 MM outer dia PE-100 grade PN 10 rated HDPE pipe in ground upto 3 mtr depth as per site requirement through Hard Soil- HDD(Horizontal drillinbg ) method including joints by welding ,fixing necessary accessories like end plugs etc. ,providing suitable pull wire(without cable pulling) for pulling cables as required | 536.00 | Meter | 10.00 | 800.00 | 428800.00 | 2450.00 | 1313200.00 | 1205.00 | 645880.00 | 890.00 | 477040.00 | 5460.00 | 2926560.00 | 2551.00 | 1367336.00 | 650.00 | 348400.00 | 450.00 | 241200.00 | 241200.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
4.00 | Laying of 160 MM outer dia PE-100 grade PN 10 rated HDPE pipe complete with all accessories like socket, bend couplers etc., cutting, jointing etc. Direct in ground (80 cm below ground level and 1.0 Mtr below pavement wherever road crossing/proposed road crossing) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 108.00 | Meter | 10.00 | 300.00 | 32400.00 | 225.00 | 24300.00 | 241.00 | 26028.00 | 400.00 | 43200.00 | 137.00 | 14796.00 | 250.00 | 27000.00 | 250.00 | 27000.00 | 200.00 | 21600.00 | 14796.00 | SARASWAT ENGINEERING SERVICES
5.00 | Laying of one number XLPE power cable of 33kV grade of following size in existing RCC/HUME/METAL/HDPE pipe as required Above 120 sqmm and upto 400 sqmm | 528.00 | Meter | 10.00 | 120.00 | 63360.00 | 150.00 | 79200.00 | 181.00 | 95568.00 | 140.00 | 73920.00 | 137.00 | 72336.00 | 250.00 | 132000.00 | 180.00 | 95040.00 | 200.00 | 105600.00 | 63360.00 | DOSHI ELECTRIC ENGG. CO.
6.00 | Laying of one number XLPE power cable of 33kV grade of following size in existing masonry open duct as required. Above 120 sqmm and upto 400 sqmm | 48.00 | Meter | 10.00 | 100.00 | 4800.00 | 150.00 | 7200.00 | 181.00 | 8688.00 | 135.00 | 6480.00 | 137.00 | 6576.00 | 250.00 | 12000.00 | 160.00 | 7680.00 | 200.00 | 9600.00 | 4800.00 | DOSHI ELECTRIC ENGG. CO.
7.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33KV grade as required : 3Cx300 Sqmm | 8.00 | Sets | 10.00 | 10000.00 | 80000.00 | 18500.00 | 148000.00 | 10783.00 | 86264.00 | 21000.00 | 168000.00 | 11201.00 | 89608.00 | 19500.00 | 156000.00 | 22500.00 | 180000.00 | 18000.00 | 144000.00 | 80000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Supply, Installation, Testing & Commissioning of indoor type (IP 4X) floor mounted metal clad, 33kV Switch Board VCB panel with 5 Nos. VCBs(2 I/C+ 2 O/C+1 B/C), totally enclosed & fully interlocked, truck mounting, horizontal draw out, horizontal isolation type vacuum breaker as per IS / IEC 62271-100 (2007) for breakers & 200 (2003),for panels / IS3247 as amended up to date, having capacities as mentioned below, free standing extensible on both sides, single break, trip free mechanism, motorised charged and auto/ annually closing breaker suitable for use on 33kV , 3 Phase, 50Hz A.C. supply with short circuit fault level of 1500 MVA, complete with self contained short time current 26.3 kA for 3 sec, Internal Arc Test for AFLR 26.3 kA for 1 sec at individual compartments i.e. busbar, VCB, and cable compartment, rack in and rack out mechanism, air insulated but encapsulated copper bus bars capacity meeting fault level current , DC power pack, breaker featured with mechanical ON / OFF indicator with and trip device, reaker control TNC switch and all accessories such as shunt trip coil, and auxiliary switch of 4NO+4NC, motorised and annually operated spring assisted closing mechanism, emergency trip push button, interconnections, space heaters, earthing, etc. and equipped with following switchgears and accessories, connections suitable for cable upto 3C x 300 sqmm XLPE cable of 33kV grade (cable entry from bottom), Separate earthing switch shall be provided for Cable earthing . The earthing truck shall be so designed that it is impossible to earth a live. cable terminations suitable for 3C x 300 sq.mm. XLPE 33kV cable A. Incomer 2 Nos. each consisting of following; 1 No. of 1250 Amp , 33kV, 3 Ph, 3P VCB 1 No - Multifunction Meter with accuracy class 0.5 LED display of I ,V, Hz, Active, Reactive , Apparent Power & Energy, Power factor, %THD , Maximum demand load, (complying with IEC61557-12) with RS 485 & Ethernet port and protection MCB and required accessories to complete the system 3 No. Cast resin drawout type PTs 33kV / √3 / 110 √3, class 0.5,100 VA burden including HT HRC fuse on 33kV Side and MCBs on secondary side protection. 3 No. Cast resin insulated Dual core 3 CTs 30 / 5-5A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. Aux. relays for Anti Pumping & indication. Trip Circuit supervision relay '- Master Trip Circuit Relay 1 No. Micro processor based over current, short circuit 50,50 N & earth fault numerical IDMT relay with having RS 485 modbus communication facility consisting 3 element for over current relay and one earth fault capable of storing last 10 trip history. 1 No. Over & under voltage protection relay 1 No. Over & under frequency relay 1 No. Alarm annunciator with minimum 8 windows and buzzer, ACK, rest, test push button for transformer faults and electrical faults in respective window B. Busbar 1250 Amps TP, 36kV Copper Bus bar with heat shrinkable insulated sleeves with cast epoxy insulator to withstand full short circuit currents upto 26.3 kA for 1 second. | 1.00 | Job | 10.00 | 5285000.00 | 5285000.00 | 6850000.00 | 6850000.00 | 5060241.00 | 5060241.00 | 5250000.00 | 5250000.00 | 4777500.00 | 4777500.00 | 4786000.00 | 4786000.00 | 5500000.00 | 5500000.00 | 7850000.00 | 7850000.00 | 4777500.00 | SARASWAT ENGINEERING SERVICES
9.00 | C. BUS COUPLER 1250 Amps., 33kV horizontal draw out type VCB with motorized spring charge mechanism, T/N/C switch and required safety switchgears complete. 1 Set of LED indication lamp protected by MCB for ON & OFF and spring charge of breaker complete Electrical interlocking with both incomers & bus coupler D. Outgoings 2 Nos EACH consisting of following; 1 No. 1250 Amp., 33kV VCB horizontal draw out type VCB with motorized spring charge mechanism, T/N/C switch and required safety switchgears complete Aux. relays for Anti Pumping & indication. Trip Circuit supervision relay '- Master Trip Circuit Relay 1 No. Micro processor based over current, short circuit 50,50 N & earth fault numerical IDMT relay with having RS 485 modbus communication facility consisting 3 element for over current relay and one earth fault capable of storing last 10 trip history 1 No - Multifunction Meter with LED display of I ,V, Hz, Active, Reactive , Apparent Power & Energy, Power factor, % %THD , Maximum demand, (complying with IEC61557-12) with RS 485 & Ethernet port and protection MCB and required accessories to complete the system. 3 No. Cast resin insulated Dual core 3 CTs 30/5-5A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. E. All I/C & O/G Breaker have following Accessories & indication 6A MCB for spring charge, DC Control Supply healthy & fails, Surge Arrestor of type 1,33kV grade shall be provided for all phases of each incomer, AC Supply control ON/OFF Switch, Circuit breaker failure Alarm indication , VCB spring charge indication, LED Illumination lamp ON / OFF with limit Switch, T-N-C (Trip, Neutral, Close) breaker control switch with indication arrangement., All control wiring with protection & test terminal block as required., Emergency trip push button, 2A MCB for lamp, 60 watts space heater with thermostat, 16 Amp MCB for space heater and plug point, 6/16 Amps 5 Pin with piano type switch socket outlet, Supply, fixing, testing and commissioning of automatic linear pneumatic tube Detection based Clean agent System for Electrical Panels (Linear Pnuematic Heat Detection tube Panel Protection System), consisting of the Mentioned components, Suitable capacity , Direct Low Pressure (DLP) Assembly with automatic valve, push in connector for tube, Clean agent, mounting bracket, End of Line adopter and low pressure switch for monitoring system activation. i) Linear Pneumatic Heat detection tube with all necessary & supports ii) Master Control Unit for controlling each system, complete with pressure switches, buzzers and electronic hooters, including all necessary accessories + electrical wiring to make each entire system functional.
10.00 | Single Input Double output, Outdoor type IP 54, 33 KV RMU Unit 630A, non-extendable Type Scope: - Design, engineering, manufacture, assembly, stage testing, inspection and testing before supply and delivery at site, storing, erection, installation, testing, commissioning, including cable termination and handing over of motorized, non-extensible, outdoor type Ring Main Units (RMUs) with 1 CB + 2 LBS with cable termination kits, terminal protectors, current transformers, Potential transformer, protection relays, and with metering facility for breakers, complete with all materials and accessories, spares etc. ( except plinth, excavation, earthing ). | 1.00 | Job | 10.00 | 3500000.00 | 3500000.00 | 4250000.00 | 4250000.00 | 2168675.00 | 2168675.00 | 3130000.00 | 3130000.00 | 2323464.00 | 2323464.00 | 2260000.00 | 2260000.00 | 2700000.00 | 2700000.00 | 3100000.00 | 3100000.00 | 2168675.00 | S.L. ELECTROMECH PVT. LTD.
11.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 10.00 | 18000.00 | 72000.00 | 14500.00 | 58000.00 | 18675.00 | 74700.00 | 20000.00 | 80000.00 | 21362.00 | 85448.00 | 25000.00 | 100000.00 | 19500.00 | 78000.00 | 15000.00 | 60000.00 | 58000.00 | RASS CONTRACTOR AND ENGINEERS
12.00 | Providing and fixing 50 mm X 6 mm copper strip on surface or in recess for connections etc. as required. | 50.00 | Mtr | 10.00 | 2000.00 | 100000.00 | 2150.00 | 107500.00 | 3072.00 | 153600.00 | 3000.00 | 150000.00 | 3130.00 | 156500.00 | 2640.00 | 132000.00 | 3200.00 | 160000.00 | 2785.00 | 139250.00 | 100000.00 | DOSHI ELECTRIC ENGG. CO.
13.00 | Providing and fixing 50 mm X 6 mm copper strip in 40 mm dia medium class G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Mtr | 11.00 | 2600.00 | 260000.00 | 1850.00 | 185000.00 | 3374.00 | 337400.00 | 3350.00 | 335000.00 | 3724.00 | 372400.00 | 2700.00 | 270000.00 | 3600.00 | 360000.00 | 655.00 | 65500.00 | 65500.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
14.00 | Supplying of Rubber hand gloves suitable for 33kV as per IS Standard | 4.00 | Pairs | 12.00 | 1200.00 | 4800.00 | 1500.00 | 6000.00 | 542.00 | 2168.00 | 3250.00 | 13000.00 | 1123.00 | 4492.00 | 1300.00 | 5200.00 | 950.00 | 3800.00 | 3000.00 | 12000.00 | 2168.00 | S.L. ELECTROMECH PVT. LTD.
15.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class C, 3 mm thick suitable for 33kV AC grade and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ± 20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 26.00 | Metre | 13.00 | 800.00 | 20800.00 | 2500.00 | 65000.00 | 700.00 | 18200.00 | 1050.00 | 27300.00 | 1006.00 | 26156.00 | 1100.00 | 28600.00 | 1500.00 | 39000.00 | 2400.00 | 62400.00 | 18200.00 | S.L. ELECTROMECH PVT. LTD.
16.00 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint "FIRE" and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. | 2.00 | Nos | 14.00 | 1200.00 | 2400.00 | 12500.00 | 25000.00 | 1800.00 | 3600.00 | 3000.00 | 6000.00 | 3145.00 | 6290.00 | 1500.00 | 3000.00 | 950.00 | 1900.00 | 3600.00 | 7200.00 | 1900.00 | Shiva Enterprises
17.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and for all lift, as directed by Engineer-in- charge. | 60.00 | cum | 15.00 | 500.00 | 30000.00 | 250.00 | 15000.00 | 361.00 | 21660.00 | 1200.00 | 72000.00 | 1092.00 | 65520.00 | 250.00 | 15000.00 | 2100.00 | 126000.00 | 250.00 | 15000.00 | 15000.00 | RASS CONTRACTOR AND ENGINEERS, VASUDEV ELECTRICAL SYSTEMS PVT. LTD., SAPPHIRE ENGINEERS
18.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level: 1:2:4 (1 cement: 2 coarse sand (zone-III) derived from natural sources: 4 graded stone aggregate 20mm nominal size derived form natural sources) | 80.00 | cum | 16.00 | 6000.00 | 480000.00 | 7500.00 | 600000.00 | 7229.00 | 578320.00 | 8000.00 | 640000.00 | 6552.00 | 524160.00 | 6000.00 | 480000.00 | 2500.00 | 200000.00 | 7200.00 | 576000.00 | 200000.00 | Shiva Enterprises
19.00 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished seamless type tubes | 120.00 | Kg | 17.00 | 200.00 | 24000.00 | 145.00 | 17400.00 | 127.00 | 15240.00 | 215.00 | 25800.00 | 280.00 | 33600.00 | 110.00 | 13200.00 | 132.00 | 15840.00 | 100.00 | 12000.00 | 12000.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
20.00 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50mm (base metal of minimum 0.45mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | 60.00 | Sqm | 18.00 | 1000.00 | 60000.00 | 500.00 | 30000.00 | 1000.00 | 60000.00 | 650.00 | 39000.00 | 1111.00 | 66660.00 | 678.00 | 40680.00 | 650.00 | 39000.00 | 900.00 | 54000.00 | 30000.00 | RASS CONTRACTOR AND ENGINEERS
21.00 | Providing and fixing G.I. chain link fabric fencing (as per OEM design and recommendation) of overall height of 2 mtr for HT Outdoor Panel in mesh size 50x50 mm made of G.I. wire of dia. 4 mm, PVC coated to achieve outer dia not less than 5 mm in required colour and shade including strengthening with 2 mm dia wire or nuts, bolts and washers as required in angle iron post & strut of size 65x65x5mm including bottom to be split and bent at right angle in opposite direction for 10 cm length and drilling holes upto 10 mm dia. etc. complete as per the direction of Engineer-in-charge. The angle iron posts at middle/centre of each face shall be bedded in cement concrete blocks 45x45x 60 cm of mix 1:2:4 (1 cement:2 fine sand : 4 graded stone aggregate 40 mm nominal size) which shall be erected on a cement concrete base of 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size)of thickness 10 cm, and the angle iron posts at corner shall be strutted on both sides with struts embedded in cement concrete blocks of size 70x45x50 cm of the same mix as for centre/middle posts including providing a gate of dimension 2x2 mtr whose door frame made of 30x30x3 mm MS angle made from MS angle and door flats of size 30x3mm at 20 cm gaps for the door including locking arrangement for the door and painting the structures with synthetic enamel paint complete as required. The cost of excavation, concreting, installation and painting is included in the scope of work. | 40.00 | Metre | 19.00 | 3500.00 | 140000.00 | 1000.00 | 40000.00 | 2000.00 | 80000.00 | 8000.00 | 320000.00 | 2964.00 | 118560.00 | 2800.00 | 112000.00 | 950.00 | 38000.00 | 5000.00 | 200000.00 | 38000.00 | Shiva Enterprises
22.00 | Supplying and making cable route marker with cement concrete 1 :2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 4.00 | Each | 20.00 | 300.00 | 1200.00 | 850.00 | 3400.00 | 422.00 | 1688.00 | 1500.00 | 6000.00 | 1560.00 | 6240.00 | 325.00 | 1300.00 | 150.00 | 600.00 | 500.00 | 2000.00 | 600.00 | Shiva Enterprises
23.00 | Supply of following size 1.1 KV grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098:1988 (Part 1) with upto date amendment complete as required. 4 X 16 sq. mm | 400.00 | Metre | 21.00 | 125.00 | 50000.00 | 325.00 | 130000.00 | 120.00 | 48000.00 | 145.00 | 58000.00 | 125.00 | 50000.00 | 122.00 | 48800.00 | 140.00 | 56000.00 | 150.00 | 60000.00 | 48000.00 | S.L. ELECTROMECH PVT. LTD.
24.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 132.00 | Metre | 22.00 | 180.00 | 23760.00 | 165.00 | 21780.00 | 157.00 | 20724.00 | 290.00 | 38280.00 | 152.00 | 20064.00 | 300.00 | 39600.00 | 100.00 | 13200.00 | 170.00 | 22440.00 | 13200.00 | Shiva Enterprises
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required. Upto 35 sq. mm | 237.00 | Metre | 23.00 | 50.00 | 11850.00 | 45.00 | 10665.00 | 36.00 | 8532.00 | 40.00 | 9480.00 | 27.00 | 6399.00 | 35.00 | 8295.00 | 40.00 | 9480.00 | 30.00 | 7110.00 | 6399.00 | SARASWAT ENGINEERING SERVICES
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct as required. Upto 35 sq. mm | 50.00 | Metre | 24.00 | 60.00 | 3000.00 | 45.00 | 2250.00 | 36.00 | 1800.00 | 30.00 | 1500.00 | 27.00 | 1350.00 | 35.00 | 1750.00 | 40.00 | 2000.00 | 30.00 | 1500.00 | 1350.00 | SARASWAT ENGINEERING SERVICES
27.00 | Supplying and fixing SMC Junction Box on surface with provisions for mounting of MCB , testing and commissioning etc. as required. | 2.00 | Job | 25.00 | 500.00 | 1000.00 | 1500.00 | 3000.00 | 602.00 | 1204.00 | 1550.00 | 3100.00 | 1341.00 | 2682.00 | 3500.00 | 7000.00 | 1400.00 | 2800.00 | 500.00 | 1000.00 | 1000.00 | DOSHI ELECTRIC ENGG. CO., VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
28.00 | Supplying and fixing 32 A Four Pole rating, 415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing SMC Box complete with connections, testing and commissioning etc. as required. | 2.00 | Each | 26.00 | 1200.00 | 2400.00 | 2500.00 | 5000.00 | 843.00 | 1686.00 | 1250.00 | 2500.00 | 1568.00 | 3136.00 | 6450.00 | 12900.00 | 550.00 | 1100.00 | 1000.00 | 2000.00 | 1100.00 | Shiva Enterprises
29.00 | Supplying and fixing following 20 A Single pole, 240V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing SMC Box complete with connections, testing and commissioning etc. as required. | 2.00 | Each | 27.00 | 150.00 | 300.00 | 200.00 | 400.00 | 193.00 | 386.00 | 200.00 | 400.00 | 244.00 | 488.00 | 926.00 | 1852.00 | 200.00 | 400.00 | 145.00 | 290.00 | 290.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
30.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 4 X 16 sq. mm | 4.00 | Set | 28.00 | 300.00 | 1200.00 | 850.00 | 3400.00 | 301.00 | 1204.00 | 300.00 | 1200.00 | 403.00 | 1612.00 | 725.00 | 2900.00 | 250.00 | 1000.00 | 245.00 | 980.00 | 980.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD.
31.00 | Dismantling of flexible pavement(bituminous course) by mechanical means and disposal of dismantled materials up to a lead of 1 kilometer, as per direction of Engineer-in-charge. | 2.00 | Cum | 29.00 | 1000.00 | 2000.00 | 1500.00 | 3000.00 | 3012.00 | 6024.00 | 800.00 | 1600.00 | 10920.00 | 21840.00 | 500.00 | 1000.00 | 4500.00 | 9000.00 | 500.00 | 1000.00 | 1000.00 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD., SAPPHIRE ENGINEERS
32.00 | Supplying and laying of following size , B class medium GI pipe with fitting and cutting, jointing etc.direct in ground (100 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 40 mm dia | 15.00 | Metre | 30.00 | 600.00 | 9000.00 | 850.00 | 12750.00 | 687.00 | 10305.00 | 354.00 | 5310.00 | 2081.00 | 31215.00 | 800.00 | 12000.00 | 650.00 | 9750.00 | 400.00 | 6000.00 | 5310.00 | Awasthi Electric Works
33.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc or making good road crossing ( at a depth of 250mm below finished road level) including form work etc as required. | 2.00 | Cum | 31.00 | 7500.00 | 15000.00 | 6500.00 | 13000.00 | 7229.00 | 14458.00 | 8200.00 | 16400.00 | 8736.00 | 17472.00 | 6000.00 | 12000.00 | 4500.00 | 9000.00 | 7000.00 | 14000.00 | 9000.00 | Shiva Enterprises
34.00 | Constructing masonry Chamber 900mm x 900mm x 1000mm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for cable chamber, with RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate) 20 mm nominal size i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate) 40 mm nominal size and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design :With common burnt clay F.P.S.(non modular) bricks of class designation 7.5. | 6.00 | Each | 32.00 | 19500.00 | 117000.00 | 15000.00 | 90000.00 | 12048.00 | 72288.00 | 5000.00 | 30000.00 | 12012.00 | 72072.00 | 12500.00 | 75000.00 | 7500.00 | 45000.00 | 9000.00 | 54000.00 | 30000.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 12911070.00 |  | 16386195.00 |  | 12097281.00 |  | 12978010.00 |  | 13915246.00 |  | 12561913.00 |  | 12236740.00 |  | 14972670.00
Lowest Amount Quoted BY: S.L. ELECTROMECH PVT. LTD.(12097281.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of 33 KV HT Power Supply System for Incomer side at Devi Ahilya Bai Holkar Airport, Indore Tender ID: 2025_AAI_226274_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | S.L. ELECTROMECH PVT. LTD. (BID ID -825724) | 12097281.00 | L1
| 2 | Shiva Enterprises (BID ID -825458) | 12236740.00 | L2
| 3 | SAPPHIRE ENGINEERS (BID ID -825882) | 12561913.00 | L3
| 4 | DOSHI ELECTRIC ENGG. CO. (BID ID -825034) | 12911070.00 | L4
| 5 | Awasthi Electric Works (BID ID -825885) | 12978010.00 | L5
| 6 | SARASWAT ENGINEERING SERVICES (BID ID -825919) | 13915246.00 | L6
| 7 | VASUDEV ELECTRICAL SYSTEMS PVT. LTD. (BID ID -825612) | 14972670.00 | L7
| 8 | RASS CONTRACTOR AND ENGINEERS (BID ID -825450) | 16386195.00 | L8