## BoQ1
Government eProcurement System Created By: Amitabh Ranjan Created Date/Time: 25-Apr-2025 04:36 PM Tender Title: Replacement of Pump for 300TR and 600TR Chiller Plant at Amritsar Airport Tender ID: 2025_AAI_226617_1
Tender Inviting Authority: <AGM Engg (Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Replacement of Pump for 300 TR and 600 TR Chiller Plant at Amritsar Airport.>
Contract No: <AAI/ASR/ENGG-ELECT/eNIT-14/2024-25>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SNOWMEX ENGINEERS LIMITED (GSTN-07AAMCS8717P1ZF) BID ID -824665 |  | PROJENIX PRIVATE LIMITED (GSTN-NA) BID ID -824513 |  | Blue Star Ltd (GSTN-NA) BID ID -819672
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of Centrifugal Split Casing primary chilled water pump set capable of delivering 165.5 cum/hour flow rate of water against a 36 meter head. Each pump shall comprise the following as required as per specifications. (a) 1 No. Horizontal Split Casing type pump with bronze impeller, S.S. Shaft, C.I. body and mechanical seal with integrel reinforced flanged rubber bellows at suction and discharge side. (b) Duly insulated with 80 Kg/cum density resin bonded fiber glass duly cladded with aluminium sheet of 0.5 mm thickness and properly clamped to pump in two semicircular section as per specifications. (c ) 1 No. Suitable H.P. TEFC squirrel cage induction motor Eff-1 with class 'F' insulation, IP-55 Protection, 1450 RPM, operating on 415 volts ± 10%, 3 Phase, 50 HZ AC supply. (d) Pump set shall be installed with existing 100/125 mm dia M.S. Pipe complete with necessary vibration isolation arrangement, MS base plate, coupling guard, foundation bolts and all other accessories including repairing/modification in existing concrete base foundation. | 1.00 | Each |  | 314195.00 | 314195.00 | 259329.00 | 259329.00 | 270000.00 | 270000.00 | 259329.00 | PROJENIX PRIVATE LIMITED
2.00 | Supply, Installation, Testing and Commissioning of Centrifugal Split Casing primary condensed water pump set capable of delivering 272 cum/hour flow rate of water against a 30 meter head. Each pump shall comprise the following as required as per specifications. (a) 1 No. Horizontal Split Casing type pump with bronze impeller, S.S. Shaft, C.I. body and mechanical seal with integrel reinforced flanged rubber bellows at suction and discharge side. (b) 1 No. Suitable H.P. TEFC squirrel cage induction motor Eff-1 with class 'F' insulation, IP-55 Protection, 1450 RPM, operating on 415 volts ± 10%, 3 Phase, 50 HZ AC supply. (c) Pump set shall be installed with existing 125/150 mm dia M.S. Pipe complete with necessary vibration isolation arrangement, MS base plate, coupling guard, foundation bolts and all other accessories including repairing/modification in existing concrete base foundation. | 1.00 | Each |  | 355014.00 | 355014.00 | 315259.00 | 315259.00 | 321000.00 | 321000.00 | 315259.00 | PROJENIX PRIVATE LIMITED
3.00 | Supply, Installation, Testing and Commissioning of Centrifugal Split Casing primary chilled water pump set capable of delivering 327 cum/hour flow rate of water against a 40 meter head. Each pump shall comprise the following as required as per specifications. (a) 1 No. Horizontal Split Casing type pump with bronze impeller, S.S. Shaft, C.I. body and mechanical seal with integrel reinforced flanged rubber bellows at suction and discharge side. (b) Duly insulated with 80 Kg/cum density resin bonded fiber glass duly cladded with aluminium sheet of 0.5 mm thickness and properly clamped to pump in two semicircular section as per specifications. (c ) 1 No. Suitable H.P. TEFC squirrel cage induction motor Eff-1 with class 'F' insulation, IP-55 Protection, 1475 RPM, operating on 415 volts ± 10%, 3 Phase, 50 HZ AC supply. (d) Pump set shall be installed with existing 100/125 mm dia M.S. Pipe complete with necessary vibration isolation arrangement, MS base plate, coupling guard, foundation bolts and all other accessories including repairing/modification in existing concrete base foundation. | 3.00 | Each |  | 521437.00 | 1564311.00 | 447117.00 | 1341351.00 | 460100.00 | 1380300.00 | 1341351.00 | PROJENIX PRIVATE LIMITED
4.00 | Supply, Installation, Testing and Commissioning of Centrifugal Split Casing primary condensed water pump set capable of delivering 545 cum/hour flow rate of water against a 30 meter head. Each pump shall comprise the following as required as per specifications. (a) 1 No. Horizontal Split Casing type pump with bronze impeller, S.S. Shaft, C.I. body and mechanical seal with integrel reinforced flanged rubber bellows at suction and discharge side. (b) 1 No. Suitable H.P. TEFC squirrel cage induction motor Eff-1 with class 'F' insulation, IP-55 Protection, 1450 RPM, operating on 415 volts ± 10%, 3 Phase, 50 HZ AC supply. (c) Pump set shall be installed with existing 125/150 mm dia M.S. Pipe complete with necessary vibration isolation arrangement, MS base plate, coupling guard, foundation bolts and all other accessories including repairing/modification in existing concrete base foundation. | 3.00 | Each |  | 689774.00 | 2069322.00 | 587648.00 | 1762944.00 | 598000.00 | 1794000.00 | 1762944.00 | PROJENIX PRIVATE LIMITED
5.00 | Supplying, fixing, testing and commissioning of following Sizes BUTTERFLY VALVE (MANUAL) with C I body SS Disc, Nitrile Rubber Seal & ORing PN 16 pressure rating, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications for chilled water/hot eater circulation as specified.
5.10 | BUTTERFLY VALVE (MANUAL) 350 mm | 6.00 | Job |  | 19500.00 | 117000.00 | 58152.00 | 348912.00 | 30143.00 | 180858.00 | 117000.00 | SNOWMEX ENGINEERS LIMITED
5.20 | BUTTERFLY VALVE (MANUAL) 250 mm | 6.00 | Job |  | 16200.00 | 97200.00 | 34574.00 | 207444.00 | 16531.00 | 99186.00 | 97200.00 | SNOWMEX ENGINEERS LIMITED
6.00 | Supplying, fixing, testing and commissioning of NON - RETURN VALVE with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating 350 mm for condenser water circulation as per specifications. | 3.00 | Job |  | 42200.00 | 126600.00 | 95142.00 | 285426.00 | 39516.00 | 118548.00 | 118548.00 | Blue Star Ltd
7.00 | Supplying, fixing, testing and commissioning of NON - RETURN VALVE with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating 250 mm for condenser water circulation as per specifications. | 3.00 | Job |  | 32500.00 | 97500.00 | 46283.00 | 138849.00 | 27154.00 | 81462.00 | 81462.00 | Blue Star Ltd
| Total in Figures |  |  |  |  | 4741142.00 |  | 4659514.00 |  | 4245354.00
Lowest Amount Quoted BY: Blue Star Ltd(4245354.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Pump for 300TR and 600TR Chiller Plant at Amritsar Airport Tender ID: 2025_AAI_226617_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Blue Star Ltd (BID ID -819672) | 4245354.00 | L1
| 2 | PROJENIX PRIVATE LIMITED (BID ID -824513) | 4659514.00 | L2
| 3 | SNOWMEX ENGINEERS LIMITED (BID ID -824665) | 4741142.00 | L3