## BoQ1
Government eProcurement System Created By: VIVEK KUMAR SINGH Created Date/Time: 08-Apr-2025 11:57 AM Tender Title: Provision of Runway Turn Pad Lights and other associated work at JPNI Airport, Patna. Tender ID: 2025_AAI_226647_1
Tender Inviting Authority: Airports Authority of India, JPNI Airport Patna
Name of Work: Provision of Runway Turn Pad Lights and other associated work at JPNI Airport, Patna.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -824178 |  | Techno Electricals (GSTN-24AAGFT9086M1ZG) BID ID -825438
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of FAA complaint Inset type medium intensity Turn Pad light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body of the fitting, inner body and outer cover made of die cast aluminium complete with LED Lamp 6.6 Amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses and all standard accessories and ready for site installation complete with all accessories as required. Unidirectional Centreline light (Green) 8-inch dia. | 76.00 | Each |  | 61200.00 | 4651200.00 | 63000.00 | 4788000.00 | 4651200.00 | Balaji Engineering
2.00 | Installation, testing and commissioning of turn pad light inset fitting with aligning and setting i/c providing sealing/compound material etc and connection with existing isolating Transformer secondary lead including cutting the bitumine & sealing compound of groove at turn pad centreline & other accessories as required for commissioning as per ICAO specification and as per site requirement. | 76.00 | Each |  | 5000.00 | 380000.00 | 6800.00 | 516800.00 | 380000.00 | Balaji Engineering
3.00 | Supply, Installation, Testing & Commissioning of FAA/ICAO/DGCA CAR compliant Indoor type air cooled constant current regulator of microprocessor controlled, thyristor type suitable for remote as well as local control operations on input voltage 230/415 volts, 50Hz AC supply with 6.6A output having 5 steps brightness control with variation of current output and able to communicate with PC or PLC controlled system, with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and digital earth leakage meter, two stage earth leakage detector, positive back indication equipment’s, LED/LCD display, suitable for connection and communication with ALCMS for operation of LED type AGL Circuits etc complete as required confirming to technical specifications for the following rating. 4 KW | 2.00 | Each |  | 250000.00 | 500000.00 | 270000.00 | 540000.00 | 500000.00 | Balaji Engineering
4.00 | Supply of CI isolating transformer housing box, water tight round type, metal container of outside size 330mm height, 450mm made of 10 mm thick cast iron moulding all round, except the top surface, which is 15 mm thick, cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole centre at one side surface centre 75mm above bottom surface suitable to receive one no. of 50 mm dia "B" class GI pipe and check nuts as required .The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220mm at the top surface and 6 no’s M10 tapped hole at the hole centre 260mm to receive fitting base plate and bolts, check nuts etc. as required as per the drawings. Three-hole type. | 76.00 | Each |  | 6500.00 | 494000.00 | 7100.00 | 539600.00 | 494000.00 | Balaji Engineering
5.00 | Installation of 450mm height C.I. transformer housing boxes with a base concrete of 1:3:6 of size 630x630x100mm thick, all round concrete of 1:2:4 of 150mm thick, top sloped with 1:2:4 cement including soil excavation, providing and fixing 300mm long 15mm dia "B" class GI pipe with check nut for drainage of water along with levelling, earth connection etc. as per confirming to tenders technical specifications, terms & conditions etc. complete and as directed by E-I-C. | 76.00 | Each |  | 2800.00 | 212800.00 | 3350.00 | 254600.00 | 212800.00 | Balaji Engineering
6.00 | Installation of old/New dummy base plate on the existing CI housing box/Collar as per site requirement along with providing & fixing of the 3mm thick new neoprene rubber gasket, M10 SS Bolts (, washer etc complete as required. (agency has to provide all accessories as neoprene rubber gasket, M10 SS Bolts (set of 6), washer etc) | 76.00 | Each |  | 300.00 | 22800.00 | 410.00 | 31160.00 | 22800.00 | Balaji Engineering
7.00 | Supply of 2X6 sqmm cable sizes of stranded annealed copper conductor, 5 KV grade, PVC insulated , PVC sheathed , unshielded, ant termite and ant rodent treated Air Field cable and confirming to IS:1554 Part-II as amended up to date and as per specification. | 4508.00 | Mtr |  | 312.00 | 1406496.00 | 335.00 | 1510180.00 | 1406496.00 | Balaji Engineering
8.00 | Supply of 1X6 sqmm cable sizes of stranded annealed copper conductor, 5 KV grade, PVC insulated , PVC sheathed , unshielded, ant termite and ant rodent treated Air Field cable and confirming to IS:1554 Part-II as amended up to date and as per specification. | 1200.00 | Mtr |  | 168.00 | 201600.00 | 175.00 | 210000.00 | 201600.00 | Balaji Engineering
9.00 | Supply of 6 sqmm, 5 KV grade plug and receptacle of type I, class 'B' connector and suitable field attachment with 5 KV grade XLPE insulated, PE sheathed, single core copper conductor cable as required. | 152.00 | Nos. |  | 750.00 | 114000.00 | 790.00 | 120080.00 | 114000.00 | Balaji Engineering
10.00 | Laying of one number PVC insulated and PVC sheathed power cable of grade exceeding 1.1 KV but not exceeding 5KV of size not exceeding 16 sqmm. in the existing RCC / Hume / HDPE/Stoneware / GI pipe complete as required. | 5571.00 | Mtr |  | 25.00 | 139275.00 | 29.00 | 161559.00 | 139275.00 | Balaji Engineering
11.00 | Making field connections by crimping 6 sq.mm. plug & receptible with existing 6 sq.mm. single core PVC copper conductor cable including filling the gap with water sealant material applying HT insulation tape over which again applying PVC insulation tape complete etc as required. | 152.00 | Nos. |  | 160.00 | 24320.00 | 180.00 | 27360.00 | 24320.00 | Balaji Engineering
12.00 | Supply of 5 KV grade 50 HZ series type isolating Transformers, of following rating encapsulated in polyester resin, finally with neoprene rubber with primary and secondary connections as required.(15 W, 6.6/6.6 Amp). | 76.00 | Each |  | 3500.00 | 266000.00 | 3640.00 | 276640.00 | 266000.00 | Balaji Engineering
13.00 | Installation, Testing and Commissioning of new Isolating Transformer i/c connection with primary and secondary lead cable etc complete as required. | 76.00 | Each |  | 400.00 | 30400.00 | 450.00 | 34200.00 | 30400.00 | Balaji Engineering
14.00 | Supply of 50 mm outer dia size HDPE pipe as per IS 4984: 2016 specification, material grade PE 100 PN 10 and as per specified in particular specification as per approved make of AAI. | 6000.00 | Mtr. |  | 200.00 | 1200000.00 | 235.00 | 1410000.00 | 1200000.00 | Balaji Engineering
15.00 | Laying of HDPE pipe up to 160 mm dia. through HDD trenchless method direct in ground up to depth of 3.0 (i/c Under runway/Taxiway/Road in all type of soil including coupling, splicing of pipe, providing nylon rope in spares pipes as per requirement etc. as required in all respect as per specification. | 4400.00 | Mtr. |  | 410.00 | 1804000.00 | 450.00 | 1980000.00 | 1804000.00 | Balaji Engineering
16.00 | Laying of HDPE pipe up to 110 mm dia direct in ground including excavating the earth and laying of pipe in trench in such a way that the top of pipe shall not be less than 750 mm below the ground level and also refilling with excavated soil etc. complete as required. (This item will be paid only where HDPE pipe is laid direct in ground without HDD method) | 1571.00 | Mtr. |  | 130.00 | 204230.00 | 145.00 | 227795.00 | 204230.00 | Balaji Engineering
17.00 | Supply of 25 mm size outer dia medium B class G.I. pipe as per approved make of AAI. | 2500.00 | Mtr. |  | 320.00 | 800000.00 | 354.00 | 885000.00 | 800000.00 | Balaji Engineering
18.00 | Laying of 25 mm size outer dia medium B class G.I. pipe i/c coupling socket connection etc in the existing trench /masonry open duct etc complete as requirement. | 2500.00 | Mtr. |  | 32.00 | 80000.00 | 40.00 | 100000.00 | 80000.00 | Balaji Engineering
19.00 | Supply of 2CX2.5 sqmm and 0.3 mtrs long copper conductor two pin secondary lead male/female suitable for airfield lighting system as required. | 152.00 | Each |  | 800.00 | 121600.00 | 865.00 | 131480.00 | 121600.00 | Balaji Engineering
20.00 | Supply of 2core X 2.5 sq.mm AFL secondary lead made out of annealed tinned copper conductor, EPR insulated PCP sheathed, unarmoured, anti-termite & anti rodent treated 600V/1100V grade for connection between isolating transformer and airfield light fixtures. | 2950.00 | Mtrs |  | 190.00 | 560500.00 | 180.00 | 531000.00 | 531000.00 | Techno Electricals
21.00 | Laying of secondary lead of up to size 2core X2.5 sqmm and making interconnection between isolating transformer and AFL fittings etc in existing pipe/open masonry duct wherever as reqd etc complete as required. | 2950.00 | Mtrs |  | 25.00 | 73750.00 | 27.00 | 79650.00 | 73750.00 | Balaji Engineering
22.00 | Cutting of pipe groove with kerf cutting machine of suitable size & depth for laying of GI/HDPE Pipe/Secondary lead in bituminous/PQC area of runway i/c kerfing, chiselling, cleaning and refilling the groove with suitable concrete/sealant DOBEFIL 60/Hardener and making good including etc. complete as required as per direction of EIC. | 50.00 | Cum |  | 1000.00 | 50000.00 | 6200.00 | 310000.00 | 50000.00 | Balaji Engineering
23.00 | Constructing brick masonry manhole chamber of min. outside dimension 1.6m x 1.6m x 1.1m with medium class bricks(side wall width 22.5cm) in cement mortar 1:6 (1 cement : 6 coarse sand) R.C.C. top slab of 100mm thick with mix 1:2:4 cement concrete (1 cement : 2 coarse sand : 4 graded stone of aggregate 20mm nominal size), foundation concrete 1: 4: 8 mix (1 cement : 4 coarse sand : 8 graded stone of aggregate 40mm nominal size) in side plastering 12 mm thick with cement mortar 1:4 (1 cement : 4 coarse sand). 02 nos. of equal sizes RCC slabs/covers should be provided in a MS angle frame work of size (35m x 35 x 3mm) at the 04 nos. of edges on top and bottom of the slab and job including excavation of soil and disposal of surplus excavated soil within a lead of 50 metres, levelling of soil to cover elevated edge around the constructed cable chamber as directed by EIC. | 13.00 | Job |  | 20000.00 | 260000.00 | 15000.00 | 195000.00 | 195000.00 | Techno Electricals
24.00 | Earthing with G.I pipe 4.5mm long x 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc with charcoal/coke and salt complete as required . | 12.00 | Each |  | 6000.00 | 72000.00 | 6250.00 | 75000.00 | 72000.00 | Balaji Engineering
25.00 | Providing and laying earth connections, from earth electrode with 6SWG dia, G.I wire in 15mm dia, G.I pipe from earth electrode as required. | 60.00 | Mtr. |  | 250.00 | 15000.00 | 290.00 | 17400.00 | 15000.00 | Balaji Engineering
26.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cable as required. | 1218.00 | Mtr |  | 32.00 | 38976.00 | 35.00 | 42630.00 | 38976.00 | Balaji Engineering
27.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of Electric panel and for levelling of cable chamber ege with area nearby in operational area and as per direction of EIC. | 10.00 | Cum |  | 6000.00 | 60000.00 | 6500.00 | 65000.00 | 60000.00 | Balaji Engineering
28.00 | Excavation & refilling for cable trench in soft soil up to 1.2 mtrs including dressing of sides and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 630.00 | Cum |  | 150.00 | 94500.00 | 200.00 | 126000.00 | 94500.00 | Balaji Engineering
29.00 | Modification in existing ALCMS architecture design for integration of new CCRs for turn pad light and other GLF as PTT edge light, Isolation bay edge and guard light etc available at Patna Airport for controlling with existing ALCMS system , configure the system for controlling the turn pad light with existing ALCMS. | 1.00 | Job |  | 125000.00 | 125000.00 | 200000.00 | 200000.00 | 125000.00 | Balaji Engineering
30.00 | Structural steel work in built up chequered plate(8mm) work including cutting, hoisting, fixing in partition and applying a primary coat of approved steel primer etc. all complete as required. | 2300.00 | Kg |  | 130.00 | 299000.00 | 150.00 | 345000.00 | 299000.00 | Balaji Engineering
31.00 | Supplying and Drawing 4 mm dia FRLS PVC insulated annealed copper conductor, unarmoured cable in the existing surface/recessed steel/ PVC conduit as required. | 2120.00 | Mtr |  | 65.00 | 137800.00 | 70.00 | 148400.00 | 137800.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 14439247.00 |  | 15879534.00
Lowest Amount Quoted BY: Balaji Engineering(14439247.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Runway Turn Pad Lights and other associated work at JPNI Airport, Patna. Tender ID: 2025_AAI_226647_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering (BID ID -824178) | 14439247.00 | L1
| 2 | Techno Electricals (BID ID -825438) | 15879534.00 | L2