## BoQ1
Government eProcurement System Created By: Gajraj Singh Bhati Created Date/Time: 21-Mar-2025 04:10 PM Tender Title: Provision of standby cables to make ringmain system for ILS and DVOR at Dimapur Airport Tender ID: 2025_AAI_226676_1
Tender Inviting Authority: AGM(E-E) AAI, Dimapur Airport.
Name of Work: “Provision of standby cables to make ringmain system for ILS and DVOR at Dimapur Airport”
Contract No: 2025_AAI_226676_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | D.D.METAL CORPORATION (GSTN-18ACGPD4624F2ZW) BID ID -821760 |  | Genesis (GSTN-09AGAPJ4118N1ZA) BID ID -825321 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -825804
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SUB HEAD:A-SUPPLY OF CABLES Supply of XLPE insulated, armoured 1.1 KV grade aluminium conductor cable as per IS 7098 (Part 1) 1988 with upto date ammendments of following sizes:
1.10 | 3.5 x 150 sq.mm | 5000.00 | mtr |  | 850.00 | 4250000.00 | 688.00 | 3440000.00 | 800.00 | 4000000.00 | 3440000.00 | Genesis
2.00 | SUB HEAD:B- LAYING OF CABLES AND ASSOCIATED WORKS Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing masonry open duct as required:
2.10 | Above 95 sq. mm and upto 185 sq. mm | 90.00 | Mtr |  | 200.00 | 18000.00 | 42.00 | 3780.00 | 70.00 | 6300.00 | 3780.00 | Genesis
3.00 | Laying and fixing of one number XLPE armoured power cable of 1.1 KV grade of following size on cable tray as required.
3.10 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 450.00 | Mtr |  | 150.00 | 67500.00 | 57.00 | 25650.00 | 70.00 | 31500.00 | 25650.00 | Genesis
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground including excavation,sand cushioning, protective covering and refilling the trench etc as required.
4.10 | Above 95 sq. mm and upto 185 sq. mm | 1800.00 | Mtr |  | 408.00 | 734400.00 | 380.00 | 684000.00 | 470.00 | 846000.00 | 684000.00 | Genesis
5.00 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground in the same trench in horizontal tier formation including excavation,sand cushioning, protective covering and refilling the trench etc as required.
5.10 | Above 120 sq. mm and upto 400 sq. mm | 1800.00 | Mtr |  | 408.00 | 734400.00 | 335.00 | 603000.00 | 300.00 | 540000.00 | 540000.00 | ECS ENGINEERING PVT LTD
6.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required:
6.10 | Above 95 sq. mm and upto 185 sq. mm | 90.00 | mtr |  | 150.00 | 13500.00 | 40.00 | 3600.00 | 70.00 | 6300.00 | 3600.00 | Genesis
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs size for following size of XLPE armoured aluminium conductor cable of 1.1 KV grade as required.
7.10 | 3.5 x 150 sq.mm | 18.00 | set |  | 1500.00 | 27000.00 | 400.00 | 7200.00 | 1176.00 | 21168.00 | 7200.00 | Genesis
8.00 | Supplying and installing following size of perforated pre painted M.S cable trays with perforation not more than 17.5 %, in convenient sections,joined with connectors and fixed on 25mmx25mmx3 mm angle supports duly grouted on the terrace floor with PCC 1:2:4 foundation of size 0.1m x 0.1m x 0.1m for each support leg and at a span not more than 1 metre etc complete as required.
8.10 | 300 mm width x 62.5 mm depth x 2.0 mm thickness | 165.00 | mtr |  | 660.00 | 108900.00 | 500.00 | 82500.00 | 917.00 | 151305.00 | 82500.00 | Genesis
9.00 | Providing,laying and fixing of following dia GI pipe (medium class) in ground complete with GI fittings including trenching (75 cm deep) and refilling etc. as required.
9.10 | 80 mm dia | 30.00 | mtr |  | 1200.00 | 36000.00 | 850.00 | 25500.00 | 1090.00 | 32700.00 | 25500.00 | Genesis
10.00 | Supply,Installation,Testing and Commissioning of outdoor feeder pillar type cable loop-in-loop box fabricated out of 2mm thick Ms sheet of size 600mm x 600mm x 350 mm(depth) ,dust and vermin proof, IP 65 with 100 A TPN aluminium busbars, suitable for termination of 2 nos. 3.5 x 120 sq.mm XLPE armoured cables of 1.1 kV grade, mounted on sutable size of angle iron frame supports of height 750 mm and grouting the same to ground with PCC 1:2:4 etc complete as required. | 6.00 | Each |  | 7800.00 | 46800.00 | 8000.00 | 48000.00 | 28000.00 | 168000.00 | 46800.00 | D.D.METAL CORPORATION
11.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal / coke and salt as required. | 6.00 | set |  | 8000.00 | 48000.00 | 3500.00 | 21000.00 | 6500.00 | 39000.00 | 21000.00 | Genesis
12.00 | Providing and fixing 6 SWG dia G.l. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ sub main wiring/ cable as required. | 60.00 | mtr |  | 30.00 | 1800.00 | 30.00 | 1800.00 | 58.00 | 3480.00 | 1800.00 | D.D.METAL CORPORATION, Genesis
13.00 | Supplying and making cable route marker with cement concrete 1:2:4( 1 cement:2 coarse sand:4 graded stone aggregate 20 mm nominal size) of size 60 cm x 60 cm at the bottom and 50 cm x 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 33.00 | Each |  | 700.00 | 23100.00 | 400.00 | 13200.00 | 1200.00 | 39600.00 | 13200.00 | Genesis
14.00 | Design, fabrication, supply, installation, testing and commissioning of weather, vermin proof, powder- coated, fully compartmentalized outdoor type feeder pillar panel {minimum IP 65 protection)with lifting hooks, fabricated with 2mm thick CRCA sheet with hinged double door with gasket, detachable gland plates for cable chamber, 2 earthing studs, bottom type cable entry provision having locking arrangement in front, chemically treated through at-least seven-tank process consisting of the following switchgears: INCOMER 4 Pole, 100 amp, 35KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker with extended terminals and adjustable Thermal setting (02 Nos.). 4 pole, 100 A, 415 Volts, 50 Hz AC Automatic transfer Switch with protection and having auto-manual selection switch- 01 No. 100 Amps, TPN alluminium Busbars of suitable for complete panel - 01 Set. OUTGOING 4 Pole, 63 amp, 25KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker adjustable Thermal setting (01 Nos.). METERING Digital Voltmeter 0-500V, three phase with selector switch and protection MCB - 02 Set. Digital Ammeter 0-100 A, three phase with suitable CTs, selector switch and protection MCB - 02 No. LED TYPE INDICATION LAMPS (RYB) with protection MCB - 2 set (1 set = 03 Lamp). | 1.00 | Job |  | 188000.00 | 188000.00 | 110000.00 | 110000.00 | 160000.00 | 160000.00 | 110000.00 | Genesis
15.00 | Supplying and installing following size of hot dipped galvanised iron cable tray ( galvanisotion thickness not less then 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, bends, Tees etc. The cable tray shall be installed on roof with suitable cement concerete / fire brics padestel including bolts & nuts etc compelete as required
15.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 165.00 | Mtr |  | 500.00 | 82500.00 | 488.00 | 80520.00 | 658.00 | 108570.00 | 80520.00 | Genesis
16.00 | Design, manufacturing, supply, installation, testing and commissioning of cubical type totally enclosed free standing, dust free, damp and vermin proof and water proof double door outdoor LT Panel fabricated out of 2mm thick CRCA sheet duly powder coated and including supply and fixing of the following items and interconnections, wiring with suitable sizes wires/ cables and including mounting legs, all civil works like excavation, cement concrete, ,brick work pedestal, plastering, refilling etc. and as per specification as required. INCOMER 01 Nos. 160A 4P MCCB (Ics=Icu=35 KA) . Incomer shall have one set of the following items: Digital Voltmeter suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch. 1 Set of Indication Lamps, LED type, R,Y,B. Digital Ammeter of suitable range (to measure 0-160A), for 3 phase 4 wire operation with LED display and selector switch and CT ratio programmable and auto ranging along with suitable range CTs. BUS BAR 1 Set of 200A TPN Busbars of aluminium alloy. OUTGOING 6 Nos. 40A FP MCCB (Ics=Icu=25 KA) with thermal magnetic release. 6 Nos. 20A DP MCB (10 KA). Control MCB, Heavy duty connector strips, Din bar etc as per requirement. | 1.00 | Each |  | 98400.00 | 98400.00 | 85000.00 | 85000.00 | 282000.00 | 282000.00 | 85000.00 | Genesis
| Total in Figures |  |  |  |  | 6478300.00 |  | 5234750.00 |  | 6435923.00
Lowest Amount Quoted BY: Genesis(5234750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of standby cables to make ringmain system for ILS and DVOR at Dimapur Airport Tender ID: 2025_AAI_226676_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Genesis (BID ID -825321) | 5234750.00 | L1
| 2 | ECS ENGINEERING PVT LTD (BID ID -825804) | 6435923.00 | L2
| 3 | D.D.METAL CORPORATION (BID ID -821760) | 6478300.00 | L3