## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 07-Apr-2025 06:55 PM Tender Title: Provision of aerosol-based fire suppression system for Electrical and AS Equipment at Bagdogra Airport. SH - Provision of aerosol-based fire suppression system and surge diverter for Electrical and AS Equipment at Bagdogra Airport. Tender ID: 2025_AAI_227392_1
Tender Inviting Authority: AGM(E-E)
Name of Work: Provision of aerosol-based fire suppression system for Electrical & AS Equipment at Bagdogra Airport. SH: - Provision of aerosol-based fire suppression system and surge diverter for Electrical & AS Equipment at Bagdogra Airport
Contract No: 2025_AAI_227392_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vrinda Nano Technologies Pvt Ltd (GSTN-06AABCV6699N1ZG) BID ID -830479 |  | Nexpo Power Solutions Pvt Ltd (GSTN-NA) BID ID -830660
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Substation SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 30gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 51.00 | Nos | 18750.00 | 16500.00 | 841500.00 | 16500.00 | 841500.00 | 841500.00 | Vrinda Nano Technologies Pvt Ltd, Nexpo Power Solutions Pvt Ltd
2.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 60gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 24.00 | Nos | 24650.00 | 21590.00 | 518160.00 | 19500.00 | 468000.00 | 468000.00 | Nexpo Power Solutions Pvt Ltd
3.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 100gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 11.00 | Nos | 32800.00 | 28500.00 | 313500.00 | 27500.00 | 302500.00 | 302500.00 | Nexpo Power Solutions Pvt Ltd
4.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 250gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 6.00 | Nos | 46375.00 | 42300.00 | 253800.00 | 40500.00 | 243000.00 | 243000.00 | Nexpo Power Solutions Pvt Ltd
5.00 | SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 500gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 33 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per BIS / NABL / EN / UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 23.00 | Nos | 61900.00 | 53625.00 | 1233375.00 | 48750.00 | 1121250.00 | 1121250.00 | Nexpo Power Solutions Pvt Ltd
6.00 | SITC of 3 Phase / Type1+2 (KEMA Certified) Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single- pole combined lightning current and surge arrester, Type 1 SPDThe device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350µs) of 25kA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV,. The device shall have inbuilt fuse for L N. Follow current extinguishing capability [L- N]/[N-PE] : 100kArms / 100Arms. The device shall have built in fuse and operation of SPD shall be independent of Line current for L N SPD. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643- 11:2011 or or EN 61643-11:2012 for testing of all parameter at 10/350 µs and 8/20 µs. with transparent enclosure IP65 | 6.00 | Set | 18250.00 | 126750.00 | 760500.00 | 60000.00 | 360000.00 | 360000.00 | Nexpo Power Solutions Pvt Ltd
7.00 | CNS Department SITC of Aerosol Generator having aerosol mass of 500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 3.00 | Nos | 61600.00 | 48270.00 | 144810.00 | 42060.00 | 126180.00 | 126180.00 | Nexpo Power Solutions Pvt Ltd
8.00 | SITC of Aerosol Generator having aerosol mass of 1500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 2.00 | Nos | 124200.00 | 104155.00 | 208310.00 | 68250.00 | 136500.00 | 136500.00 | Nexpo Power Solutions Pvt Ltd
9.00 | SITC of Aerosol Generator having aerosol mass of 2500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 10.00 | Nos | 157000.00 | 130736.00 | 1307360.00 | 105000.00 | 1050000.00 | 1050000.00 | Nexpo Power Solutions Pvt Ltd
10.00 | SITC of EN CERTIFIED Fire Detection Cum Release System with cross zoning of EN CERTIFIED heat & smoke detectors, EN CERTIFIED hooter cum strobe, EN CERTIFIED abort & release button. | 4.00 | Nos | 18250.00 | 120000.00 | 480000.00 | 50000.00 | 200000.00 | 200000.00 | Nexpo Power Solutions Pvt Ltd
11.00 | Supply and Laying of 2 core 1.5 sq. mm. FRLS armored Cable with accessories Llike juction boxes, shaddle, clamp, screws etc. | 150.00 | Mtr | 350.00 | 450.00 | 67500.00 | 125.00 | 18750.00 | 18750.00 | Nexpo Power Solutions Pvt Ltd
| Total in Figures |  |  |  |  | 6128815.00 |  | 4867680.00
Lowest Amount Quoted BY: Nexpo Power Solutions Pvt Ltd(4867680.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of aerosol-based fire suppression system for Electrical and AS Equipment at Bagdogra Airport. SH - Provision of aerosol-based fire suppression system and surge diverter for Electrical and AS Equipment at Bagdogra Airport. Tender ID: 2025_AAI_227392_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexpo Power Solutions Pvt Ltd (BID ID -830660) | 4867680.00 | L1
| 2 | Vrinda Nano Technologies Pvt Ltd (BID ID -830479) | 6128815.00 | L2