## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 27-Mar-2025 05:42 PM Tender Title: Enhancement of illumination in city side at B M Airport Ranchi. SH - SITC of High Mast and associated work. Tender ID: 2025_AAI_228542_1
Tender Inviting Authority: SM (E-E), AAI, B.M.Airport, Ranchi
Name of Work: Enhancement of illumination in city side at B M Airport Ranchi. SH- : SITC of High Mast & associated work.
Contract No: 2025_AAI_228542_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -832953 |  | DILIGENT SERVICES (GSTN-NA) BID ID -833367 |  | waystone engicon private limited (GSTN-NA) BID ID -829520
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design ,Fabrication,Supply, Installation, Testing and Commissioning of 12.5 (Tweleve & half) metre height hot dip galvanised high mast in two sectioned suitable for wind velocity as per IS 875 part-3 along with its all accessories i.e head frame, suitable SS wire rope, double drum winch,Galvanised lantern carriage arrangement to install minimum 08 Nos. flood Light luminaries symmetrical arrangenment with required cable coonection from panel to mast top & fitting cable connection with counter weight (08 Nos.1x200W LED Flood Light luminaries), lightning finial, suitable integral power tool motor installed inside the base compartment for its operation, trailing cable with suitable size,connector,manual handle,junction box, foundation bolts along with nuts, washers, anchor plates and templates etc. as reqiured suitable to meet out minimum average lux level of 20 lux as per ICAO standards. | 4.00 | Job | 195934.00 | 130000.00 | 520000.00 | 197000.00 | 788000.00 | 100000.00 | 400000.00 | 400000.00 | waystone engicon private limited
2.00 | Design and casting of suitable shallow foundation with M-20 concrete for the high mast mentioned in item no.-1 considering the safe soil bearing capacity at site as 10T/Sq.Mtr at min. 2 metres depth and as per soil bearing capacity, works also included hard/soft soil exacavation & disposal for foundation including erection, testing and commissioning of 12.5 mtrs high mast system etc. as required and as per specification mentioned in TS & as per direction of EIC. ( Foundation design shall be vetted by the NIT/IIT or any Goverment institution). | 4.00 | Job | 90363.00 | 40000.00 | 160000.00 | 80000.00 | 320000.00 | 80000.00 | 320000.00 | 160000.00 | M/S AMAR ENTERPRISES
3.00 | Supply,Installation,Testing and Commissioning of following type LED Flood light luminaire which should have system efficacy not less than 120 lm/W, toughened glass, secondary lens optic should have should have Narrow beam & SW beam with individual optic lens, IP66 protection, IK08 should have system surge protection upto 20 KV,single piece integral high pressure dicast aluminium housing, complete with electronic power driver, all its accessories,colour temperature should not more than 5700K , suitable to works on 230V+ 10% ,50 Hz AC power suppl etc complete as required following flood light fixtures on the lantern carrier of high mast etc. as required. 200 W LED Flood light | 40.00 | Each | 7381.00 | 8700.00 | 348000.00 | 8500.00 | 340000.00 | 6000.00 | 240000.00 | 240000.00 | waystone engicon private limited
4.00 | Supply,Installation,Testing and Commissioning of LED Type low intensity aviation obstruction light suitable for 220 V , 50 HZ AC supply and as per ICAO standard etc. complete as required. As per list of approved make or equivalent. | 4.00 | Each | 2434.00 | 5250.00 | 21000.00 | 2500.00 | 10000.00 | 10000.00 | 40000.00 | 10000.00 | DILIGENT SERVICES
5.00 | Design,Supply,Installation,Testing and Commissioning of outdoor type distribution feeder pillar box with 40 A TPN MCB as incommer,totally enclosed,free standing, vermin dust proof,Water proof,front operated, double door made of 2 mm thick ,rubber gasket,powder coating painting with provision for incoming cable connection 35 Sqmm and out going 16 & 2.5 Sqmm terminals for the power tool motor etc. complete as required provisions for earthing, support for switchgears & busbars with suitable angle iron frame base, floor mounting, Al. bus bar,suitable for operation on 3 Phase and 4 wire, 415V, 50 Hz AC supply system including control wiring, necessary connections etc and supply & mountings of following items. (a) 32 A TPN MCB with breaking Capacity of 10 KA -02 No. (b )Suitable TPN Bus bars of Aluminum alloy-1 Set (c )Power Contactor(32A,3P,3Ph,415V,50 Hz) with necessary timer,relay,MCB as required for automatic switching of luminaries,-1 Set. (d )Power Contactor(9A,2P,1Ph,230 V,50Hz) with necessary timer,relay,MCB as required for automatic switching of aviation light, -1Set. (e)RYB Indicating Lamp ( LED Type) - 1 set (f) Rotary switch for auto & manual syastem-1 set (g) Push Button for motor opeartion-1 Set (h) Ammeter with selector switch and suitable C/T etc. -01 set (i) Voltmeter with selector switch - 01 set (j) 16 &2.5 Sqmm terminals/connectors for out going etc - 01 set | 4.00 | Job | 27994.00 | 27500.00 | 110000.00 | 22000.00 | 88000.00 | 30000.00 | 120000.00 | 88000.00 | DILIGENT SERVICES
6.00 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, Al conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments. 3.5 x 35 Sq.mm. Aluminium conductor | 595.00 | Metre | 273.00 | 226.00 | 134470.00 | 185.00 | 110075.00 | 230.00 | 136850.00 | 110075.00 | DILIGENT SERVICES
7.00 | Supply of following sizes XLPE insulated & extruded PVC inner sheath and PVC outer sheath solid Copper conductor armoured Control cable of 1.1 KV grade conforming to IS-7098 (part-I)-1988 with upto date amendments etc complete as required. 10 Core x 2.5 Sqmm | 100.00 | Metre | 234.00 | 220.00 | 22000.00 | 315.00 | 31500.00 | 150.00 | 15000.00 | 15000.00 | waystone engicon private limited
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable/RC Cable of 1.1 KV grade upto size 35 Sq.mm in the existing masonry open duct as required. | 40.00 | Metre | 25.00 | 22.00 | 880.00 | 120.00 | 4800.00 | 30.00 | 1200.00 | 880.00 | M/S AMAR ENTERPRISES
9.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable/RC Cable 1.1KV grade of upto size 35 Sq.mm. in the existing RCC/HUME/STONE WARE/Metal /HDPE pipe as reqd. | 435.00 | Metre | 33.00 | 14.00 | 6090.00 | 60.00 | 26100.00 | 40.00 | 17400.00 | 6090.00 | M/S AMAR ENTERPRISES
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable RC Cable of 1.1 KV grade upto size 35 Sq.mm. on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 120.00 | Metre | 50.00 | 22.00 | 2640.00 | 80.00 | 9600.00 | 40.00 | 4800.00 | 2640.00 | M/S AMAR ENTERPRISES
11.00 | Supplying and making end termination with brass compression gland and aluminium/copper lugs for following size of PVC insuated and PVC sheathed/XLPE power cable of 1.1KV grade as reqd. 3.5 x 35 Sq.mm. Al Cable | 8.00 | Each | 405.00 | 44.00 | 352.00 | 250.00 | 2000.00 | 200.00 | 1600.00 | 352.00 | M/S AMAR ENTERPRISES
12.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 6600.00 | 4950.00 | 19800.00 | 6000.00 | 24000.00 | 10000.00 | 40000.00 | 19800.00 | M/S AMAR ENTERPRISES
13.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 12.00 | Meter | 620.00 | 330.00 | 3960.00 | 200.00 | 2400.00 | 500.00 | 6000.00 | 2400.00 | DILIGENT SERVICES
14.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 12.00 | Meter | 129.00 | 99.00 | 1188.00 | 300.00 | 3600.00 | 500.00 | 6000.00 | 1188.00 | M/S AMAR ENTERPRISES
15.00 | Supplying and fixing of 25 mm X 5 mm G.I strip on surface/reccese etc as required. | 40.00 | Meter | 233.00 | 198.00 | 7920.00 | 250.00 | 10000.00 | 100.00 | 4000.00 | 4000.00 | waystone engicon private limited
16.00 | Excavation of hard rock for existing concrete platform/cable trench up to width of 1.5 mtr & lift upto 1.5 mtr including getting out and disposal of excavated soil as directed by EIC. | 20.00 | Cum | 1182.00 | 990.00 | 19800.00 | 4000.00 | 80000.00 | 100.00 | 2000.00 | 2000.00 | waystone engicon private limited
17.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required. 50 mm dia | 80.00 | Metre | 1583.00 | 550.00 | 44000.00 | 100.00 | 8000.00 | 100.00 | 8000.00 | 8000.00 | waystone engicon private limited, DILIGENT SERVICES
18.00 | Supply of 50 mm dia ISI marked HDPE pipe as per IS 4984:2016 of PE 80 grade and PN 6 rating complete etc. as required. | 250.00 | Meter | 60.00 | 55.00 | 13750.00 | 55.00 | 13750.00 | 50.00 | 12500.00 | 12500.00 | waystone engicon private limited
19.00 | Providing the HDD upto a depth of approx 2 mtr. Suitable for laying of 50 mm dia HDPE pipe etc. as required. | 250.00 | Meter | 394.00 | 198.00 | 49500.00 | 500.00 | 125000.00 | 250.00 | 62500.00 | 49500.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 1485350.00 |  | 1996825.00 |  | 1437850.00
Lowest Amount Quoted BY: waystone engicon private limited(1437850.00)

## BOQ Summary
BOQ Summary Details Tender Title: Enhancement of illumination in city side at B M Airport Ranchi. SH - SITC of High Mast and associated work. Tender ID: 2025_AAI_228542_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | waystone engicon private limited (BID ID -829520) | 1437850.00 | L1
| 2 | M/S AMAR ENTERPRISES (BID ID -832953) | 1485350.00 | L2
| 3 | DILIGENT SERVICES (BID ID -833367) | 1996825.00 | L3