## BoQ1
Government eProcurement System Created By: Madan Mohan Agrawal Created Date/Time: 07-Apr-2025 12:46 PM Tender Title: Construction of New DVOR at Surat International Airport. SH. Electrical Works. Tender ID: 2025_AAI_228598_1
Tender Inviting Authority: AGM (E-E), AAI, Surat Airport, Surat
Name of Work :"Construction of New DVOR at Surat Int'l Airport. SH: Electrical Works."
Contract No: Tender ID 2025_AAI_228598_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s. Jyona Power (GSTN-24AAIFJ5981F2Z6) BID ID -833845 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -835109
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH:I- Internal Electrification,Light Fixtures.
1.01 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed steel conduit i/c supply and laying of suitable size medium class steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLSH PVC insulated copper conductor single core cable etc as required. (a) Group B | 24.00 | Point |  | 768.00 | 18432.00 | 1251.00 | 30024.00 | 18432.00 | M/s. Jyona Power
1.02 | Wiring for circuit/ submain wiring alongwith earth wire with the sizes of 2 x 2.5 Sq.mm + 1 x 2.5 Sq.mm Earth Wire FRLSH PVC insulated copper conductor, single core cable in surface/ recessed steel conduit i/c supply and laying of suitable size medium class steel conduit complete as required. | 120.00 | Meter |  | 168.00 | 20160.00 | 230.70 | 27684.00 | 20160.00 | M/s. Jyona Power
1.03 | Wiring for circuit/ submain wiring alongwith earth wire with the sizes of 2 x 4 Sq.mm + 1 x 4 Sq.mm Earth Wire FRLSH PVC insulated copper conductor, single core cable in surface/ recessed steel conduit i/c supply and laying of suitable size medium class steel conduit complete as required. | 220.00 | Meter |  | 194.00 | 42680.00 | 279.90 | 61578.00 | 42680.00 | M/s. Jyona Power
1.04 | Wiring for circuit/ submain wiring alongwith earth wire with the sizes of 2 x 6 Sq.mm + 1 x 6 Sq.mm Earth Wire FRLSH PVC insulated copper conductor, single core cable in surface/ recessed steel conduit i/c supply and laying of suitable size medium class steel conduit complete as required. | 50.00 | Meter |  | 267.00 | 13350.00 | 354.10 | 17705.00 | 13350.00 | M/s. Jyona Power
1.05 | Wiring for light/ power plug with 2X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 250.00 | Meter |  | 197.00 | 49250.00 | 161.00 | 40250.00 | 40250.00 | Instapower Ltd
1.06 | Supplying and fixing of 25 mm sizes of medium class steel conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | 30.00 | Meter |  | 117.00 | 3510.00 | 130.60 | 3918.00 | 3510.00 | M/s. Jyona Power
1.07 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 20.00 | Each |  | 267.00 | 5340.00 | 745.00 | 14900.00 | 5340.00 | M/s. Jyona Power
1.08 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. (A). Telephone Socket Outlet | 3.00 | Each |  | 68.00 | 204.00 | 188.00 | 564.00 | 204.00 | M/s. Jyona Power
1.09 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.(A). 15/16 A Switch | 30.00 | Each |  | 72.00 | 2160.00 | 173.60 | 5208.00 | 2160.00 | M/s. Jyona Power
1.10 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. (A). 6 pin 15/16 A socket outlet | 30.00 | Each |  | 90.00 | 2700.00 | 235.00 | 7050.00 | 2700.00 | M/s. Jyona Power
1.11 | Supplying and fixing 12 Module (200 mm x 150 mm) size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. | 2.00 | Each |  | 247.00 | 494.00 | 560.00 | 1120.00 | 494.00 | M/s. Jyona Power
1.12 | Supplying and fixing 3 Module (100 mm x 75 mm) size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. | 6.00 | Each |  | 151.00 | 906.00 | 212.00 | 1272.00 | 906.00 | M/s. Jyona Power
1.13 | Supplying and fixing 6 Module (200 mm x 75 mm) size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required. | 6.00 | Each |  | 185.00 | 1110.00 | 311.00 | 1866.00 | 1110.00 | M/s. Jyona Power
1.14 | Supplying and fixing of 6 way (4 +18), double door , metal, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing, blanking plates etc. as required. (But without MCB/RCCB/Isolator). | 2.00 | Each |  | 2217.00 | 4434.00 | 3236.00 | 6472.00 | 4434.00 | M/s. Jyona Power
1.15 | Supplying and fixing of 12 way (2+10), Double Door, Single pole and neutral (SPN), sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing , blanking plates etc. as required. (But without MCB/RCCB/Isolator) | 6.00 | Each |  | 1040.00 | 6240.00 | 1620.00 | 9720.00 | 6240.00 | M/s. Jyona Power
1.16 | Supplying and fixing of 6 way (2+4), Double Door, Single pole and neutral (SPN), sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing , blanking plates etc. as required. (But without MCB/RCCB/Isolator) | 2.00 | Each |  | 988.00 | 1976.00 | 1349.00 | 2698.00 | 1976.00 | M/s. Jyona Power
1.17 | Supplying and fixing of 63A rating, 415 V, 10 kA, 4 Pole MCB suitable in the existing TPN MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Each |  | 1135.00 | 2270.00 | 1748.00 | 3496.00 | 2270.00 | M/s. Jyona Power
1.18 | Supplying and fixing of 63A rating, 240/415 V, 10 kA, "C" curve, DP MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 6.00 | Each |  | 655.00 | 3930.00 | 908.00 | 5448.00 | 3930.00 | M/s. Jyona Power
1.19 | Supplying and fixing of 32 Amp rating, Two pole, (one phase and neutral), 415/240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 5.00 | Each |  | 2265.00 | 11325.00 | 3027.00 | 15135.00 | 11325.00 | M/s. Jyona Power
1.20 | Supplying and fixing of 40 Amp rating, Two pole SPN, (one phase and neutral), 240 volts, residual current breaker with overload protection (RCBO), having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 5.00 | Each |  | 2570.00 | 12850.00 | 335.00 | 1675.00 | 1675.00 | Instapower Ltd
1.21 | Supplying and fixing of 5 A to 32 A rating , 240/415 V, 10 kA, "C" curve, SP MCB suitable for inductive load in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 82.00 | Each |  | 145.00 | 11890.00 | 199.00 | 16318.00 | 11890.00 | M/s. Jyona Power
1.22 | Supply and Fixing of Modular type Socket having Residual Current Device (SRCD) with steel enclosure with 25 Amps DP MCB having Over current protection suitable for 1.5 TR Inverter AC complete as required. | 9.00 | Each |  | 1130.00 | 10170.00 | 3465.00 | 31185.00 | 10170.00 | M/s. Jyona Power
1.23 | Supply of Recessed mounting 2' x 2' LED panel Luminaire, 36W, IP 20, 6500K CRCA deep-drawn housing suitable for 600 mm X 600 mm modular ceiling complete as per technical specifications. | 10.00 | Each |  | 2035.00 | 20350.00 | 2604.00 | 26040.00 | 20350.00 | M/s. Jyona Power
1.24 | Supply of Recessed mounting 2' x 2' LED panel Luminaire, 36W, IP 20, 6500K CRCA deep-drawn housing suitable for 600 mm X 600 mm modular ceiling having battery back up complete as per technical specifications. (Make : eveready model :LEDPLB036I6-04BB or Equivalent). | 10.00 | Each |  | 2750.00 | 27500.00 | 5990.00 | 59900.00 | 27500.00 | M/s. Jyona Power
1.25 | Supply of 35 Watt LED type Road/ Street light with minimum protection level IP 66, pressure die cast housing with epoxy power coated prismatic poly carbonate cover with individual LED lenses and complete assembly with LED, driver and accessories pre-wired up to terminal block i/c suitable mounting accessories etc. as required. | 6.00 | Each |  | 2115.00 | 12690.00 | 5990.00 | 35940.00 | 12690.00 | M/s. Jyona Power
1.26 | Installation, testing and commissioning of pre-wired, LED fitting of all types, complete with all accessories etc. directly on/in ceiling/ wall, including connection with 1.5 Sq.mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 19.00 | Each |  | 100.00 | 1900.00 | 1353.00 | 25707.00 | 1900.00 | M/s. Jyona Power
1.27 | Fixing of LED street light fitting on pole / wall including supply and bending the 40mm medium class GI pipe upto 2.5 mtr length to the required shape, iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint including connection with 1.5 Sq.mm PVC insulated copper conductor single core cable, testing and commissioning complete as required. | 6.00 | Each |  | 745.00 | 4470.00 | 650.00 | 3900.00 | 3900.00 | Instapower Ltd
1.28 | Supply of 1200 mm sweep five star BLDC ceiling fan of rating from 26 watt to 32 watt and all standard accessories etc., complete as required.(Havells , Model no.FHCEO5SWHT48 or euivalent) | 4.00 | Each |  | 2500.00 | 10000.00 | 3185.00 | 12740.00 | 10000.00 | M/s. Jyona Power
1.29 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 Sq.mm FRLSH PVC insulated, copper conductor, single core cable etc. as required. | 4.00 | Each |  | 105.00 | 420.00 | 3690.00 | 14760.00 | 420.00 | M/s. Jyona Power
1.30 | Supply and fixing of 12 W fully Automatic Emergency LED Light having back up time of 3 hours complete with standard accessories all as required. Make: Prolite or AAI preffered make list. | 3.00 | Each |  | 2890.00 | 8670.00 | 325.00 | 975.00 | 975.00 | Instapower Ltd
1.31 | Supply and Installation of Astro digital time switch suitable for single phase 240V AC for lighting control based on sunrise/sunset timings by lattitude/longititude settings. (Make: L&T ; Model : DHTQB01016 or Equivalent) (Time switch is to be installed near street light DB of DVOR building) | 1.00 | Each |  | 2075.00 | 2075.00 | 6185.00 | 6185.00 | 2075.00 | M/s. Jyona Power
1.32 | Supply & Fixing of 230 Volt , 50 Hz industrial heavy duty exhaust fan having 300 mm sweep, 1400 rev/minute including Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | 2.00 | Each |  | 2465.00 | 4930.00 | 4524.00 | 9048.00 | 4930.00 | M/s. Jyona Power
1.33 | Supply of LED type Aviation Obsctruction light as per ICAO requirement.(bajaj model no BGJV 302 or equivalent) | 2.00 | Each |  | 2500.00 | 5000.00 | 4586.00 | 9172.00 | 5000.00 | M/s. Jyona Power
2.00 | SH:II - SITC of Earthing , LA , SPD.
2.01 | SITC of Three Phase modular type Surge Protection Device (CLASS- B,1,Stage-1/primary) with minimum lightning impulse current (Iimp) of 100KA (10/350 micro seconds) neutral to earth, 50 KA (10/350 micro sec) line to neutral ,limiting voltage less than 1.5 KV,to be installed in parrallel at the mains panel of power entry point including making connection of surge protection device in parallel to the busbar of the main electrical panel using 16 Sq mm single core PVC insulated flexible copper conductor cables, in IP55 grade powder coated metal enclosure with 63 Amp. service / bypass changeover switch, on the mains power entry point at the incomers including all accessories such as suitable rating , MCBs, making end terminations, fixing/mounting arrangement of SPD , modifications in the existing panels by cutting the section,wiring/cable connection modification if required as per the site requirement etc complete as required as per enclosed specification. | 1.00 | Each |  | 51000.00 | 51000.00 | 22825.00 | 22825.00 | 22825.00 | Instapower Ltd
2.02 | SITC of Single Phase modular type Surge Protection Device (CLASS- B,1,Stage-1/primary) with minimum lightning impulse current (Iimp) of 100KA (10/350 micro seconds) neutral to earth, 50 KA (10/350 micro sec) line to neutral ,limiting voltage less than 1.5 KV,to be installed in parrallel at the mains panel of power entry point including making connection of surge protection device in parallel to the busbar of the main electrical panel using 16 Sq mm single core PVC insulated flexible copper conductor cables, in IP55 grade powder coated metal enclosure with 63 Amp. service / bypass changeover switch, on the mains power entry point at the incomers including all accessories such as suitable rating , MCBs, making end terminations, fixing/mounting arrangement of SPD , modifications in the existing panels by cutting the section,wiring/cable connection modification if required as per the site requirement etc complete as required as per enclosed specification. | 1.00 | Each |  | 37500.00 | 37500.00 | 11966.00 | 11966.00 | 11966.00 | Instapower Ltd
2.03 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc.with charcoal/ coke and salt as required. | 3.00 | Set |  | 4500.00 | 13500.00 | 6835.00 | 20505.00 | 13500.00 | M/s. Jyona Power
2.04 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with GI nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter |  | 315.00 | 9450.00 | 401.90 | 12057.00 | 9450.00 | M/s. Jyona Power
2.05 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 30.00 | Meter |  | 115.00 | 3450.00 | 172.90 | 5187.00 | 3450.00 | M/s. Jyona Power
2.06 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 6000.00 | 24000.00 | 12370.00 | 49480.00 | 24000.00 | M/s. Jyona Power
2.07 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 2.00 | Each |  | 315.00 | 630.00 | 369.00 | 738.00 | 630.00 | M/s. Jyona Power
2.08 | Supplying and fixing of Medium class G.I. pipe of 50 mm dia. (nominal) 02 metres length and to be grouted on concrete foundation with installation including base plate , nut bolts , washer etc complete as required on the roof. | 4.00 | Each |  | 1500.00 | 6000.00 | 1360.00 | 5440.00 | 5440.00 | Instapower Ltd
2.09 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For horizontal run) | 30.00 | Meter |  | 60.00 | 1800.00 | 87.90 | 2637.00 | 1800.00 | M/s. Jyona Power
2.10 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For vertical run) | 30.00 | Meter |  | 95.00 | 2850.00 | 68.40 | 2052.00 | 2052.00 | Instapower Ltd
2.11 | Providing joints by using brazing technique on 25 mm X 3 mm copper strip on surface or in recess for connections to another copper earth strip for interconnection to all earth's of Lightening Arrestors, counterpoise , Equipment and Electrical power supply earthing etc. as required. | 200.00 | Each |  | 205.00 | 41000.00 | 750.00 | 150000.00 | 41000.00 | M/s. Jyona Power
2.12 | Supply of Copper Plate of Size 600 mm x 600 mm x 3.15 mm thickness of purity not less than 90% complete as required | 17.00 | Each |  | 14000.00 | 238000.00 | 12100.00 | 205700.00 | 205700.00 | Instapower Ltd
2.13 | Supply of Copper strip of Size 25 mm x 5 mm thickness of purity not less than 90% complete as required. | 1000.00 | Meter |  | 1125.00 | 1125000.00 | 864.00 | 864000.00 | 864000.00 | Instapower Ltd
2.14 | Supply of Copper wire of atleast 4 mm dia.of purity not less than 90% complete as required | 400.00 | Meter |  | 145.00 | 58000.00 | 49.00 | 19600.00 | 19600.00 | Instapower Ltd
2.15 | Supply of Copper rod of 1 inch dia and 5 feet length having 2 inch thread on one side and cone shape on other side of purity not less than 90% complete as required | 10.00 | Each |  | 8750.00 | 87500.00 | 6765.00 | 67650.00 | 67650.00 | Instapower Ltd
2.16 | Supply of 70 Sqmm HRFR PVC Insulated Copper conductor flexible cable suitable for 1.1 kv confirming to IS:694 of green color complete as required | 200.00 | Meter |  | 815.00 | 163000.00 | 861.00 | 172200.00 | 163000.00 | M/s. Jyona Power
2.17 | Supply of 4 inch (100 mm) dia medium class GI pipewith suitable GI base plate to mount 4-inch GI pipe complete as required. | 12.00 | Meter |  | 1600.00 | 19200.00 | 799.00 | 9588.00 | 9588.00 | Instapower Ltd
2.18 | Supply of 2 inch (50 mm) dia medium class GI pipe having minimum thickness 3 mm alongwith the required socket from 2 inch to 1 inch complete as required. | 36.00 | Meter |  | 1350.00 | 48600.00 | 381.00 | 13716.00 | 13716.00 | Instapower Ltd
2.19 | Supply of 40 mm dia dia perforated and 10 feet length GI pipe for earthing having minimum thickness of 3 mm complete as required. | 17.00 | Each |  | 975.00 | 16575.00 | 2275.00 | 38675.00 | 16575.00 | M/s. Jyona Power
2.20 | Supply of UV resistant PVC pipe of 2 inch dia and 20 feet length complete as required | 50.00 | Each |  | 1875.00 | 93750.00 | 369.00 | 18450.00 | 18450.00 | Instapower Ltd
2.21 | Supply of Heavy duty PVC pipe (plastic corrugated hose) of 4 inch dia complete as required. | 20.00 | Meter |  | 250.00 | 5000.00 | 123.00 | 2460.00 | 2460.00 | Instapower Ltd
2.22 | Supply of Heavy duty PVC pipe (plastic corrugated hose) of 2 inch dia complete as required. | 90.00 | Meter |  | 97.00 | 8730.00 | 110.70 | 9963.00 | 8730.00 | M/s. Jyona Power
2.23 | Supply of granular salt having approx size of 1-3 cm complete as required. | 4250.00 | Kg |  | 5.00 | 21250.00 | 6.20 | 26350.00 | 21250.00 | M/s. Jyona Power
2.24 | Supply of granular Charcoal having approx size of 1-3 cm complete as required. | 4250.00 | Kg |  | 7.00 | 29750.00 | 6.20 | 26350.00 | 26350.00 | Instapower Ltd
2.25 | Supply of 150mm width x 50 mm depth x 1.6 mm thickness hot dipped GI cable raceway (Galvanisation thickenss shall not be less than 50 microns) alongwith L and T joint complete as required. | 15.00 | Meter |  | 485.00 | 7275.00 | 307.00 | 4605.00 | 4605.00 | Instapower Ltd
2.26 | Supply of 150mm width x 50 mm depth x 1.6 mm thickness hot dipped GI perforated cable tray (Galvanisation thickenss shall not be less than 50 microns) with perforation not more tha 17.5% alongwith L and T joint complete as required. | 15.00 | Meter |  | 405.00 | 6075.00 | 307.00 | 4605.00 | 4605.00 | Instapower Ltd
2.27 | Supply of extension board having 4 x 5/15 amp with individaul switch with 30 meter 3x1.5 sqmm PVC sheather copper conductor cable complete as required. | 2.00 | Each |  | 1750.00 | 3500.00 | 2890.00 | 5780.00 | 3500.00 | M/s. Jyona Power
2.28 | Supply of 16 Amps 3-Pin Top complete as required. | 10.00 | Each |  | 115.00 | 1150.00 | 98.00 | 980.00 | 980.00 | Instapower Ltd
2.29 | Supply of 3x2.5 Sqmm Copper conductor flexible cable as per IS 694 complete as required. | 40.00 | Meter |  | 145.00 | 5800.00 | 92.00 | 3680.00 | 3680.00 | Instapower Ltd
2.30 | Supply of 4x16 Sqmm Cu Flexible Cable as per IS 694 complete as required | 100.00 | Meter |  | 1135.00 | 113500.00 | 738.00 | 73800.00 | 73800.00 | Instapower Ltd
3.00 | SH: III - Supply and Laying of Cable, HDPE Pipe, LT panel
3.01 | Supply of 3.5CX 240 sq.mm size of XLPE insulated, PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date complete as required. | 2600.00 | Mtr |  | 1600.00 | 4160000.00 | 1120.00 | 2912000.00 | 2912000.00 | Instapower Ltd
3.02 | Supply of 110mm (OD-110mm, PN 8, PE 80) ISI marked HDPE pipe, conforming to IS 4984, along with all acessories like socket, bend, couplers as required including fitting, cutting, jointing etc., etc. complete in all respect as per direction of Engineer-in-Charge. required. | 2600.00 | Mtr |  | 440.00 | 1144000.00 | 334.00 | 868400.00 | 868400.00 | Instapower Ltd
3.03 | Laying of 110 mm (OD-110mm,PN 08,PE 80) ISI marked HDPE pipe, along with all accessories like socket, bend, couplers, suitable size PP rope as required including fitting, cutting, jointing with HDD trenchless method direct in ground (up to 3 mtrs below ground level ) in all type of soil etc complete in all respect as per direction of Engineer-in-Charge. required. | 2500.00 | Mtr |  | 550.00 | 1375000.00 | 1555.00 | 3887500.00 | 1375000.00 | M/s. Jyona Power
3.04 | Laying of 110 mm (OD-110mm,PN 08,PE 80) ISI marked HDPE pipe, along with all accessories like socket, bend, couplers, suitable size PP rope as required including fitting, cutting, jointing direct in ground (up to 75cm below ground level ) in all type of soil i/c excavation & re-filling the trench but excluding sand cushioning and protective covering etc complete in all respect as per direction of Engineer-in-Charge. required. | 100.00 | Mtr |  | 90.00 | 9000.00 | 156.00 | 15600.00 | 9000.00 | M/s. Jyona Power
3.05 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required | 2600.00 | Mtr |  | 70.00 | 182000.00 | 45.50 | 118300.00 | 118300.00 | Instapower Ltd
3.06 | Supplying and making end termination with brass compression gland and aluminium/copper lugs for 3.5 X 240 sq. mm (62 mm) - Aluminimum size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Set |  | 750.00 | 4500.00 | 1609.00 | 9654.00 | 4500.00 | M/s. Jyona Power
3.07 | Design, Supply, Installation, Testing & Commissioning of Indoor Type, Floor Mounted compartmentalized cubical type panel board of 415 Volt (Nominal), fabricated out of 2 mm (14 SWG) thick CRCA Sheet, free standing and totally enclosed, IP42, Weather proof / dust proof / vermin proof with bottom / top cable entries and cable alleys. The panel board shall be suitable for operation on 3 Phase, 4 wire, 50 Hz AC Supply and with suitable size busbar, earth bar and following switchgear instrumentation and protection devices etc. complete with connections, interconnection, earthing, painting and marking as per site conditions etc complete as required as per the specifications. Supplier must take LT Panel Design Approval from EIC before the supply. (i) Incomer: 160A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. Multi function Meter (Shows Voltage, Current & Frequency) with 3 line LCD/LED Display of size 96 x 96 mm. - 02 Nos.,Indication Lamp R, Y & B ( LED Type) -02 set, (ii) Buscoupler : 160A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 No. with ON, OFF indication lamp. Outgoing: 63A, MCCB, 4P, 25 KA (Icu= 100% Ics) with extended rotary handle - 08 Nos.,Indication Lamp R & G ( LED type) - 08 Set, 200A Aluminium busbar, 3 Phase & Neutral,Electrically & Mechanically interlocked with Mechanical key lock (3 Lock +2 Key), Necessary CT & Control wiring arrangement , Power terminal and other accessories . The Bus bar chamber size shall be suitable for connection of 3.5x 240 Sqmm size incoming cable. | 1.00 | Job |  | 200000.00 | 200000.00 | 191000.00 | 191000.00 | 191000.00 | Instapower Ltd
3.08 | Design, Supply, Installation, Testing & Commissioning of Outdoor Type, Floor Mounted compartmentalized cubical type panel board of 415 Volt (Nominal), fabricated out of 2 mm thick CRCA Sheet, free standing and totally enclosed, IP66, Weather proof / dust proof / vermin proof with bottom / top cable entries and cable alleys. The panel board shall be suitable for operation on 3 Phase, 4 wire, 50 Hz AC Supply and with suitable size busbar, earth bar and following switchgear instrumentation and protection devices etc. complete with connections, interconnection, earthing, painting and marking as per site conditions etc complete as required as per the specifications. Supplier must take LT Panel Design Approval from EIC before the supply. (i) Incomer: 160A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. Multi function Meter (Shows Voltage, Current & Frequency) with 3 line LCD/LED Display of size 96 x 96 mm. - 02 Nos.,Indication Lamp R, Y & B ( LED Type) -02 set, (ii) Buscoupler : 160A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 No. with ON, OFF indication lamp. Outgoing: 63A, MCCB, 4P, 25 KA (Icu= 100% Ics) with extended rotary handle - 04 Nos.,Indication Lamp R & G ( LED type) - 04 Set, 200A Aluminium busbar, 3 Phase & Neutral,Electrically & Mechanically interlocked with Mechanical key lock (3 Lock +2 Key), Necessary CT & Control wiring arrangement , Power terminal and other accessories . The Bus bar chamber shall be suitable for connection of 3.5x 240 Sqmm size incoming cable. | 1.00 | Job |  | 175000.00 | 175000.00 | 166400.00 | 166400.00 | 166400.00 | Instapower Ltd
3.09 | Supply and fixing of 5KVA-02 (1+1) single phase 230V online UPS system alongwith 26 Ah+ 10% Battery- (1+1) with 30 minute back up as per technical specifications complete as required. | 1.00 | Job |  | 250000.00 | 250000.00 | 111050.00 | 111050.00 | 111050.00 | Instapower Ltd
3.10 | Supply and fixing of insultion mats for electric shock protection of 2 mm thickness x 1 m wide polysynthetic mats conforming to IS 15652 : 2006, Class - A up to 3.3 KV along with suitable adhesive etc complete as required. | 30.00 | Mtr |  | 1540.00 | 46200.00 | 1479.00 | 44370.00 | 44370.00 | Instapower Ltd
3.11 | Supply Installation Testing and commissioning of IP65 Mi combinable type Bus Bars Junction Box with 250 amps Al. bus bars, should be made of high quality Polycarbonate PC-GFS ( totally insulated class II ) (shock proof, rust free, corrosion free, acid and chemical resistant, fire retardant, having high impact, made of halogen and silica free recyclable material),UV resistant, having high grade gasket made of Polyurethane, should withstand glow wire test at 9600C, should be flame retardant,materials suitable for outdoor application and the enclosure should have pre-moulded knock out for cable entry on side walls and enclosure should have PC hinged option. For cable entry from bottom part a de-touchable type PC flange should be fitted with plain wall. The plain wall of flange can be drilled as per cable size. Lid screws should be made of polyamide spring loaded half turn type and to open a triangular key or tool will be required. Inside enclosure should have lot of self-threaded holes so that mounting plate/bus bars can be mounted easily. Degree of Protection : IP 65 _Busbar rating: 250A (RYBN: 30 X 06) MM CU Dimensions : 500 [L] x 1075 [H] x 630 [D] mm_ Given Cable Size : 3.5C X 240 Sq.mm Al. Cable (Loop In / Loop Out) Mounting Type : Outdoor / Floor Mounting ( FRP Frangible Frame) | 6.00 | Each |  | 13750.00 | 82500.00 | 27200.00 | 163200.00 | 82500.00 | M/s. Jyona Power
3.12 | Providing and fixing of 100 A Change over switch along with Metal Enclosure and required bus bar with DIN type 4 fuses suitable to terminate the 240 Sq.mm cable as incomer (02 nos) and 240 Sq.mm Cable as outgoing complete as required. | 1.00 | Job |  | 9000.00 | 9000.00 | 12370.00 | 12370.00 | 9000.00 | M/s. Jyona Power
3.13 | SITC of 100A, 3phase, 415VAC, four pole, solenoid based Automatic Transfer Switch (changeover time range 0.1 - 6 seconds programmable) with Microprocessor based Programmable controller for monitoring and storing electrical parameters of power supply, and optically isolated RS 485 Interface including dismantling of existing ATS from the existing housing, fixing of new ATS in existing housing including modification in the housing if required, laying and connection of power cables, supply and laying of Modbus serial communication cables for interconnection between ATS controller and gateway, connection of CT, suitable for existing air conditioning, lighting & UPS load etc. compelete as per the site requirement. | 1.00 | Job |  | 98500.00 | 98500.00 | 76400.00 | 76400.00 | 76400.00 | Instapower Ltd
3.14 | SITC of 3 phase Multi functional meter for measuring Line Voltage, Phase Voltage, Line Current, Frequency, Watts, power factor, VA,Watt hour with RS 485 serial Interface and optically isolated, 50A Clip on CT's, including all other works such as fixing of Multi functional meters in distribution panel by cutting face plate of distribution panel, laying and connection of power cables, supply and laying of Modbus serial communication cables for interconnection between Multifunctional Meters and gateway, connection of CT, wiring etc. compelete as per the site requirement. | 4.00 | Job |  | 6000.00 | 24000.00 | 5795.00 | 23180.00 | 23180.00 | Instapower Ltd
3.15 | SITC of Temperature monitor with RS 485 serial Interface and optically isolated including all other works such as fixing of Temperature sensors in remote room, laying and connection of power cables, supply and laying of Modbus serial communication cables for interconnection between Temperature Sensor monitor and gateway, connection of sensor, wiring etc. compelete as per the site requirement. | 1.00 | Job |  | 7500.00 | 7500.00 | 5180.00 | 5180.00 | 5180.00 | Instapower Ltd
3.16 | SITC of gateway for the serial interface of existing RS 485 to GPRS with included LTE 4G sim having one year internet plan subscription for cloud based remote monitoring with inbuilt 16GB memory for data backup including wall mounted enclosure/housing for housing the same gateway and all other activities such as fixing of gateway in provided wall mounted enclosure/housing, laying and connection of power cables, connection of communication cables, wiring etc. compelete as per the site requirement. | 1.00 | Job |  | 105000.00 | 105000.00 | 7415.00 | 7415.00 | 7415.00 | Instapower Ltd
3.17 | SITC of Line Interactive UPS with Load Capacity of minimum 600VA and having Input voltage range 140-300VAC , 50 Hz, 230VAC Output voltage, inbuilt battery of capacity 12V /7AH for supplying power backup to Multi Functional Meters and Gateway. | 1.00 | Job |  | 5500.00 | 5500.00 | 2966.00 | 2966.00 | 2966.00 | Instapower Ltd
3.18 | Interfacing of item no. 76 to item no. 80 including providing and commisioning of totally hiring based and Cloud based Energy Monitoring Software with Programming , required Licencing, facility of data logging, remote monitoring, event notification system (Max. 5 minutes delay interval between two successive readings), Auto SMS, Email Alert Feature for any abnormal deviation of pre-set electrical parameters range of the power supply at the site etc. with five year subscription of cloud based energy management system, site support etc. complete as required. | 1.00 | Job |  | 5000.00 | 5000.00 | 200000.00 | 200000.00 | 5000.00 | M/s. Jyona Power
3.19 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 2600.00 | Meter |  | 20.00 | 52000.00 | 21.00 | 54600.00 | 52000.00 | M/s. Jyona Power
4.00 | SH: IV - SITC of Air Conditioning System
4.01 | Supply of 5 Star rating fully inverter split type Air conditioner of 1.5 TR (Minimum ISEER 4.5) capacity with adjustable mode different cooling capacities for different cooling needs, fitted with rotary/scroll compressor of min 05 years warranty, having copper condenser coil, operating for Refrigerant R32/other eco riendly green gas and indoor unit suitable for wall mounting operation with cordless LCD/LED Remote, Auto restart operation, connecting copper refrigerant pipes (with suitable nitrile insulation including charging of suitable refrigerant gas, 4C x 4 Sq.mm copper cable, drain pipe) up to 3Mtr. and suitable for operating on 230V ±10%, 50Hz, Single Phase, AC , control wiring, thermostat, washable synthetic air filter etc. complete as capable of performing Cooling, Dehumidifying, Air Circulating, Filtering functions, stablizer free operation etc. meeting the technical specifications and make as per the list of approved make.Note:- The AC units shall be rust proof coating in cooling coil and condensor. | 9.00 | Each |  | 40000.00 | 360000.00 | 55842.00 | 502578.00 | 360000.00 | M/s. Jyona Power
4.02 | Installation, Testing and Commissioning of split type Air conditioner of upto and including 1.5TR capacity and fixing of refrigerant copper piping of suitable size for both suction and discharge along with suitable nitrile / thermal Insulation and Electrical Cable (4C x 4 Sq.mm) of size having suitable size of copper conductor for connection from indoor to outdoor unit including charging of suitable refrigerant gas, providing mounting stand for out door unit and all suitable necessary accessories complete as per site requirement. | 9.00 | Each |  | 2525.00 | 22725.00 | 2600.00 | 23400.00 | 22725.00 | M/s. Jyona Power
4.03 | Supply & Fixing of Extra Refrigerant copper piping for 1.5 TR A.C of suitable size for both suction and discharge along with suitable thermal Insulation and Electrical Cable of suitable size copper conductor for connection from indoor to outdoor unit and suitable necessary accessories for connection complete as required. (One length of suction piping , one length of discharge piping and one length of copper wire shall be measured one meter for this item) | 50.00 | Mtr |  | 910.00 | 45500.00 | 1114.00 | 55700.00 | 45500.00 | M/s. Jyona Power
4.04 | Supply and fixing of 75mm dia medium class PVC pipe for covering refrigerant copper piping for both suction , discharge and Electrical Cable with suitable necessary accessories for pipe connection complete as required. | 50.00 | Mtr |  | 152.00 | 7600.00 | 372.50 | 18625.00 | 7600.00 | M/s. Jyona Power
4.05 | Supply and fixing of hard UPVC drain pipe of 25 mm dia connection from indoor to outside of wall including bends, sitable insulation , U straps , clamps and necessary accessories for connection etc. complete as required. | 50.00 | Mtr |  | 157.00 | 7850.00 | 173.60 | 8680.00 | 7850.00 | M/s. Jyona Power
4.06 | Supply and fixing of 5KVA, 15Amp / 130V-300V working voltage Digital electronics voltage stabilizer of wall mounting type with Instant Start and Intelligent time delay provisions suitable for 1.5 TR Split AC units. (Make : V-guard Model : VGB500 Digital/ Make: Everest Model: EWD 500 or its Equivalent from AAI approved make list) | 9.00 | Each |  | 2500.00 | 22500.00 | 3328.00 | 29952.00 | 22500.00 | M/s. Jyona Power
4.07 | Supply & fixing of of Timer with 2 hr/4 hr / 8 hr duration and having digital temp. controller & sensor suitable for AC power supply 240 V, 50 Hz. etc. complete as required. (Make: Smart Electronics Model: TIM 2T or euivalent) | 4.00 | Each |  | 2500.00 | 10000.00 | 7450.00 | 29800.00 | 10000.00 | M/s. Jyona Power
5.00 | SH: V-SITC of Fire Alarm & Fire Suppression System
5.01 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | 100.00 | Meter |  | 105.00 | 10500.00 | 179.80 | 17980.00 | 10500.00 | M/s. Jyona Power
5.02 | Supplying, installation,testing & commissioning of IP based Addressable fire alarm panel,LCD display, suitable for 01 loop,complying relevant national fire alarm code for local fire alarm system with mimic diagram for all area / zone covered,complete with all connections.The panel shall have input of 240 volts AC power supply,inbuilt automatic battery charger, 24volts, 2X12volts, 7Ah sealed lead acid maintenance free batteries sufficient for 24 hours normal power backup & working, interconnections. The panel shall be UL / EN / FM listed and along with GSM auto dialer facility (20 Nos min.) etc. as required. | 1.00 | Each |  | 227250.00 | 227250.00 | 62000.00 | 62000.00 | 62000.00 | Instapower Ltd
5.03 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) addressable Smoke detector base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications ,complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors). | 10.00 | Each |  | 3333.00 | 33330.00 | 2765.00 | 27650.00 | 27650.00 | Instapower Ltd
5.04 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) Addressable Manual call station (Resetable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or poly carbonate equivalent) with clear operating instruction and the word Fire appearing on the front complete with connections etc. as required and as per enclosed specifications. | 2.00 | Each |  | 4545.00 | 9090.00 | 5605.00 | 11210.00 | 9090.00 | M/s. Jyona Power
5.05 | Supply, installation, testing and commissioning of UL / EN listed (latest version) Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 1.00 | Each |  | 2121.00 | 2121.00 | 7450.00 | 7450.00 | 2121.00 | M/s. Jyona Power
5.06 | SITC of 4.5 kg Co2 type fire extingusher wall mounting accessories etc complete as required. | 4.00 | Each |  | 3939.00 | 15756.00 | 6185.00 | 24740.00 | 15756.00 | M/s. Jyona Power
5.07 | SITC of 4.5 kg ABC type fire extingusher wall mounting accessories etc complete as required. | 2.00 | Each |  | 2121.00 | 4242.00 | 2604.00 | 5208.00 | 4242.00 | M/s. Jyona Power
5.08 | SITC of 2.8 kg Aerosole based automatic fire exingushers along with complete system required to operate in case of fire complete as required. | 6.00 | Each |  | 103020.00 | 618120.00 | 80650.00 | 483900.00 | 483900.00 | Instapower Ltd
5.09 | SITC of 2 Zone Gas release panel complete with battery back up complete as required. | 3.00 | Each |  | 15150.00 | 45450.00 | 12405.00 | 37215.00 | 37215.00 | Instapower Ltd
5.10 | SITC of conventional multi criteria type smoke detector complete as required. | 14.00 | Each |  | 1515.00 | 21210.00 | 2679.00 | 37506.00 | 21210.00 | M/s. Jyona Power
5.11 | SITC of Monitor Module complete as required. | 3.00 | Each |  | 3333.00 | 9999.00 | 3110.00 | 9330.00 | 9330.00 | Instapower Ltd
5.12 | Supply and fixing of Aerosol fire Extinguishing Generator - 8 Gram | 16.00 | Each |  | 4848.00 | 77568.00 | 14830.00 | 237280.00 | 77568.00 | M/s. Jyona Power
5.13 | Supply and fixing of Aerosol fire Extinguishing Generator - 20 Gram | 7.00 | Each |  | 12120.00 | 84840.00 | 16675.00 | 116725.00 | 84840.00 | M/s. Jyona Power
6.00 | SH: VI-SITC of DG Sets
6.01 | SITC of 4 wheel Trolley mounted (with jack arrangement) outdoor Mobile DG Set along with canopy of 25 KVA capacity complying the CPCB standards complete as required. | 1.00 | Each |  | 525000.00 | 525000.00 | 750000.00 | 750000.00 | 525000.00 | M/s. Jyona Power
6.02 | Dismentling, Shifting , installation , testing and commissiong of existing 35 kVA DG Set of Mahindra make from Existing DVOR to New Location of DVOR at approx distance of 2 km by loading/ unloading by truck in operationla area complete as required. | 1.00 | Job |  | 25455.00 | 25455.00 | 65000.00 | 65000.00 | 25455.00 | M/s. Jyona Power
| Total in Figures |  |  |  |  | 12687027.00 |  | 13792206.00
Lowest Amount Quoted BY: M/s. Jyona Power(12687027.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New DVOR at Surat International Airport. SH. Electrical Works. Tender ID: 2025_AAI_228598_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s. Jyona Power (BID ID -833845) | 12687027.00 | L1
| 2 | Instapower Ltd (BID ID -835109) | 13792206.00 | L2